## Revision
Revision
Date | Version | Author | Observations
42418 | v0 | C.CAMARA | Creation (from v4.2) | CHANGE TO :
42443 | B | T.MARTINEZ | Update following adopted ICD template
42904 | B1 | T.MARTINEZ | Updating to new Template V0.35
43061 | B2 | Sogema | Modifying IO class.
43061 | B2 | T. MARTINEZ | Merge to newest template Classification of Alarm
43069 | B2 | T. MARTINEZ | Moving to template v0.36
43090 | B2 | T. MARTINEZ | Generation SW code and Adresses
43156 | C- | T. MARTINEZ | Update to V0.37
43299 | C- | J.LAW | Class List: 1. Update default value for row 11 - 23
Partners view

## Introduction
Introduction
For all ICD relative to equipment monitoring & control , this ECI (Equipment Classes & Instances) file template must be used as appendix to define: - the equipment classes, from an I/O point of view - all instances relative to each class
Recommandations
1 | Use one ECI file for each ICD document (one ICD=one subsystem)
2 | Do not change the organisation of the ECI file:
- Sheet "Equipment classes" : define all classes for the relative subsystem (see meaning of each field in the "Definitions" sheet)
- Sheet "Equipment instances" : define all instances for the relative subsystem (see meaning of each field in the "Definitions" sheet)
3 | For each sheet, do not change the organisation of the sheet (does not remove any column) in order to be able to use the standard export/import tools
4 | Create the necessary number of classes: for example, if similar equipment have different numbers of DI, DO, AI, create one class for each case
5 | Define, if possible, contiguous addresses for equipments/points within the same class.
Use the internal macro (### to be implemented in next release ###) to check the consistency of all data included in the sheet "Equipment classes" and "Equipment instances"
Notes
Issues to be addressed in future release
## Use appropriate point & bit value descriptions to create alarm label (DI) #####
### define rules for separators

## Definitions
Subsystem TVS - Equipment classes & instances
Definitions
1-Class List
Column Class | Column Name | Column Description | Values
| Revision | Identifiy the IO revision in witch the information was added , deleted or modified | version (string)
| isAComment | Specify whether the line is a comment or not | Y or N
EQUIPMENT CLASSES
| System | Define the trigram of the system's name in which the equipment is included | XXX
| Sub-system | Define the trigram of the sub-system's name in which the equipment is included | XXX
| Class name | Short equipment name on XXX characters number (minimum 3 characters - maximum 12 characters)
| CSS Point Name | Normalized name, used within the SCADA
EXTERNAL SYSTEM DATA
| Point Name | Name of equipment point from supplier
| Point Description | Any useful documentation on the point
| Point Type | Point can be qualified as Event or Alarm. Operational are not sent to MMS, Technical and Meter are sent to MMS. Hence, supported values are | Operational Event |  | Event which are from the nominal mode of the equipment. For exmaple open/close, locked/unlocked …
|  |  | Operational Alarm |  | Alarm that are from the nominal operation mode of the equipment. For example operator changing mode which put the equipment in Alarm state or equipment changing its status triggering an alarm.
|  |  | Technical Alarm |  | Alarm that deviated from the nominal operation mode. For example all detect fault. These are not part of the system nominal behavior
|  |  | Meter |  | Event which are needed for maintenance procedures.
Command
| Frequency | Time interval between data transmissions from SCADA to MMS | Daily
Weekly
Monthly
| Data Type | Digital Input | DI | 1 | bit
|  |  | DI2 | 2 | bits
|  | Digital Output | DO | 1 | bits
|  |  | DO2 | 2 | bits
|  | Analog Input | AI | 16 | bits
|  |  | AI2 | 32 | bits
|  | Analog Output | AO | 16 | bits
|  |  | AO2 | 32 | bits
EXTERNAL SYSTEM DATA DETAILS
| SIL Level | Identify the SIL level for the equipment point which can be | SIL0
SIL2_Monitoring
SIL2_Control
| Protocol | Applicable protocol: may be Modbus or IEC104
| Operation code | Operation code needed to manage the point at protocol level
| Memory Block | TODO
DI POINT
| DI/DI2 Value = 0 | For a DI or DI2, definition of the supervised status when the value is set to 0
| DI/DI2 Value = 1 | For a DI or DI2, definition of the supervised status when the value is set to 1
| DI2 Value = 2 | For a DI2, definition of the supervised status when the value is set to 2
| DI2 Value = 3 | For a DI2, definition of the supervised status when the value is set to 3
| Default value | Default value of the equipment point
| Alarm severity | Define the alarm severity for each value with the format (value1: severity label 1, value2: severity label 2, etc) Severity labels are: - None for events - Min for Minor alarms - Maj for Major alarms - Crit for Critical alarms Example: - 0: None, 1: Maj - 0: None, 1: None
| Alarm label | This label will be presented to the operators on the HMI for english language. It consists of: CCS Point Name: DI value when=0 / DI value when=1 / …
DO POINT
| DO/DO2 Value = 0 | For a DO or DO2, definition of the supervised status when the value is set to 0
| DO/DO2 Value = 1 | For a DO or DO2, definition of the supervised status when the value is set to 1
| DO2 Value = 2 | For a DO2, definition of the supervised status when the value is set to 2
| DO2 Value = 3 | For a DO2, definition of the supervised status when the value is set to 3
| Default value | Define the default value of the equipment point
| Output duration (ms) | Give the properties of the output signal command in ms: <empty>: continuous signal integer value: temporal duration of the pulse (in ms)
| Timeout for reaction (s) | Expected response time between the command sending and the modification of the associated status
| Initial condition | Pre-condition to be checked before sending the command
| Final condition | Post-condition to be checked to make sure the command is successful
| Associated return status | Return equipment status associated with the command
AI POINT
| Unit | Give the measurement unity of the analog data
| Min value | Define the minimum value of the data
| Max value | Define the maximum value of the data
| Limit 1 (optional) | Threshold in order to add range of the supervised value between min and max values
| Limit 2 (optional) | Threshold in order to add range of the supervised value between min and max values
In the template, alarm thresholds are defined through two value limits plus a minimum value and a maximum value. As shown in the figure on the right, this defines 5 ranges for which an alarm may be defined
| Range <i> alarm severity | Define the alarm severity for a range Severity labels are: - None for events - Min for Minor alarms - Maj for Major alarms - Crit for Critical alarms
| Range <i> alarm label | Define the alarm label for a range
| Dead band | Define the tolerance of variation around a threshold
| Default value | Define the default value of the equipment point
| Alarm label | This label will be presented to the operators on the HMI. It consists on: Equipment description (displayed in HMI): under Min value / under Max value / etc.
AO POINT
| Unit | Give the measurement unity of the analog data
| Range Min value | Define the minimum range of the command value
| Range Max value | Define the maximum range of the command value
| Output duration (ms) | Give the properties of the output signal command in ms: Nothing to fill: continuous signal XXX: temporal duration of the pulse
| Timeout for reaction (s) | Response time between the command and the associated status modification on the equipment
| Initial condition | Conditions to verify before sending the command
| Final condition | Conditions to verify after the sending of the command
| Associated return status | Return equipment status associated with the command
2-Instance List
Column Class | Column Name | Column Description
| Revision | Identifiy the IO revision in witch the information was added , deleted or modified
| GBS Code | TBC
| LBS Code (LRT) | TBC
| LBS Code (QRC) | TBC
| Description | Textual description or precision about the Location/sublocation of the equipment instance
| Location | Define in a short designation the geographical location in which the equipment is based
| Sublocation | Define in a short designation the sublocation (Subsystem / Level / Building / room) in which the equipment is based
| Class name | Class name identical to the class name defined in the "1-Class List" tab
| Equipment name | Give the instance name of the equipment.
| RTU Name | Name of the concentrator (as viewed in the SCADA subsystem) for the equipment
| PLC Name | Name of the partner PLC
| InvalidVar1 | name of the first external variable used to invalidate this equipement (usually comStatus of the gateway or PRTU)
| InvalidVar2 | name of the second external variable used to invalidate this equipement (usually comStatus of the gateway or PRTU)
| InvalidVar3 | name of the third external variable used to invalidate this equipement (usually comStatus of the gateway or PRTU)

## Generation
Execute |  | To do before Generation => Check that there are no ROW filters set in the Class and instance worksheets
Tool version | #NAME?
Generation Time: | 12/21/2017 at 5:04:14 PM
Found Classes: | 1
Found Errors: | 0
Found Warnings: | 0
Not Found Classes: | 0
Generate Points
Fill Code & Index Address

## 1-Class List
|  | EQUIPMENT CLASSES |  |  |  | EXTERNAL SYSTEM DATA |  |  |  |  | EXTERNAL SYSTEM DATA DETAILS |  |  |  | DI or DI2 | [6 empty] | DO | [8 empty] | AI | [17 empty] | AO | [8 empty] | MMS | SE Engineering |  |  |  | SW Engineering | HMI details (dictionnaries)
Revision | isAComment | System | Sub-system | Class name | CSS Point Name | Point Name | Point Description | Point Type | Frequency | Data Type | SIL Level | Protocol | Operation code (FC, ASDU, ...) | Memory Block | DI or DI2 value = 0 (00) | DI or DI2 value = 1(01) | DI2 value = 2 (10) | DI2 value = 3 (11) | Default value | Alarm severity | Alarm label | DO or DO2 value = 0 (00) | DO or DO2 value = 1(01) | DO2 value = 2 (10) | DO2 value = 3 (11) | Output duration (ms) | Timeout for reaction (s) | Initial condition | Final condition | Associated return status | Unit | Min value | Max value | Limit 1 (optional) | Limit 2 (optional) | Range 1 alarm severity ] -∞,min value] | Range 1 alarm label ] -∞,min value] | Range 2 alarm severity ]min value,limit1] | Range 2 alarm label ]min value,limit1] | Range 3 alarm severity ]limit1,limit2] | Range 3 alarm label ]limit1,limit2] | Range 4 alarm severity ]limit2,max value] | Range 4 alarm label ]limit2,max value] | Range 5 alarm severity ]max value,+∞[ | Range 5 alarm label ]max value,+∞[ | Dead band | Default value | Formula | Unit | Range Min value | Range Max value | Output duration (ms) | Timeout for reaction (s) | Initial condition | Final condition | Associated return status | Formula | [Lusail] PBS code | Data Length | Index Address | Bit position | IsAnimated | Code | System (Native language) | Sub-system (Native language) | Class name (Native language) | Equipment description (displayed in HMI) (Native language) | Description (Details of description) (Native language)
A.1 | Y | This part should be filled up by System Engineering and gives the indication on how to modelize prototypes
B.1 | Y | + | UFWL |  | Under Floor Wheel Lathe
B.1 | N | UFWL | UFWL | UFWL | Main Power Supply 425V Status | Main Power Supply 425V Status | Main Power Supply 425V On / Off | Operational Alarm |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OFF | ON |  |  | OFF | 0: None, 1: None | Main Power Supply 425V Status: OFF/ON | [37 empty] | 1 | 0 | 1 | OFF | MainPowSta
B.1 | N | UFWL | UFWL | UFWL | Drive Rollers Status | Drive Rollers Status | Drive Rollers On / Off | Operational Alarm |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OFF | ON |  |  | OFF | 0: None, 1: None | Drive Rollers Status: OFF/ON | [37 empty] | 1 | 0 | 2 | OFF | DriRolSta
B.1 | N | UFWL | UFWL | UFWL | Crusher and conveyors status | Crusher and conveyors Status | Crusher and conveyors On / Off | Operational Event |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OFF | ON |  |  | OFF | 0: None, 1: None | Crusher and conveyors status: OFF/ON | [37 empty] | 1 | 0 | 3 | OFF | CruConSta
B.1 | N | UFWL | UFWL | UFWL | Smoke Extractor Status | Smoke Extractor Status | Smoke Extractor On / Off | Operational Event |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OFF | ON |  |  | OFF | 0: None, 1: None | Smoke Extractor Status: OFF/ON | [37 empty] | 1 | 0 | 6 | OFF | SmoExtSta
B.1 | N | UFWL | UFWL | UFWL | Hydraulic Status | Hydraulic Status | Hydraulic | Operational Alarm |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OFF | ON |  |  | OFF | 0: None, 1: None | Hydraulic Status: OFF/ON | [37 empty] | 1 | 0 | 7 | OFF | HydSta
B.1 | N | UFWL | UFWL | UFWL | Pneumatic Status | Pneumatic Status | Pneumatic | Operational Event |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OFF | ON |  |  | OFF | 0: None, 1: None | Pneumatic Status: OFF/ON | [37 empty] | 1 | 1 | 0 | OFF | PneuSta
B.1 | N | UFWL | UFWL | UFWL | Sharf Crusher Alarm | Sharf Crusher Alarm | Sharf Crusher | Technical Alarm |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | Normal | Alarm |  |  | Normal | 0: None, 1: Maj | Sharf Crusher Alarm: Normal/Alarm | [37 empty] | 1 | 1 | 2 | OFF | SharfCrushAla
B.1 | N | UFWL | UFWL | UFWL | Chip Conveyor 1 Alarm | Chip Conveyor 1 Alarm | Chip Conveyor 1 | Technical Alarm |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | Normal | Alarm |  |  | Normal | 0: None, 1: Maj | Chip Conveyor 1 Alarm: Normal/Alarm | [37 empty] | 1 | 1 | 3 | OFF | Chip1Ala
B.1 | N | UFWL | UFWL | UFWL | Chip Conveyor 2 Alarm | Chip Conveyor 2 Alarm | Chip Conveyor 2 | Technical Alarm |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | Normal | Alarm |  |  | Normal | 0: None, 1: Maj | Chip Conveyor 2 Alarm: Normal/Alarm | [37 empty] | 1 | 1 | 4 | OFF | Chip2Ala
B.1 | N | UFWL | UFWL | UFWL | Emergency Stop Alarm | Emergency Stop Alarm | Emergency Stop | Operational Alarm |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | Normal | Alarm |  |  | Normal | 0: None, 1: Crit | Emergency Stop Alarm: Normal/Alarm | [37 empty] | 1 | 1 | 6 | OFF | EmeStopAla
B.1 | N | UFWL | UFWL | UFWL | Smoke Extractor System Alarm | Smoke Extractor System Alarm | Smoke Extractor System | Technical Alarm |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | Normal | Alarm |  |  | Normal | 0: None, 1: Maj | Smoke Extractor System Alarm: Normal/Alarm | [37 empty] | 1 | 2 | 7 | OFF | SmoExtSysAla
B.1 | N | UFWL | UFWL | UFWL | Lathe Lubrification System Alarm | Lathe Lubrification System Alarm | Lathe Lubrification System | Technical Alarm |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | Normal | Alarm |  |  | Normal | 0: None, 1: Crit | Lathe Lubrification System Alarm: Normal/Alarm | [37 empty] | 1 | 2 | 0 | OFF | LatLubSysAla
B.1 | N | UFWL | UFWL | UFWL | Lathe Out of Service Alarm | Lathe Out of Service Alarm | Lathe Out of Service | Technical Alarm |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | Normal | Alarm |  |  | Normal | 0: None, 1: Crit | Lathe Out of Service Alarm: Normal/Alarm | [37 empty] | 1 | 2 | 4 | OFF | LatOutSerAla
B.1 | N | UFWL | UFWL | UFWL | Roller drive Alarm | Roller drive Alarm | Roller drive Alarm | Technical Alarm |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | Normal | Alarm |  |  | Normal | 0: None, 1: Crit | Roller drive Alarm: Normal/Alarm | [37 empty] | 1 | 2 | 5 | OFF | RolDriAla
B.1 | N | UFWL | UFWL | UFWL | Heater Alarm | Heater Alarm | Heater Alarm | Technical Alarm |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | Normal | Alarm |  |  | Normal | 0: None, 1: Min | Heater Alarm: Normal/Alarm | [37 empty] | 1 | 2 | 7 | OFF | HeaAla
B.1 | N | UFWL | UFWL | UFWL | Pneumatic Alarm | Pneumatic Alarm | Pneumatic Alarm | Technical Alarm |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | Normal | Alarm |  |  | Normal | 0: None, 1: Crit | Pneumatic Alarm: Normal/Alarm | [37 empty] | 1 | 3 | 0 | OFF | PneuAla
B.1 | N | UFWL | UFWL | UFWL | Oil Level Alarm | Oil Level Alarm | Oil Level Alarm | Technical Alarm |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | Normal | Alarm |  |  | Normal | 0: None, 1: Crit | Oil Level Alarm: Normal/Alarm | [37 empty] | 1 | 3 | 1 | OFF | OilLevAla
B.1 | N | UFWL | UFWL | UFWL | Oil temperature Alarm | Oil temperature Alarm | Oil temperature Alarm | Technical Alarm |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | Normal | Alarm |  |  | Normal | 0: None, 1: Maj | Oil temperature Alarm: Normal/Alarm | [37 empty] | 1 | 3 | 2 | OFF | OilTemAla
B.1 | N | UFWL | UFWL | UFWL | Oil Filter Alarm | Oil Filter Alarm | Oil Filter Alarm | Technical Alarm |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | Normal | Alarm |  |  | Normal | 0: None, 1: Maj | Oil Filter Alarm: Normal/Alarm | [37 empty] | 1 | 3 | 3 | OFF | OilFilAla
B.1 | N | UFWL | UFWL | UFWL | Lathe In Service Status | Lathe In Service Status | Lathe In Service Status | Operational Event |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OFF | ON |  |  | OFF | 0: None, 1: None | Lathe In Service Status: OFF/ON | [37 empty] | 1 | 6 | 1 | OFF | LatSerSta
B.1 | N | UFWL | UFWL | UFWL | Lathe In Maintenance Status | Lathe In Maintenance Status | Lathe In Maintenance Status | Operational Event |  | DI | SIL0 | MODBUS-RTU | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OFF | ON |  |  | OFF | 0: None, 1: None | Lathe In Maintenance Status: OFF/ON | [37 empty] | 1 | 6 | 2 | OFF | LatMainSta

## 2-Instance List
|  | LRT/QRC DESIGNATION |  |  |  | EQUIPMENT INSTANCES | [9 empty] | PRTU Configuration
Revision | isAComment | [Lusail] GBS Code | [Lusail] LBS Code LRT Designation Code | [Lusail] LBS Code QRC Designation Code | Description | Location | Sublocation | Class name | Equipment name | RTU Name | PLC Name | InvalidVar1 | InvalidVar2 | InvalidVar3 | Avalanche Condition | Instance Id | External System Name | Device Unit Id | FEP Name | FEP instance Id | Short name | hvId | SCADA Transfert function (Internal THALES) | Address | Description (Native language) | ToBeInstantiated
A.1 | Y |  |  |  |  | ROOT Location | [19 empty] | N
A.1 | Y |  |  |  | root node | DPT |  | Hierarchy | [17 empty] | N
A.1 | Y |  |  |  |  | Depot building OMF05 | [19 empty] | N
A.1 | Y |  |  |  |  | Hierarchy and locations (everything but equipments) | [19 empty] | N
A.1 | Y |  |  |  | root node |  |  | Hierarchy |  | - | [10 empty] | - | OMF05 |  |  |  | N
A.1 | Y |  |  |  | Under floor wheel lafe | OMF05 | DBP | FunctionalCat | DBP | - | [10 empty] | - | OMF05:UFWL |  |  |  | N
A.1 | Y |  |  |  | ModBus Terminal Unit | OMF09 |  | FunctionalCat | MBT | - | [10 empty] | - |  |  |  |  | N
A.1 | Y |  |  |  |  | PRTU | [19 empty] | N
A.1 | Y |  |  |  | Modbus interface | OMF09 | MBT | RTU | Daccom | OMF09_RTU | [5 empty] | 1 | RTU | 1 |  |  | DacCom IEC |  |  |  |  | N
A.1 | Y |  |  |  |  | Under Floor Wheel Lafe (UFWL) | [19 empty] | N
A.1 | N |  |  |  | UFWL | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | OMF09_RTU | [5 empty] | 2 | UFWL | 1 |  |  | &UFWL_1 | UFWL_OMF05_UFWL_Room_UFWL_1 |  |  |  | Y

## 3-Class Mapping
Class name | Prototype | Aggregate name | Object type | isAComment | Scstype | Abbreviated class name
UFWL | LusailHK:LusUfwlUfwl |  |  | N | LusUfwlUfwlType | UFWL

## 4-External Variables
Class name | iopath | vetype | ve_basename | description | address | EVGroup | Concentrator Suffix | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
UFWL | dciUFWL-MainPowSta:dac | DEIV | MainPowSta | Main Power Supply 425V On / Off | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-DriRolSta:dac | DEIV | DriRolSta | Drive Rollers On / Off | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-CruConSta:dac | DEIV | CruConSta | Crusher and conveyors On / Off | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-SmoExtSta:dac | DEIV | SmoExtSta | Smoke Extractor On / Off | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-HydSta:dac | DEIV | HydSta | Hydraulic | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-PneuSta:dac | DEIV | PneuSta | Pneumatic | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-SharfCrushAla:dac | DEIV | SharfCrushAla | Sharf Crusher | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-Chip1Ala:dac | DEIV | Chip1Ala | Chip Conveyor 1 | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-Chip2Ala:dac | DEIV | Chip2Ala | Chip Conveyor 2 | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-EmeStopAla:dac | DEIV | EmeStopAla | Emergency Stop | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-SmoExtSysAla:dac | DEIV | SmoExtSysAla | Smoke Extractor System | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-LatLubSysAla:dac | DEIV | LatLubSysAla | Lathe Lubrification System | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-LatOutSerAla:dac | DEIV | LatOutSerAla | Lathe Out of Service | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-RolDriAla:dac | DEIV | RolDriAla | Roller drive Alarm | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-HeaAla:dac | DEIV | HeaAla | Heater Alarm | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-PneuAla:dac | DEIV | PneuAla | Pneumatic Alarm | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-OilLevAla:dac | DEIV | OilLevAla | Oil Level Alarm | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-OilTemAla:dac | DEIV | OilTemAla | Oil temperature Alarm | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-OilFilAla:dac | DEIV | OilFilAla | Oil Filter Alarm | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-LatSerSta:dac | DEIV | LatSerSta | Lathe In Service Status | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
UFWL | dciUFWL-LatMainSta:dac | DEIV | LatMainSta | Lathe In Maintenance Status | $VOID | VEE_SCADA1 | _S0 | 0 | [6 empty] | N
Note on F1: HILDEBERT Rene: To be calculated from the instance List

## 4-External Variables - SIL0
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
Note on F1: HILDEBERT Rene: To be calculated from the instance List

## 4-External Variables - SIL2MON
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
Note on F1: HILDEBERT Rene: To be calculated from the instance List

## 4-External Variables - SIL2CON
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
Note on F1: HILDEBERT Rene: To be calculated from the instance List

## 10-PLC Points
row_id | concentrator | location | sub_location | class_name | eqp_name | instance_id | attribute_code | sil_channel | operation_type | point_address | start_bit | nb_bits | Warning | Error | PRTU Name | SWC Name | Daccom Source File | Daccom Variable Type | FC Code / ASDU Type | Daccom Type Num | Protocol Address | Start Bit | Nb Bits | Daccom External Variable Name | field1 | field2 | field3 | field4 | field5 | External Var Comment
1 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | MainPowSta | SIL0 | MODBUS:4:Read:Input Registers | 20020 | 1 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20020 | 1 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1MainPowSta | 4 |  |  | 0 | $ComStatus , , | #Main Power Supply 425V On / Off
2 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | DriRolSta | SIL0 | MODBUS:4:Read:Input Registers | 20020 | 2 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20020 | 2 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1DriRolSta | 4 |  |  | 0 | $ComStatus , , | #Drive Rollers On / Off
3 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | CruConSta | SIL0 | MODBUS:4:Read:Input Registers | 20020 | 3 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20020 | 3 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1CruConSta | 4 |  |  | 0 | $ComStatus , , | #Crusher and conveyors On / Off
4 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | SmoExtSta | SIL0 | MODBUS:4:Read:Input Registers | 20020 | 6 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20020 | 6 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1SmoExtSta | 4 |  |  | 0 | $ComStatus , , | #Smoke Extractor On / Off
5 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | HydSta | SIL0 | MODBUS:4:Read:Input Registers | 20020 | 7 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20020 | 7 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1HydSta | 4 |  |  | 0 | $ComStatus , , | #Hydraulic
6 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | PneuSta | SIL0 | MODBUS:4:Read:Input Registers | 20021 | 0 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20021 | 0 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1PneuSta | 4 |  |  | 0 | $ComStatus , , | #Pneumatic
7 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | SharfCrushAla | SIL0 | MODBUS:4:Read:Input Registers | 20021 | 2 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20021 | 2 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1SharfCrushAla | 4 |  |  | 0 | $ComStatus , , | #Sharf Crusher
8 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | Chip1Ala | SIL0 | MODBUS:4:Read:Input Registers | 20021 | 3 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20021 | 3 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1Chip1Ala | 4 |  |  | 0 | $ComStatus , , | #Chip Conveyor 1
9 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | Chip2Ala | SIL0 | MODBUS:4:Read:Input Registers | 20021 | 4 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20021 | 4 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1Chip2Ala | 4 |  |  | 0 | $ComStatus , , | #Chip Conveyor 2
10 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | EmeStopAla | SIL0 | MODBUS:4:Read:Input Registers | 20021 | 6 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20021 | 6 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1EmeStopAla | 4 |  |  | 0 | $ComStatus , , | #Emergency Stop
11 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | SmoExtSysAla | SIL0 | MODBUS:4:Read:Input Registers | 20022 | 7 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20022 | 7 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1SmoExtSysAla | 4 |  |  | 0 | $ComStatus , , | #Smoke Extractor System
12 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | LatLubSysAla | SIL0 | MODBUS:4:Read:Input Registers | 20022 | 0 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20022 | 0 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1LatLubSysAla | 4 |  |  | 0 | $ComStatus , , | #Lathe Lubrification System
13 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | LatOutSerAla | SIL0 | MODBUS:4:Read:Input Registers | 20022 | 4 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20022 | 4 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1LatOutSerAla | 4 |  |  | 0 | $ComStatus , , | #Lathe Out of Service
14 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | RolDriAla | SIL0 | MODBUS:4:Read:Input Registers | 20022 | 5 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20022 | 5 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1RolDriAla | 4 |  |  | 0 | $ComStatus , , | #Roller drive Alarm
15 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | HeaAla | SIL0 | MODBUS:4:Read:Input Registers | 20022 | 7 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20022 | 7 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1HeaAla | 4 |  |  | 0 | $ComStatus , , | #Heater Alarm
16 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | PneuAla | SIL0 | MODBUS:4:Read:Input Registers | 20023 | 0 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20023 | 0 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1PneuAla | 4 |  |  | 0 | $ComStatus , , | #Pneumatic Alarm
17 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | OilLevAla | SIL0 | MODBUS:4:Read:Input Registers | 20023 | 1 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20023 | 1 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1OilLevAla | 4 |  |  | 0 | $ComStatus , , | #Oil Level Alarm
18 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | OilTemAla | SIL0 | MODBUS:4:Read:Input Registers | 20023 | 2 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20023 | 2 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1OilTemAla | 4 |  |  | 0 | $ComStatus , , | #Oil temperature Alarm
19 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | OilFilAla | SIL0 | MODBUS:4:Read:Input Registers | 20023 | 3 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20023 | 3 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1OilFilAla | 4 |  |  | 0 | $ComStatus , , | #Oil Filter Alarm
20 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | LatSerSta | SIL0 | MODBUS:4:Read:Input Registers | 20026 | 1 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20026 | 1 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1LatSerSta | 4 |  |  | 0 | $ComStatus , , | #Lathe In Service Status
21 | OMF09_RTU | UFWL:OMF05 | UFWL_Room | UFWL | UFWL_1 | 2 | LatMainSta | SIL0 | MODBUS:4:Read:Input Registers | 20026 | 2 | 1 |  |  | OMF05-SIL0 | UFWL | OMF09_RTU.dat | DEIV | 4 | 1 | 20026 | 2 | 1 | deiUFWLOMF05UFWL_RoomUFWL_1LatMainSta | 4 |  |  | 0 | $ComStatus , , | #Lathe In Maintenance Status
-END-

## A-Validation Data list
RTU_Protocol_Operation_Code | Memory_Block | RTU_Protocol | Operation Code List | Association with Memory Block | RTU_Undefined_Operation_Code | RTU_Undefined_Operation_Code | RTU_Modbus_Operation_Code | Modbus_Memory_Block | RTU_IEC104_Operation_Code | IEC104_Memory_Block | RTU_Data_Check_Function | RTU_Data_Translation_Function | Bit_Position
MODBUS:1:Read:Coils | MODBUS:MEMBLOCK01 | MODBUS-TCP | SE_RTU_Modbus_Operation_Code | SE_RTU_Modbus_Table |  |  | MODBUS:1:Read:Coils | MODBUS:MEMBLOCK01 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | cfRANGE | tfNOT | 0
MODBUS:2:Read:Discrete Inputs | MODBUS:MEMBLOCK02 | MODBUS-RTU | SE_RTU_Modbus_Operation_Code | SE_RTU_Modbus_Table |  |  | MODBUS:2:Read:Discrete Inputs | MODBUS:MEMBLOCK02 | IEC104:M_DP_NA_1 | IEC104:MEMBLOCK01 |  | tfLIN | 1
MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | IEC60870-5-104 | SE_RTU_IEC104_Operation_Code | SE_RTU_IEC104_Table |  |  | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 |  | BTL32 | 2
MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | IEC60870-5-101 | SE_RTU_IEC104_Operation_Code | SE_RTU_IEC104_Table |  |  | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | IEC104:M_ME_NB_1 | IEC104:MEMBLOCK01 |  | LTB16 | 3
MODBUS:5:Write:Coil | MODBUS:MEMBLOCK01 | DNP3.0 | SE_RTU_Undefined_Operation_Code | SE_RTU_Undefined_Table |  |  | MODBUS:5:Write:Coil | MODBUS:MEMBLOCK01 | IEC104:M_ME_NC_1 | IEC104:MEMBLOCK01 |  | USHORT | 4
MODBUS:6:Write:Holding Register | MODBUS:MEMBLOCK03 | BACNET-TCP | SE_RTU_Undefined_Operation_Code | SE_RTU_Undefined_Table |  |  | MODBUS:6:Write:Holding Register | MODBUS:MEMBLOCK03 | IEC104:M_IT_NA_1 | IEC104:MEMBLOCK01 |  |  | 5
MODBUS:15:Write:Coils | MODBUS:MEMBLOCK01 |  | SE_RTU_Undefined_Operation_Code | SE_RTU_Undefined_Table |  |  | MODBUS:15:Write:Coils | MODBUS:MEMBLOCK01 | IEC104:M_SP_TB_1 | IEC104:MEMBLOCK01 |  |  | 6
MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [5 empty] | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | IEC104:M_DP_TB_1 | IEC104:MEMBLOCK01 |  |  | 7
IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SC_NA_1 | IEC104:MEMBLOCK01 |  |  | 8
IEC104:M_DP_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 |  |  | 9
IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_RC_NA_1 | IEC104:MEMBLOCK01 |  |  | 10
IEC104:M_ME_NB_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SE_NA_1 | IEC104:MEMBLOCK01 |  |  | 11
IEC104:M_ME_NC_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SE_NB_1 | IEC104:MEMBLOCK01 |  |  | 12
IEC104:M_IT_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SE_NC_1 | IEC104:MEMBLOCK01 |  |  | 13
IEC104:M_SP_TB_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_IC_NA_1 | IEC104:MEMBLOCK01 |  |  | 14
IEC104:M_DP_TB_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_CI_NA_1 | IEC104:MEMBLOCK01 |  |  | 15
IEC104:C_SC_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_RD_NA_1 | IEC104:MEMBLOCK01 |  |  | 16
IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 17
IEC104:C_RC_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 18
IEC104:C_SE_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 19
IEC104:C_SE_NB_1 | IEC104:MEMBLOCK01 | [11 empty] | 20
IEC104:C_SE_NC_1 | IEC104:MEMBLOCK01 | [11 empty] | 21
IEC104:C_IC_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 22
IEC104:C_CI_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 23
IEC104:C_RD_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 24
25
|  | Check of Validation Lists | [10 empty] | 26
|  | PLC Protocol | Available Operation Code | [9 empty] | 27
|  | IEC60870-5-104 | IEC104:M_ME_NA_1 | [9 empty] | 28
|  | MODBUS-RTU | MODBUS:4:Read:Input Registers | [9 empty] | 29
30
31
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
Note on E1: BERNARD Olivier: This column identifies the list to the associated operation codes. This list is defined through a name (Excel Formula name)

## B-Address Qty
FC / Class Name | UFWL
MODBUS:1:Read:Coils | 40;1000
MODBUS:2:Read:Discrete Inputs | 40;5000
MODBUS:3:Read:Holding Registers | 10;10000
MODBUS:4:Read:Input Registers | 10;20000
MODBUS:5:Write:Coil | 20;1000
MODBUS:6:Write:Holding Register | 20;10000
MODBUS:15:Write:Coils | 20;1000
MODBUS:16:Write:Holding Registers | 20;10000
IEC104:M_SP_NA_1 | 40;1000
IEC104:M_DP_NA_1 | 40;4000
IEC104:M_ME_NA_1 | 40;7000
IEC104:M_ME_NB_1 | 40;10000
IEC104:M_ME_NC_1 | 40;13000
IEC104:M_IT_NA_1 | 40;16000
IEC104:M_SP_TB_1 | 40;17000
IEC104:M_DP_TB_1 | 40;20000
IEC104:C_SC_NA_1 | 20;23000
IEC104:C_DC_NA_1 | 20;25000
IEC104:C_RC_NA_1 | 20;27000
IEC104:C_SE_NA_1 | 20;28000
IEC104:C_SE_NB_1 | 20;29000
IEC104:C_SE_NC_1 | 20;30000
IEC104:C_IC_NA_1 | 20;31000
IEC104:C_CI_NA_1
IEC104:C_RD_NA_1