## Revision
Revision
Date | Version | Author | Observations
42418 | v0 | C.CAMARA | Creation (from v4.2) | CHANGE TO :
42476 | A- | C.CAMARA | Updated version following QVDC Comment
42901 | A1 | T.MARTINEZ | Updated version with new templates
43053 | A2 | T. MARTINEZ | -Updated to v0.36 version - Updated with new IO from MLJ partners
43111 | A2 | T. MARTINEZ | -Generated SW code
43149 | B- | T. MARTINEZ | Align on V0.37 template
43288 |  | HK Team | 1-Class List Changed code capitalization to match with Java naming rules. 10-PLC points Change attribute_code capitalization to match with Code in class list
Partners view

## Introduction
Introduction
For all ICD relative to equipment monitoring & control , this ECI (Equipment Classes & Instances) file template must be used as appendix to define: - the equipment classes, from an I/O point of view - all instances relative to each class
Recommandations
1 | Use one ECI file for each ICD document (one ICD=one subsystem)
2 | Do not change the organisation of the ECI file:
- Sheet "Equipment classes" : define all classes for the relative subsystem (see meaning of each field in the "Definitions" sheet)
- Sheet "Equipment instances" : define all instances for the relative subsystem (see meaning of each field in the "Definitions" sheet)
3 | For each sheet, do not change the organisation of the sheet (does not remove any column) in order to be able to use the standard export/import tools
4 | Create the necessary number of classes: for example, if similar equipment have different numbers of DI, DO, AI, create one class for each case
5 | Define, if possible, contiguous addresses for equipments/points within the same class.
Use the internal macro (### to be implemented in next release ###) to check the consistency of all data included in the sheet "Equipment classes" and "Equipment instances"
Notes
Issues to be addressed in future release
## Use appropriate point & bit value descriptions to create alarm label (DI) #####
### define rules for separators

## Definitions
Subsystem TVS - Equipment classes & instances
Definitions
1-Class List
Column Class | Column Name | Column Description | Values
| Revision | Identifiy the IO revision in witch the information was added , deleted or modified | version (string)
| isAComment | Specify whether the line is a comment or not | Y or N
EQUIPMENT CLASSES
| System | Define the trigram of the system's name in which the equipment is included | XXX
| Sub-system | Define the trigram of the sub-system's name in which the equipment is included | XXX
| Class name | Short equipment name on XXX characters number (minimum 3 characters - maximum 12 characters)
| CSS Point Name | Normalized name, used within the SCADA
EXTERNAL SYSTEM DATA
| Point Name | Name of equipment point from supplier
| Point Description | Any useful documentation on the point
| Point Type | Point can be qualified as Event or Alarm. Operational are not sent to MMS, Technical and Meter are sent to MMS. Hence, supported values are | Operational Event |  | Event which are from the nominal mode of the equipment. For exmaple open/close, locked/unlocked …
|  |  | Operational Alarm |  | Alarm that are from the nominal operation mode of the equipment. For example operator changing mode which put the equipment in Alarm state or equipment changing its status triggering an alarm.
|  |  | Technical Alarm |  | Alarm that deviated from the nominal operation mode. For example all detect fault. These are not part of the system nominal behavior
|  |  | Meter |  | Event which are needed for maintenance procedures.
Command
| Frequency | Time interval between data transmissions from SCADA to MMS | Daily
Weekly
Monthly
| Data Type | Digital Input | DI | 1 | bit
|  |  | DI2 | 2 | bits
|  | Digital Output | DO | 1 | bits
|  |  | DO2 | 2 | bits
|  | Analog Input | AI | 16 | bits
|  |  | AI2 | 32 | bits
|  | Analog Output | AO | 16 | bits
|  |  | AO2 | 32 | bits
EXTERNAL SYSTEM DATA DETAILS
| SIL Level | Identify the SIL level for the equipment point which can be | SIL0
SIL2_Monitoring
SIL2_Control
| Protocol | Applicable protocol: may be Modbus or IEC104
| Operation code | Operation code needed to manage the point at protocol level
| Memory Block | TODO
DI POINT
| DI/DI2 Value = 0 | For a DI or DI2, definition of the supervised status when the value is set to 0
| DI/DI2 Value = 1 | For a DI or DI2, definition of the supervised status when the value is set to 1
| DI2 Value = 2 | For a DI2, definition of the supervised status when the value is set to 2
| DI2 Value = 3 | For a DI2, definition of the supervised status when the value is set to 3
| Default value | Default value of the equipment point
| Alarm severity | Define the alarm severity for each value with the format (value1: severity label 1, value2: severity label 2, etc) Severity labels are: - None for events - Min for Minor alarms - Maj for Major alarms - Crit for Critical alarms Example: - 0: None, 1: Maj - 0: None, 1: None
| Alarm label | This label will be presented to the operators on the HMI for english language. It consists of: CCS Point Name: DI value when=0 / DI value when=1 / …
DO POINT
| DO/DO2 Value = 0 | For a DO or DO2, definition of the supervised status when the value is set to 0
| DO/DO2 Value = 1 | For a DO or DO2, definition of the supervised status when the value is set to 1
| DO2 Value = 2 | For a DO2, definition of the supervised status when the value is set to 2
| DO2 Value = 3 | For a DO2, definition of the supervised status when the value is set to 3
| Default value | Define the default value of the equipment point
| Output duration (ms) | Give the properties of the output signal command in ms: <empty>: continuous signal integer value: temporal duration of the pulse (in ms)
| Timeout for reaction (s) | Expected response time between the command sending and the modification of the associated status
| Initial condition | Pre-condition to be checked before sending the command
| Final condition | Post-condition to be checked to make sure the command is successful
| Associated return status | Return equipment status associated with the command
AI POINT
| Unit | Give the measurement unity of the analog data
| Min value | Define the minimum value of the data
| Max value | Define the maximum value of the data
| Limit 1 (optional) | Threshold in order to add range of the supervised value between min and max values
| Limit 2 (optional) | Threshold in order to add range of the supervised value between min and max values
In the template, alarm thresholds are defined through two value limits plus a minimum value and a maximum value. As shown in the figure on the right, this defines 5 ranges for which an alarm may be defined
| Range <i> alarm severity | Define the alarm severity for a range Severity labels are: - None for events - Min for Minor alarms - Maj for Major alarms - Crit for Critical alarms
| Range <i> alarm label | Define the alarm label for a range
| Dead band | Define the tolerance of variation around a threshold
| Default value | Define the default value of the equipment point
| Alarm label | This label will be presented to the operators on the HMI. It consists on: Equipment description (displayed in HMI): under Min value / under Max value / etc.
AO POINT
| Unit | Give the measurement unity of the analog data
| Range Min value | Define the minimum range of the command value
| Range Max value | Define the maximum range of the command value
| Output duration (ms) | Give the properties of the output signal command in ms: Nothing to fill: continuous signal XXX: temporal duration of the pulse
| Timeout for reaction (s) | Response time between the command and the associated status modification on the equipment
| Initial condition | Conditions to verify before sending the command
| Final condition | Conditions to verify after the sending of the command
| Associated return status | Return equipment status associated with the command
2-Instance List
Column Class | Column Name | Column Description
| Revision | Identifiy the IO revision in witch the information was added , deleted or modified
| GBS Code | TBC
| LBS Code (LRT) | TBC
| LBS Code (QRC) | TBC
| Description | Textual description or precision about the Location/sublocation of the equipment instance
| Location | Define in a short designation the geographical location in which the equipment is based
| Sublocation | Define in a short designation the sublocation (Subsystem / Level / Building / room) in which the equipment is based
| Class name | Class name identical to the class name defined in the "1-Class List" tab
| Equipment name | Give the instance name of the equipment.
| RTU Name | Name of the concentrator (as viewed in the SCADA subsystem) for the equipment
| PLC Name | Name of the partner PLC
| InvalidVar1 | name of the first external variable used to invalidate this equipement (usually comStatus of the gateway or PRTU)
| InvalidVar2 | name of the second external variable used to invalidate this equipement (usually comStatus of the gateway or PRTU)
| InvalidVar3 | name of the third external variable used to invalidate this equipement (usually comStatus of the gateway or PRTU)

## Generation
Execute |  | To do before Generation => Check that there are no ROW filters set in the Class and instance worksheets
Tool version | #NAME?
Generation Time: | 1/11/2018 at 11:20:07 AM
Found Classes: | 2
Found Errors: | 0
Found Warnings: | 0
Not Found Classes: | 0
Generate Points
Fill Code & Index Address

## 1-Class List
|  | EQUIPMENT CLASSES |  |  |  | EXTERNAL SYSTEM DATA |  |  |  |  | EXTERNAL SYSTEM DATA DETAILS |  |  |  | DI or DI2 | [6 empty] | DO | [8 empty] | AI | [17 empty] | AO | [8 empty] | MMS | SE Engineering |  |  |  | SW Engineering | HMI details (dictionnaries)
Revision | isAComment | System | Sub-system | Class name | CSS Point Name | Point Name | Point Description | Point Type | Frequency | Data Type | SIL Level | Protocol | Operation code (FC, ASDU, ...) | Memory Block | DI or DI2 value = 0 (00) | DI or DI2 value = 1(01) | DI2 value = 2 (10) | DI2 value = 3 (11) | Default value | Alarm severity | Alarm label | DO or DO2 value = 0 (00) | DO or DO2 value = 1(01) | DO2 value = 2 (10) | DO2 value = 3 (11) | Output duration (ms) | Timeout for reaction (s) | Initial condition | Final condition | Associated return status | Unit | Min value | Max value | Limit 1 (optional) | Limit 2 (optional) | Range 1 alarm severity ] -∞,min value] | Range 1 alarm label ] -∞,min value] | Range 2 alarm severity ]min value,limit1] | Range 2 alarm label ]min value,limit1] | Range 3 alarm severity ]limit1,limit2] | Range 3 alarm label ]limit1,limit2] | Range 4 alarm severity ]limit2,max value] | Range 4 alarm label ]limit2,max value] | Range 5 alarm severity ]max value,+∞[ | Range 5 alarm label ]max value,+∞[ | Dead band | Default value | Formula | Unit | Range Min value | Range Max value | Output duration (ms) | Timeout for reaction (s) | Initial condition | Final condition | Associated return status | Formula | [Lusail] PBS code | Data Length | Index Address | Bit position | IsAnimated | Code | System (Native language) | Sub-system (Native language) | Class name (Native language) | Equipment description (displayed in HMI) (Native language) | Description (Details of description) (Native language)
A.1 | Y | This part should be filled up by System Engineering and gives the indication on how to modelize prototypes
A.1 | Y | + |  |  | Mobile Lifting Jacks
A.1 | N | MLJ | MLJ | MLJ | MLJ In Service Status | MLJ In Service Status | MLC In Service | Event | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | No | Yes |  |  | No | 0: Min, 1: Min | MLJ In Service Status: No/Yes | [37 empty] | 1 | 0 | 0 |  | ServSta
A.2 | N | MLJ | MLJ | MLJ | MLJ Rising | MLJ Rising | MLJ Rising | Event | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | No | Yes |  |  | No | 0: Min, 1: Min | MLJ Rising: No/Yes | [37 empty] | 1 | 0 | 1 |  | MljRis
A.2 | N | MLJ | MLJ | MLJ | MLJ Descending | MLJ Descending | MLJ Descending | Event | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | No | Yes |  |  | No | 0: Min, 1: Min | MLJ Descending: No/Yes | [37 empty] | 1 | 0 | 2 |  | MljDes
A.2 | N | MLJ | MLJ | MLJ | MLJ in Setting Mode | MLJ Setting Mode | MLJ in Setting Mode | Operational Alarm | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | No | Yes |  |  | No | 0: Min, 1: Min | MLJ in Setting Mode: No/Yes | [37 empty] | 1 | 0 | 3 |  | MljSetMod
A.2 | N | MLJ | MLJ | MLJ | MLJ in Synchronisation Mode | MLJ Synchronisation Mode | MLJ in Synchronisation mode | Operational Alarm | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | No | Yes |  |  | No | 0: Min, 1: Min | MLJ in Synchronisation Mode: No/Yes | [37 empty] | 1 | 0 | 4 |  | MljSyncMod
A.1 | N | MLJ | MLJ | MLJ | Emergency Stop Alarm | Emergency Stop Alarm | Emergency Stop | Operational Alarm | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | Emergency Stop Alarm: Reset/Alarm | [37 empty] | 1 | 0 | 5 |  | EmrStopAla
A.1 | N | MLJ | MLJ | MLJ | MLJ Out of Service Alarm | MLJ Out of Service Alarm | MLC Out of Service | Operational Alarm | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Min | MLJ Out of Service Alarm: Reset/Alarm | [37 empty] | 1 | 0 | 6 |  | MljOutOfServ
A.2 | N | MLJ | MLJ | MLJ | MLJ First Upper Limit | MLJ First Upper Limit | First Upper Limit | Operational Alarm | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | No | Yes |  |  | No | 0: Min, 1: Min | MLJ First Upper Limit: No/Yes | [37 empty] | 1 | 0 | 7 |  | MljFirUpLimi
A.2 | N | MLJ | MLJ | MLJ | MLJ First Lower Limit | MLJ First Lower Limit | First Lower Limit | Operational Alarm | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | No | Yes |  |  | No | 0: Min, 1: Min | MLJ First Lower Limit: No/Yes | [37 empty] | 1 | 0 | 8 |  | MljFirLowLimi
A.2 | N | MLJ | MLJ | MLJ | MLJ All in Park Position | MLJ All in Park Position | All Parked | Operational Alarm | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | No | Yes |  |  | No | 0: Min, 1: Min | MLJ All in Park Position: No/Yes | [37 empty] | 1 | 0 | 9 |  | MljAllParkPos
A.2 | N | MLJ | MLJ | MLJ | Main/Console Power Supply Status | Main/Console Power Supply Status | Main Power Supply Alarm | Maintenance Alarm | MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | ON | 0: Min, 1: crit | Main/Console Power Supply Status: Reset/Alarm | [37 empty] | 1 | 0 | 10 |  | MaiPowSupSta
A.1 | N | MLJ | MLJ | MLJ | Main Controle Console Alarm | Main Controle Console Alarm | MCC Alarm | Maintenance Alarm | MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | Main Controle Console Alarm: Reset/Alarm | [37 empty] | 1 | 0 | 11 |  | MaiConConsAla
A.2 | N | MLJ | MLJ | MLJ | MCC Circuit Breaker Tripped | MCC Circuit Breaker Tripped | MCC Circuit Breaker Alarm | Maintenance Alarm | MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | MCC Circuit Breaker Tripped: Reset/Alarm | [37 empty] | 1 | 0 | 12 |  | MccCircBreaTrip
A.2 | N | MLJ | MLJ | MLJ | MCC Internal Communication Alarm | MCC Internal Communication Alarm | MCC Internal Communication Alarm | Maintenance Alarm | MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | MCC Internal Communication Alarm: Reset/Alarm | [37 empty] | 1 | 0 | 13 |  | MccInterComAla
A.2 | N | MLJ | MLJ | MLJ | MCC Contactor Alarm | MCC Contactor Alarm | MCC Contactor Alarm | Maintenance Alarm | MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | MCC Contactor Alarm: Reset/Alarm | [37 empty] | 1 | 0 | 14 |  | MccContaAla
A.2 | N | MLJ | MLJ | MLJ | MCC EDM Circuit Alarm | MCC EDM Circuit Alarm | All relays are not tripped following a push of Emergency button | Maintenance Alarm | MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | MCC EDM Circuit Alarm: Reset/Alarm | [37 empty] | 1 | 0 | 15 |  | MccEdmCircAla
A.2 | N | MLJ | MLJ | MLJ | MCC Pushbutton stuck Alarm | MCC Pushbutton Alarm | MCC Pushbutton Alarm | Maintenance Alarm | MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | MCC Pushbutton stuck Alarm: Reset/Alarm | [37 empty] | 1 | 1 | 0 |  | MccPushStuckAla
A.2 | N | MLJ | MLJ | MLJ | MCC Battery Alarm | MCC Battery Alarm | MCC Battery Empty | Maintenance Alarm | MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | MCC Battery Alarm: Reset/Alarm | [37 empty] | 1 | 1 | 1 |  | MccBattAla
A.1 | Y | + |  |  | Jacks (For J-1 to J-14)
A.1 | N | MLJ | MLJ | JCK | Availability | Availability | Power Supply MLC 1 | Operational Alarm | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Unplugged | Plugged |  |  | Unplugged | 0: Min, 1: Crit | Availability: Unplugged/Plugged | [37 empty] | 1 | 2 | 0 |  | Avail
A.2 | N | MLJ | MLJ | JCK | Lower limit | Lower limit | Park Position MLC 1 | Event | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | No | Yes |  |  | No | 0: Min, 1: Min | Lower limit: No/Yes | [37 empty] | 1 | 2 | 1 |  | LowLim
A.2 | N | MLJ | MLJ | JCK | Upper limit | Upper limit | Top Position MLC 1 | Event | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | No | Yes |  |  | No | 0: Min, 1: Min | Upper limit: No/Yes | [37 empty] | 1 | 2 | 2 |  | UpLim
A.2 | N | MLJ | MLJ | JCK | Load Available | Load Available | Load on MLC 1 | Operational Alarm | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | No | Yes |  |  | No | 0: Min, 1: Maj | Load Available: No/Yes | [37 empty] | 1 | 2 | 3 |  | LoadAvai
A.2 | N | MLJ | MLJ | JCK | Jacks Rising | Jacks Rising | Rising MLC 1 | Operational Alarm | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | No | Yes |  |  | No | 0: Min, 1: Maj | Jacks Rising: No/Yes | [37 empty] | 1 | 2 | 4 |  | JackRis
A.2 | N | MLJ | MLJ | JCK | Jacks Descending | Jacks Descending | Descending MLC 1 | Operational Alarm | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | No | Yes |  |  | No | 0: Min, 1: Maj | Jacks Descending: No/Yes | [37 empty] | 1 | 2 | 5 |  | JackDesc
A.2 | N | MLJ | MLJ | JCK | Jacks Standing on Floor | Jacks Standing on Floor | Standing on Floor MLC 1 | Operational Alarm | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | No | Yes |  |  | Yes | 0: Min, 1: Min | Jacks Standing on Floor: No/Yes | [37 empty] | 1 | 2 | 6 |  | JackStanOnFloo
A.2 | N | MLJ | MLJ | JCK | Jacks Height Value | Jacks Height Value | Height value MLC 1 | Operational Alarm | SCADA / MMS | AI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | [16 empty] | HEX | -9999 | 9999 | [13 empty] | 0000 | [11 empty] | 16 | 3 | 0 |  | JackHeighVal
A.2 | N | MLJ | MLJ | JCK | Jacks Running Time MIN | Jacks Running Time MIN | Running Time MIN MLC 1 | Maintenance Alarm | MMS | AI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | [16 empty] | HEX | 0 | 9999 | [13 empty] | 0000 | [11 empty] | 16 | 4 | 0 |  | JackRunTimMin
A.2 | N | MLJ | MLJ | JCK | Jacks Running Time HOUR | Jacks Running Time HOUR | Running Time HOUR MLC 1 | Maintenance Alarm | MMS | AI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | [16 empty] | HEX | 0 | 9999 | [13 empty] | 0000 | [11 empty] | 16 | 5 | 0 |  | JackRunTimHour
A.1 | N | MLJ | MLJ | JCK | Jacks Alarm | Jacks Alarm | Alarm MLC 1 | Operational Alarm | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | Jacks Alarm: Reset/Alarm | [37 empty] | 1 | 2 | 7 |  | JackAla
A.1 | N | MLJ | MLJ | JCK | Jacks in service Status | Jacks in service Status | In service MLC 1 | Operational Alarm | SCADA / MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | No | Yes |  |  | No | 0: Min, 1: Min | Jacks in service Status: No/Yes | [37 empty] | 1 | 2 | 8 |  | JackServStatus
A.2 | N | MLJ | MLJ | JCK | Jacks Emergency Stop Alarm | Jacks Emergency Stop Alarm | Emergency Stop MLC 1 | Maintenance Alarm | MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | Jacks Emergency Stop Alarm: Reset/Alarm | [37 empty] | 1 | 2 | 9 |  | JackEmerStopAla
A.2 | N | MLJ | MLJ | JCK | Jacks Nut Fault Alarm | Jacks Nut Fault Alarm | Nut Fault MLC 1 | Maintenance Alarm | MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | Jacks Nut Fault Alarm: Reset/Alarm | [37 empty] | 1 | 2 | 10 |  | JackNutFaulAla
A.2 | N | MLJ | MLJ | JCK | Jacks Obstruction Alarm | Jacks Obstruction Alarm | Jacks Obstruction MLC 1 | Maintenance Alarm | MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | Jacks Obstruction Alarm: Reset/Alarm | [37 empty] | 1 | 2 | 11 |  | JackObstAla
A.2 | N | MLJ | MLJ | JCK | Jacks Load missing Alam | Jacks Load missing Alam | Jacks Load missing MLC 1 | Maintenance Alarm | MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | Jacks Load missing Alam: Reset/Alarm | [37 empty] | 1 | 2 | 12 |  | JackLoadMissAla
A.2 | N | MLJ | MLJ | JCK | Jacks Impulse Sensor Alarm | Jacks Impulse Sensor Alarm | Jacks Impulse Sensor MLC 1 | Maintenance Alarm | MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | Jacks Impulse Sensor Alarm: Reset/Alarm | [37 empty] | 1 | 2 | 13 |  | JackImpSensAla
A.2 | N | MLJ | MLJ | JCK | Jacks Motorprotection Alarm | Jacks Motorprotection Alarm | Jacks Motorprotection MLC 1 | Maintenance Alarm | MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | Jacks Motorprotection Alarm: Reset/Alarm | [37 empty] | 1 | 2 | 14 |  | JackMotorAla
A.2 | N | MLJ | MLJ | JCK | Jacks Synchronisation Alarm | Jacks Synchronisation Alarm | Jacks Synchronisation MLC 1 | Maintenance Alarm | MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | Jacks Synchronisation Alarm: Reset/Alarm | [37 empty] | 1 | 2 | 15 |  | JackSyncAla
A.2 | N | MLJ | MLJ | JCK | Jacks Contactor Alarm | Jacks Contactor Alarm | Jacks Contactor MLC 1 | Maintenance Alarm | MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | Jacks Contactor Alarm: Reset/Alarm | [37 empty] | 1 | 6 | 0 |  | JackContAla
A.2 | N | MLJ | MLJ | JCK | Jacks Floor Contact Alarm | Jacks Floor Contact Alarm | Jacks Floor Contact MLC 1 | Maintenance Alarm | MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | Jacks Floor Contact Alarm: Reset/Alarm | [37 empty] | 1 | 6 | 1 |  | JackFlooContAla
A.2 | N | MLJ | MLJ | JCK | Jacks Synchronisation Sensores Differences | Jacks Synchronisation Sensores Differences | Jacks Synch. Sensor Diff. Values MLC 1 | Maintenance Alarm | MMS | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Reset | Alarm |  |  | Reset | 0: Min, 1: Maj | Jacks Synchronisation Sensores Differences: Reset/Alarm | [37 empty] | 1 | 6 | 2 |  | JackSyncSensDiff
Note on H20: Jason Law: All relays are not tripped following a push of an Emergency push button
Note on AG31: Thibault MARTINEZ: Is there any formula to get back the value or just hex to decimal ? Szabolcs Kozma: Just hex to decimal, but if you would like than we can send it diretly in decimal format

## 2-Instance List
|  | LRT/QRC DESIGNATION |  |  |  | EQUIPMENT INSTANCES | [9 empty] | PRTU Configuration
Revision | isAComment | [Lusail] GBS Code | [Lusail] LBS Code LRT Designation Code | [Lusail] LBS Code QRC Designation Code | Description | Location | Sublocation | Class name | Equipment name | RTU Name | PLC Name | InvalidVar1 | InvalidVar2 | InvalidVar3 | Avalanche Condition | Instance Id | External System Name | Device Unit Id | FEP Name | FEP instance Id | Short name | hvId | SCADA Transfert function (Internal THALES) | Address | Description (Native language) | ToBeInstantiated
A.1 | Y |  |  |  |  | ROOT Location | [19 empty] | N
A.1 | Y |  |  |  | root node | DPT |  | Hierarchy | [17 empty] | N
A.1 | Y |  |  |  |  | Depot building OMF05 | [19 empty] | N
A.1 | Y |  |  |  |  | Hierarchy and locations (everything but equipments) | [19 empty] | N
A.1 | Y |  |  |  | root node |  |  | Hierarchy |  | - | [10 empty] | - | OMF05 |  |  |  | N
A.1 | Y |  |  |  | Mobile Lifting Jack | OMF05 | MLJ | FunctionalCat | MLJ | - | [10 empty] | - | OMF05:MLJ |  |  |  | N
A.1 | Y |  |  |  | ModBus Terminal Unit | OMF09 |  | FunctionalCat | MBT | - | [10 empty] | - |  |  |  |  | N
A.1 | Y |  |  |  |  | PRTU | [19 empty] | N
A.1 | Y |  |  |  | Modbus interface | OMF09 | MBT | RTU | Daccom | OMF09_RTU | [5 empty] | 1 | MLJ | 1 |  |  | DacCom IEC |  |  |  |  | N
A.1 | Y |  |  |  |  | Mobile Lifting Jack (MLJ) | [19 empty] | N
A.1 | N |  |  |  | Mobile Lifting Jack | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | OMF09_RTU | [5 empty] | 2 | MLJ | 1 |  |  | &MLJ-1 | MLJ_OMF05_MLJ_Room_MLJ_1 |  |  |  | Y
A.1 | Y |  |  |  |  | Jacks (JCK) | [19 empty] | N
A.1 | N |  |  |  | Jacks 1 | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | OMF09_RTU | [5 empty] | 3 | JCK | 1 |  |  | &JCK-1 | JCK_OMF05_MLJ_Room_JCK_1 |  |  |  | Y
A.1 | N |  |  |  | Jacks 2 | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | OMF09_RTU | [5 empty] | 4 | JCK | 1 |  |  | &JCK-2 | JCK_OMF05_MLJ_Room_JCK_2 |  |  |  | Y
A.1 | N |  |  |  | Jacks 3 | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | OMF09_RTU | [5 empty] | 5 | JCK | 1 |  |  | &JCK-3 | JCK_OMF05_MLJ_Room_JCK_3 |  |  |  | Y
A.1 | N |  |  |  | Jacks 4 | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | OMF09_RTU | [5 empty] | 6 | JCK | 1 |  |  | &JCK-4 | JCK_OMF05_MLJ_Room_JCK_4 |  |  |  | Y
A.1 | N |  |  |  | Jacks 5 | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | OMF09_RTU | [5 empty] | 7 | JCK | 1 |  |  | &JCK-5 | JCK_OMF05_MLJ_Room_JCK_5 |  |  |  | Y
A.1 | N |  |  |  | Jacks 6 | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | OMF09_RTU | [5 empty] | 8 | JCK | 1 |  |  | &JCK-6 | JCK_OMF05_MLJ_Room_JCK_6 |  |  |  | Y
A.1 | N |  |  |  | Jacks 7 | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | OMF09_RTU | [5 empty] | 9 | JCK | 1 |  |  | &JCK-7 | JCK_OMF05_MLJ_Room_JCK_7 |  |  |  | Y
A.1 | N |  |  |  | Jacks 8 | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | OMF09_RTU | [5 empty] | 10 | JCK | 1 |  |  | &JCK-8 | JCK_OMF05_MLJ_Room_JCK_8 |  |  |  | Y
A.1 | N |  |  |  | Jacks 9 | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | OMF09_RTU | [5 empty] | 11 | JCK | 1 |  |  | &JCK-9 | JCK_OMF05_MLJ_Room_JCK_9 |  |  |  | Y
A.1 | N |  |  |  | Jacks 10 | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | OMF09_RTU | [5 empty] | 12 | JCK | 1 |  |  | &JCK-10 | JCK_OMF05_MLJ_Room_JCK_10 |  |  |  | Y
A.1 | N |  |  |  | Jacks 11 | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | OMF09_RTU | [5 empty] | 13 | JCK | 1 |  |  | &JCK-11 | JCK_OMF05_MLJ_Room_JCK_11 |  |  |  | Y
A.1 | N |  |  |  | Jacks 12 | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | OMF09_RTU | [5 empty] | 14 | JCK | 1 |  |  | &JCK-12 | JCK_OMF05_MLJ_Room_JCK_12 |  |  |  | Y
A.1 | N |  |  |  | Jacks 13 | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | OMF09_RTU | [5 empty] | 15 | JCK | 1 |  |  | &JCK-13 | JCK_OMF05_MLJ_Room_JCK_13 |  |  |  | Y
A.1 | N |  |  |  | Jacks 14 | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | OMF09_RTU | [5 empty] | 16 | JCK | 1 |  |  | &JCK-14 | JCK_OMF05_MLJ_Room_JCK_14 |  |  |  | Y

## 3-Class Mapping
Class name | Prototype | Aggregate name | Object type | isAComment | Scstype | Abbreviated Class name
MLJ | LusailHK:LusMljMlj |  |  | N | LusMljMljType | MLJ
JCK | LusailHK:LusMljJck |  |  | N | LusMljJckType | JCK

## 4-External Variables
Class name | iopath | vetype | ve_basename | description | address | EVGroup | Concentrator Suffix | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
MLJ | dciMLJ-ServSta:dac | DEIV | ServSta | MLC In Service | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
MLJ | dciMLJ-MljRis:dac | DEIV | MljRis | MLJ Rising | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
MLJ | dciMLJ-MljDes:dac | DEIV | MljDes | MLJ Descending | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
MLJ | dciMLJ-MljSetMod:dac | DEIV | MljSetMod | MLJ in Setting Mode | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
MLJ | dciMLJ-MljSyncMod:dac | DEIV | MljSyncMod | MLJ in Synchronisation mode | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
MLJ | dciMLJ-EmrStopAla:dac | DEIV | EmrStopAla | Emergency Stop | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
MLJ | dciMLJ-MljOutOfServ:dac | DEIV | MljOutOfServ | MLC Out of Service | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
MLJ | dciMLJ-MljFirUpLimi:dac | DEIV | MljFirUpLimi | First Upper Limit | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
MLJ | dciMLJ-MljFirLowLimi:dac | DEIV | MljFirLowLimi | First Lower Limit | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
MLJ | dciMLJ-MljAllParkPos:dac | DEIV | MljAllParkPos | All Parked | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
MLJ | dciMLJ-MaiPowSupSta:dac | DEIV | MaiPowSupSta | Main Power Supply Alarm | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
MLJ | dciMLJ-MaiConConsAla:dac | DEIV | MaiConConsAla | MCC Alarm | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
MLJ | dciMLJ-MccCircBreaTrip:dac | DEIV | MccCircBreaTrip | MCC Circuit Breaker Alarm | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
MLJ | dciMLJ-MccInterComAla:dac | DEIV | MccInterComAla | MCC Internal Communication Alarm | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
MLJ | dciMLJ-MccContaAla:dac | DEIV | MccContaAla | MCC Contactor Alarm | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
MLJ | dciMLJ-MccEdmCircAla:dac | DEIV | MccEdmCircAla | All relays are not tripped following a push of Emergency button | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
MLJ | dciMLJ-MccPushStuckAla:dac | DEIV | MccPushStuckAla | MCC Pushbutton Alarm | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
MLJ | dciMLJ-MccBattAla:dac | DEIV | MccBattAla | MCC Battery Empty | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-Avail:dac | DEIV | Avail | Power Supply MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-LowLim:dac | DEIV | LowLim | Park Position MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-UpLim:dac | DEIV | UpLim | Top Position MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-LoadAvai:dac | DEIV | LoadAvai | Load on MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-JackRis:dac | DEIV | JackRis | Rising MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-JackDesc:dac | DEIV | JackDesc | Descending MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-JackStanOnFloo:dac | DEIV | JackStanOnFloo | Standing on Floor MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | aciJCK-JackHeighVal:aac | AEIV | JackHeighVal | Height value MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | aciJCK-JackRunTimMin:aac | AEIV | JackRunTimMin | Running Time MIN MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | aciJCK-JackRunTimHour:aac | AEIV | JackRunTimHour | Running Time HOUR MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-JackAla:dac | DEIV | JackAla | Alarm MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-JackServStatus:dac | DEIV | JackServStatus | In service MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-JackEmerStopAla:dac | DEIV | JackEmerStopAla | Emergency Stop MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-JackNutFaulAla:dac | DEIV | JackNutFaulAla | Nut Fault MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-JackObstAla:dac | DEIV | JackObstAla | Jacks Obstruction MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-JackLoadMissAla:dac | DEIV | JackLoadMissAla | Jacks Load missing MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-JackImpSensAla:dac | DEIV | JackImpSensAla | Jacks Impulse Sensor MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-JackMotorAla:dac | DEIV | JackMotorAla | Jacks Motorprotection MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-JackSyncAla:dac | DEIV | JackSyncAla | Jacks Synchronisation MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-JackContAla:dac | DEIV | JackContAla | Jacks Contactor MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-JackFlooContAla:dac | DEIV | JackFlooContAla | Jacks Floor Contact MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
JCK | dciJCK-JackSyncSensDiff:dac | DEIV | JackSyncSensDiff | Jacks Synch. Sensor Diff. Values MLC 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
Note on F1: HILDEBERT Rene: To be calculated from the instance List
Note on E17: Jason Law: All relays are not tripped following a push of an Emergency push button

## 4-External Variables - SIL0
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
MLJ
MLJ
MLJ
MLJ
MLJ
MLJ
MLJ
MLJ
MLJ
MLJ
MLJ
MLJ
MLJ
MLJ
MLJ
MLJ
MLJ
MLJ
JCK
JCK
JCK
JCK
JCK
JCK
JCK
JCK
JCK
JCK
JCK
JCK
JCK
JCK
JCK
JCK
JCK
JCK
JCK
JCK
JCK
JCK
Note on F1: HILDEBERT Rene: To be calculated from the instance List

## 4-External Variables - SIL2MON
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
Note on F1: HILDEBERT Rene: To be calculated from the instance List

## 4-External Variables - SIL2CON
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
Note on F1: HILDEBERT Rene: To be calculated from the instance List

## 10-PLC Points
row_id | concentrator | location | sub_location | class_name | eqp_name | instance_id | attribute_code | sil_channel | operation_type | point_address | start_bit | nb_bits | Warning | Error | PRTU Name | SWC Name | Daccom Source File | Daccom Variable Type | FC Code / ASDU Type | Daccom Type Num | Protocol Address | Start Bit | Nb Bits | Daccom External Variable Name | field1 | field2 | field3 | field4 | field5 | External Var Comment
1 | OMF09_RTU | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | 2 | ServSta | SIL0 | MODBUS:3:Read:Holding Registers | 2001 | 1 | 1 |  |  | OMF05-SIL0 | MLJ | OMF09_RTU.dat | DEIV | 3 | 1 | 10020 | 0 | 1 | deiMLJOMF05MLJ_RoomMLJ_1ServSta | 4 |  |  | 0 | $ComStatus , , | #MLC In Service
2 | OMF09_RTU | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | 2 | MljRis | SIL0 | MODBUS:3:Read:Holding Registers | 2001 | 2 | 1 |  |  | OMF05-SIL0 | MLJ | OMF09_RTU.dat | DEIV | 3 | 1 | 10020 | 1 | 1 | deiMLJOMF05MLJ_RoomMLJ_1MLJRis | 4 |  |  | 0 | $ComStatus , , | #MLJ Rising
3 | OMF09_RTU | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | 2 | MljDes | SIL0 | MODBUS:3:Read:Holding Registers | 2001 | 3 | 1 |  |  | OMF05-SIL0 | MLJ | OMF09_RTU.dat | DEIV | 3 | 1 | 10020 | 2 | 1 | deiMLJOMF05MLJ_RoomMLJ_1MLJDes | 4 |  |  | 0 | $ComStatus , , | #MLJ Descending
4 | OMF09_RTU | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | 2 | MljSetMod | SIL0 | MODBUS:3:Read:Holding Registers | 2001 | 4 | 1 |  |  | OMF05-SIL0 | MLJ | OMF09_RTU.dat | DEIV | 3 | 1 | 10020 | 3 | 1 | deiMLJOMF05MLJ_RoomMLJ_1MLJSetMod | 4 |  |  | 0 | $ComStatus , , | #MLJ in Setting Mode
5 | OMF09_RTU | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | 2 | MljSyncMod | SIL0 | MODBUS:3:Read:Holding Registers | 2001 | 5 | 1 |  |  | OMF05-SIL0 | MLJ | OMF09_RTU.dat | DEIV | 3 | 1 | 10020 | 4 | 1 | deiMLJOMF05MLJ_RoomMLJ_1MLJSyncMod | 4 |  |  | 0 | $ComStatus , , | #MLJ in Synchronisation mode
6 | OMF09_RTU | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | 2 | EmrStopAla | SIL0 | MODBUS:3:Read:Holding Registers | 2001 | 6 | 1 |  |  | OMF05-SIL0 | MLJ | OMF09_RTU.dat | DEIV | 3 | 1 | 10020 | 5 | 1 | deiMLJOMF05MLJ_RoomMLJ_1EmrStopAla | 4 |  |  | 0 | $ComStatus , , | #Emergency Stop
7 | OMF09_RTU | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | 2 | MljOutOfServ | SIL0 | MODBUS:3:Read:Holding Registers | 2001 | 0 | 1 |  |  | OMF05-SIL0 | MLJ | OMF09_RTU.dat | DEIV | 3 | 1 | 10020 | 6 | 1 | deiMLJOMF05MLJ_RoomMLJ_1MLJOutOfServ | 4 |  |  | 0 | $ComStatus , , | #MLC Out of Service
8 | OMF09_RTU | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | 2 | MljFirUpLimi | SIL0 | MODBUS:3:Read:Holding Registers | 2001 | 0 | 1 |  |  | OMF05-SIL0 | MLJ | OMF09_RTU.dat | DEIV | 3 | 1 | 10020 | 7 | 1 | deiMLJOMF05MLJ_RoomMLJ_1MLJFirUpLimi | 4 |  |  | 0 | $ComStatus , , | #First Upper Limit
9 | OMF09_RTU | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | 2 | MljFirLowLimi | SIL0 | MODBUS:3:Read:Holding Registers | 2001 | 0 | 1 |  |  | OMF05-SIL0 | MLJ | OMF09_RTU.dat | DEIV | 3 | 1 | 10020 | 8 | 1 | deiMLJOMF05MLJ_RoomMLJ_1MLJFirLowLimi | 4 |  |  | 0 | $ComStatus , , | #First Lower Limit
10 | OMF09_RTU | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | 2 | MljAllParkPos | SIL0 | MODBUS:3:Read:Holding Registers | 2001 | 7 | 1 |  |  | OMF05-SIL0 | MLJ | OMF09_RTU.dat | DEIV | 3 | 1 | 10020 | 9 | 1 | deiMLJOMF05MLJ_RoomMLJ_1MLJAllParkPos | 4 |  |  | 0 | $ComStatus , , | #All Parked
11 | OMF09_RTU | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | 2 | MaiPowSupSta | SIL0 | MODBUS:3:Read:Holding Registers | 2001 | 8 | 1 |  |  | OMF05-SIL0 | MLJ | OMF09_RTU.dat | DEIV | 3 | 1 | 10020 | 10 | 1 | deiMLJOMF05MLJ_RoomMLJ_1MaiPowSupSta | 4 |  |  | 0 | $ComStatus , , | #Main Power Supply Alarm
12 | OMF09_RTU | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | 2 | MaiConConsAla | SIL0 | MODBUS:3:Read:Holding Registers | 2001 | 9 | 1 |  |  | OMF05-SIL0 | MLJ | OMF09_RTU.dat | DEIV | 3 | 1 | 10020 | 11 | 1 | deiMLJOMF05MLJ_RoomMLJ_1MaiConConsAla | 4 |  |  | 0 | $ComStatus , , | #MCC Alarm
13 | OMF09_RTU | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | 2 | MccCircBreaTrip | SIL0 | MODBUS:3:Read:Holding Registers | 2001 | 10 | 1 |  |  | OMF05-SIL0 | MLJ | OMF09_RTU.dat | DEIV | 3 | 1 | 10020 | 12 | 1 | deiMLJOMF05MLJ_RoomMLJ_1MCCCircBreaTrip | 4 |  |  | 0 | $ComStatus , , | #MCC Circuit Breaker Alarm
14 | OMF09_RTU | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | 2 | MccInterComAla | SIL0 | MODBUS:3:Read:Holding Registers | 2001 | 11 | 1 |  |  | OMF05-SIL0 | MLJ | OMF09_RTU.dat | DEIV | 3 | 1 | 10020 | 13 | 1 | deiMLJOMF05MLJ_RoomMLJ_1MCCInterComAla | 4 |  |  | 0 | $ComStatus , , | #MCC Internal Communication Alarm
15 | OMF09_RTU | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | 2 | MccContaAla | SIL0 | MODBUS:3:Read:Holding Registers | 2001 | 12 | 1 |  |  | OMF05-SIL0 | MLJ | OMF09_RTU.dat | DEIV | 3 | 1 | 10020 | 14 | 1 | deiMLJOMF05MLJ_RoomMLJ_1MCCContaAla | 4 |  |  | 0 | $ComStatus , , | #MCC Contactor Alarm
16 | OMF09_RTU | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | 2 | MccEdmCircAla | SIL0 | MODBUS:3:Read:Holding Registers | 2001 | 13 | 1 |  |  | OMF05-SIL0 | MLJ | OMF09_RTU.dat | DEIV | 3 | 1 | 10020 | 15 | 1 | deiMLJOMF05MLJ_RoomMLJ_1MCCEdmCircAla | 4 |  |  | 0 | $ComStatus , , | #All relays are not tripped following a push of an Emergency push button.
17 | OMF09_RTU | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | 2 | MccPushStuckAla | SIL0 | MODBUS:3:Read:Holding Registers | 2001 | 14 | 1 |  |  | OMF05-SIL0 | MLJ | OMF09_RTU.dat | DEIV | 3 | 1 | 10021 | 0 | 1 | deiMLJOMF05MLJ_RoomMLJ_1MCCPushStuckAla | 4 |  |  | 0 | $ComStatus , , | #MCC Pushbutton Alarm
18 | OMF09_RTU | MLJ:OMF05 | MLJ_Room | MLJ | MLJ_1 | 2 | MccBattAla | SIL0 | MODBUS:3:Read:Holding Registers | 2001 | 15 | 1 |  |  | OMF05-SIL0 | MLJ | OMF09_RTU.dat | DEIV | 3 | 1 | 10021 | 1 | 1 | deiMLJOMF05MLJ_RoomMLJ_1MCCBattAla | 4 |  |  | 0 | $ComStatus , , | #MCC Battery Empty
19 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | Avail | SIL0 | MODBUS:3:Read:Holding Registers | 2011 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10032 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_1Avail | 4 |  |  | 0 | $ComStatus , , | #Power Supply MLC 1
20 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | LowLim | SIL0 | MODBUS:3:Read:Holding Registers | 2011 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10032 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_1LowLim | 4 |  |  | 0 | $ComStatus , , | #Park Position MLC 1
21 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | UpLim | SIL0 | MODBUS:3:Read:Holding Registers | 2011 | 2 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10032 | 2 | 1 | deiJCKOMF05MLJ_RoomJCK_1UpLim | 4 |  |  | 0 | $ComStatus , , | #Top Position MLC 1
22 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | LoadAvai | SIL0 | MODBUS:3:Read:Holding Registers | 2011 | 3 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10032 | 3 | 1 | deiJCKOMF05MLJ_RoomJCK_1LoadAvai | 4 |  |  | 0 | $ComStatus , , | #Load on MLC 1
23 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | JackRis | SIL0 | MODBUS:3:Read:Holding Registers | 2011 | 4 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10032 | 4 | 1 | deiJCKOMF05MLJ_RoomJCK_1JackRis | 4 |  |  | 0 | $ComStatus , , | #Rising MLC 1
24 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | JackDesc | SIL0 | MODBUS:3:Read:Holding Registers | 2011 | 5 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10032 | 5 | 1 | deiJCKOMF05MLJ_RoomJCK_1JackDesc | 4 |  |  | 0 | $ComStatus , , | #Descending MLC 1
25 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | JackStanOnFloo | SIL0 | MODBUS:3:Read:Holding Registers | 2011 | 6 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10032 | 6 | 1 | deiJCKOMF05MLJ_RoomJCK_1JackStanOnFloo | 4 |  |  | 0 | $ComStatus , , | #Standing on Floor MLC 1
26 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | JackHeighVal | SIL0 | MODBUS:3:Read:Holding Registers | 2013 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10033 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_1JackHeighVal | 4 |  |  | 0 | $ComStatus , , | #Height value MLC 1
27 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | JackRunTimMin | SIL0 | MODBUS:3:Read:Holding Registers | 2014 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10034 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_1JackRunTimMin | 4 |  |  | 0 | $ComStatus , , | #Running Time MIN MLC 1
28 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | JackRunTimHour | SIL0 | MODBUS:3:Read:Holding Registers | 2015 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10035 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_1JackRunTimHour | 4 |  |  | 0 | $ComStatus , , | #Running Time HOUR MLC 1
29 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | JackAla | SIL0 | MODBUS:3:Read:Holding Registers | 2011 | 7 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10032 | 7 | 1 | deiJCKOMF05MLJ_RoomJCK_1JackAla | 4 |  |  | 0 | $ComStatus , , | #Alarm MLC 1
30 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | JackServStatus | SIL0 | MODBUS:3:Read:Holding Registers | 2011 | 8 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10032 | 8 | 1 | deiJCKOMF05MLJ_RoomJCK_1JackServStatus | 4 |  |  | 0 | $ComStatus , , | #In service MLC 1
31 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | JackEmerStopAla | SIL0 | MODBUS:3:Read:Holding Registers | 2011 | 9 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10032 | 9 | 1 | deiJCKOMF05MLJ_RoomJCK_1JackEmerStopAla | 4 |  |  | 0 | $ComStatus , , | #Emergency Stop MLC 1
32 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | JackNutFaulAla | SIL0 | MODBUS:3:Read:Holding Registers | 2011 | 10 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10032 | 10 | 1 | deiJCKOMF05MLJ_RoomJCK_1JackNutFaulAla | 4 |  |  | 0 | $ComStatus , , | #Nut Fault MLC 1
33 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | JackObstAla | SIL0 | MODBUS:3:Read:Holding Registers | 2011 | 11 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10032 | 11 | 1 | deiJCKOMF05MLJ_RoomJCK_1JackObstAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Obstruction MLC 1
34 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | JackLoadMissAla | SIL0 | MODBUS:3:Read:Holding Registers | 2011 | 12 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10032 | 12 | 1 | deiJCKOMF05MLJ_RoomJCK_1JackLoadMissAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Load missing MLC 1
35 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | JackImpSensAla | SIL0 | MODBUS:3:Read:Holding Registers | 2011 | 13 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10032 | 13 | 1 | deiJCKOMF05MLJ_RoomJCK_1JackImpSensAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Impulse Sensor MLC 1
36 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | JackMotorAla | SIL0 | MODBUS:3:Read:Holding Registers | 2011 | 14 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10032 | 14 | 1 | deiJCKOMF05MLJ_RoomJCK_1JackMotorAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Motorprotection MLC 1
37 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | JackSyncAla | SIL0 | MODBUS:3:Read:Holding Registers | 2011 | 15 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10032 | 15 | 1 | deiJCKOMF05MLJ_RoomJCK_1JackSyncAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Synchronisation MLC 1
38 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | JackContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2012 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10036 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_1JackContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Contactor MLC 1
39 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_1 | 3 | JackFlooContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2012 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10036 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_1JackFlooContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Floor Contact MLC 1
40 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | Avail | SIL0 | MODBUS:3:Read:Holding Registers | 2021 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10042 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_2Avail | 4 |  |  | 0 | $ComStatus , , | #Power Supply MLC 1
41 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | LowLim | SIL0 | MODBUS:3:Read:Holding Registers | 2021 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10042 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_2LowLim | 4 |  |  | 0 | $ComStatus , , | #Park Position MLC 1
42 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | UpLim | SIL0 | MODBUS:3:Read:Holding Registers | 2021 | 2 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10042 | 2 | 1 | deiJCKOMF05MLJ_RoomJCK_2UpLim | 4 |  |  | 0 | $ComStatus , , | #Top Position MLC 1
43 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | LoadAvai | SIL0 | MODBUS:3:Read:Holding Registers | 2021 | 3 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10042 | 3 | 1 | deiJCKOMF05MLJ_RoomJCK_2LoadAvai | 4 |  |  | 0 | $ComStatus , , | #Load on MLC 1
44 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | JackRis | SIL0 | MODBUS:3:Read:Holding Registers | 2021 | 4 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10042 | 4 | 1 | deiJCKOMF05MLJ_RoomJCK_2JackRis | 4 |  |  | 0 | $ComStatus , , | #Rising MLC 1
45 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | JackDesc | SIL0 | MODBUS:3:Read:Holding Registers | 2021 | 5 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10042 | 5 | 1 | deiJCKOMF05MLJ_RoomJCK_2JackDesc | 4 |  |  | 0 | $ComStatus , , | #Descending MLC 1
46 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | JackStanOnFloo | SIL0 | MODBUS:3:Read:Holding Registers | 2021 | 6 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10042 | 6 | 1 | deiJCKOMF05MLJ_RoomJCK_2JackStanOnFloo | 4 |  |  | 0 | $ComStatus , , | #Standing on Floor MLC 1
47 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | JackHeighVal | SIL0 | MODBUS:3:Read:Holding Registers | 2023 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10043 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_2JackHeighVal | 4 |  |  | 0 | $ComStatus , , | #Height value MLC 1
48 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | JackRunTimMin | SIL0 | MODBUS:3:Read:Holding Registers | 2024 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10044 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_2JackRunTimMin | 4 |  |  | 0 | $ComStatus , , | #Running Time MIN MLC 1
49 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | JackRunTimHour | SIL0 | MODBUS:3:Read:Holding Registers | 2025 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10045 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_2JackRunTimHour | 4 |  |  | 0 | $ComStatus , , | #Running Time HOUR MLC 1
50 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | JackAla | SIL0 | MODBUS:3:Read:Holding Registers | 2021 | 7 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10042 | 7 | 1 | deiJCKOMF05MLJ_RoomJCK_2JackAla | 4 |  |  | 0 | $ComStatus , , | #Alarm MLC 1
51 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | JackServStatus | SIL0 | MODBUS:3:Read:Holding Registers | 2021 | 8 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10042 | 8 | 1 | deiJCKOMF05MLJ_RoomJCK_2JackServStatus | 4 |  |  | 0 | $ComStatus , , | #In service MLC 1
52 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | JackEmerStopAla | SIL0 | MODBUS:3:Read:Holding Registers | 2021 | 9 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10042 | 9 | 1 | deiJCKOMF05MLJ_RoomJCK_2JackEmerStopAla | 4 |  |  | 0 | $ComStatus , , | #Emergency Stop MLC 1
53 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | JackNutFaulAla | SIL0 | MODBUS:3:Read:Holding Registers | 2021 | 10 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10042 | 10 | 1 | deiJCKOMF05MLJ_RoomJCK_2JackNutFaulAla | 4 |  |  | 0 | $ComStatus , , | #Nut Fault MLC 1
54 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | JackObstAla | SIL0 | MODBUS:3:Read:Holding Registers | 2021 | 11 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10042 | 11 | 1 | deiJCKOMF05MLJ_RoomJCK_2JackObstAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Obstruction MLC 1
55 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | JackLoadMissAla | SIL0 | MODBUS:3:Read:Holding Registers | 2021 | 12 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10042 | 12 | 1 | deiJCKOMF05MLJ_RoomJCK_2JackLoadMissAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Load missing MLC 1
56 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | JackImpSensAla | SIL0 | MODBUS:3:Read:Holding Registers | 2021 | 13 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10042 | 13 | 1 | deiJCKOMF05MLJ_RoomJCK_2JackImpSensAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Impulse Sensor MLC 1
57 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | JackMotorAla | SIL0 | MODBUS:3:Read:Holding Registers | 2021 | 14 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10042 | 14 | 1 | deiJCKOMF05MLJ_RoomJCK_2JackMotorAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Motorprotection MLC 1
58 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | JackSyncAla | SIL0 | MODBUS:3:Read:Holding Registers | 2021 | 15 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10042 | 15 | 1 | deiJCKOMF05MLJ_RoomJCK_2JackSyncAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Synchronisation MLC 1
59 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | JackContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2022 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10046 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_2JackContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Contactor MLC 1
60 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_2 | 4 | JackFlooContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2022 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10046 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_2JackFlooContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Floor Contact MLC 1
61 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | Avail | SIL0 | MODBUS:3:Read:Holding Registers | 2031 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10052 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_3Avail | 4 |  |  | 0 | $ComStatus , , | #Power Supply MLC 1
62 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | LowLim | SIL0 | MODBUS:3:Read:Holding Registers | 2031 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10052 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_3LowLim | 4 |  |  | 0 | $ComStatus , , | #Park Position MLC 1
63 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | UpLim | SIL0 | MODBUS:3:Read:Holding Registers | 2031 | 2 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10052 | 2 | 1 | deiJCKOMF05MLJ_RoomJCK_3UpLim | 4 |  |  | 0 | $ComStatus , , | #Top Position MLC 1
64 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | LoadAvai | SIL0 | MODBUS:3:Read:Holding Registers | 2031 | 3 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10052 | 3 | 1 | deiJCKOMF05MLJ_RoomJCK_3LoadAvai | 4 |  |  | 0 | $ComStatus , , | #Load on MLC 1
65 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | JackRis | SIL0 | MODBUS:3:Read:Holding Registers | 2031 | 4 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10052 | 4 | 1 | deiJCKOMF05MLJ_RoomJCK_3JackRis | 4 |  |  | 0 | $ComStatus , , | #Rising MLC 1
66 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | JackDesc | SIL0 | MODBUS:3:Read:Holding Registers | 2031 | 5 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10052 | 5 | 1 | deiJCKOMF05MLJ_RoomJCK_3JackDesc | 4 |  |  | 0 | $ComStatus , , | #Descending MLC 1
67 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | JackStanOnFloo | SIL0 | MODBUS:3:Read:Holding Registers | 2031 | 6 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10052 | 6 | 1 | deiJCKOMF05MLJ_RoomJCK_3JackStanOnFloo | 4 |  |  | 0 | $ComStatus , , | #Standing on Floor MLC 1
68 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | JackHeighVal | SIL0 | MODBUS:3:Read:Holding Registers | 2033 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10053 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_3JackHeighVal | 4 |  |  | 0 | $ComStatus , , | #Height value MLC 1
69 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | JackRunTimMin | SIL0 | MODBUS:3:Read:Holding Registers | 2034 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10054 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_3JackRunTimMin | 4 |  |  | 0 | $ComStatus , , | #Running Time MIN MLC 1
70 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | JackRunTimHour | SIL0 | MODBUS:3:Read:Holding Registers | 2035 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10055 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_3JackRunTimHour | 4 |  |  | 0 | $ComStatus , , | #Running Time HOUR MLC 1
71 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | JackAla | SIL0 | MODBUS:3:Read:Holding Registers | 2031 | 7 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10052 | 7 | 1 | deiJCKOMF05MLJ_RoomJCK_3JackAla | 4 |  |  | 0 | $ComStatus , , | #Alarm MLC 1
72 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | JackServStatus | SIL0 | MODBUS:3:Read:Holding Registers | 2031 | 8 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10052 | 8 | 1 | deiJCKOMF05MLJ_RoomJCK_3JackServStatus | 4 |  |  | 0 | $ComStatus , , | #In service MLC 1
73 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | JackEmerStopAla | SIL0 | MODBUS:3:Read:Holding Registers | 2031 | 9 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10052 | 9 | 1 | deiJCKOMF05MLJ_RoomJCK_3JackEmerStopAla | 4 |  |  | 0 | $ComStatus , , | #Emergency Stop MLC 1
74 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | JackNutFaulAla | SIL0 | MODBUS:3:Read:Holding Registers | 2031 | 10 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10052 | 10 | 1 | deiJCKOMF05MLJ_RoomJCK_3JackNutFaulAla | 4 |  |  | 0 | $ComStatus , , | #Nut Fault MLC 1
75 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | JackObstAla | SIL0 | MODBUS:3:Read:Holding Registers | 2031 | 11 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10052 | 11 | 1 | deiJCKOMF05MLJ_RoomJCK_3JackObstAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Obstruction MLC 1
76 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | JackLoadMissAla | SIL0 | MODBUS:3:Read:Holding Registers | 2031 | 12 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10052 | 12 | 1 | deiJCKOMF05MLJ_RoomJCK_3JackLoadMissAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Load missing MLC 1
77 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | JackImpSensAla | SIL0 | MODBUS:3:Read:Holding Registers | 2031 | 13 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10052 | 13 | 1 | deiJCKOMF05MLJ_RoomJCK_3JackImpSensAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Impulse Sensor MLC 1
78 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | JackMotorAla | SIL0 | MODBUS:3:Read:Holding Registers | 2031 | 14 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10052 | 14 | 1 | deiJCKOMF05MLJ_RoomJCK_3JackMotorAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Motorprotection MLC 1
79 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | JackSyncAla | SIL0 | MODBUS:3:Read:Holding Registers | 2031 | 15 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10052 | 15 | 1 | deiJCKOMF05MLJ_RoomJCK_3JackSyncAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Synchronisation MLC 1
80 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | JackContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2032 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10056 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_3JackContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Contactor MLC 1
81 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_3 | 5 | JackFlooContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2032 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10056 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_3JackFlooContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Floor Contact MLC 1
82 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | Avail | SIL0 | MODBUS:3:Read:Holding Registers | 2041 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10062 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_4Avail | 4 |  |  | 0 | $ComStatus , , | #Power Supply MLC 1
83 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | LowLim | SIL0 | MODBUS:3:Read:Holding Registers | 2041 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10062 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_4LowLim | 4 |  |  | 0 | $ComStatus , , | #Park Position MLC 1
84 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | UpLim | SIL0 | MODBUS:3:Read:Holding Registers | 2041 | 2 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10062 | 2 | 1 | deiJCKOMF05MLJ_RoomJCK_4UpLim | 4 |  |  | 0 | $ComStatus , , | #Top Position MLC 1
85 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | LoadAvai | SIL0 | MODBUS:3:Read:Holding Registers | 2041 | 3 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10062 | 3 | 1 | deiJCKOMF05MLJ_RoomJCK_4LoadAvai | 4 |  |  | 0 | $ComStatus , , | #Load on MLC 1
86 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | JackRis | SIL0 | MODBUS:3:Read:Holding Registers | 2041 | 4 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10062 | 4 | 1 | deiJCKOMF05MLJ_RoomJCK_4JackRis | 4 |  |  | 0 | $ComStatus , , | #Rising MLC 1
87 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | JackDesc | SIL0 | MODBUS:3:Read:Holding Registers | 2041 | 5 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10062 | 5 | 1 | deiJCKOMF05MLJ_RoomJCK_4JackDesc | 4 |  |  | 0 | $ComStatus , , | #Descending MLC 1
88 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | JackStanOnFloo | SIL0 | MODBUS:3:Read:Holding Registers | 2041 | 6 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10062 | 6 | 1 | deiJCKOMF05MLJ_RoomJCK_4JackStanOnFloo | 4 |  |  | 0 | $ComStatus , , | #Standing on Floor MLC 1
89 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | JackHeighVal | SIL0 | MODBUS:3:Read:Holding Registers | 2043 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10063 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_4JackHeighVal | 4 |  |  | 0 | $ComStatus , , | #Height value MLC 1
90 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | JackRunTimMin | SIL0 | MODBUS:3:Read:Holding Registers | 2044 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10064 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_4JackRunTimMin | 4 |  |  | 0 | $ComStatus , , | #Running Time MIN MLC 1
91 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | JackRunTimHour | SIL0 | MODBUS:3:Read:Holding Registers | 2045 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10065 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_4JackRunTimHour | 4 |  |  | 0 | $ComStatus , , | #Running Time HOUR MLC 1
92 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | JackAla | SIL0 | MODBUS:3:Read:Holding Registers | 2041 | 7 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10062 | 7 | 1 | deiJCKOMF05MLJ_RoomJCK_4JackAla | 4 |  |  | 0 | $ComStatus , , | #Alarm MLC 1
93 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | JackServStatus | SIL0 | MODBUS:3:Read:Holding Registers | 2041 | 8 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10062 | 8 | 1 | deiJCKOMF05MLJ_RoomJCK_4JackServStatus | 4 |  |  | 0 | $ComStatus , , | #In service MLC 1
94 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | JackEmerStopAla | SIL0 | MODBUS:3:Read:Holding Registers | 2041 | 9 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10062 | 9 | 1 | deiJCKOMF05MLJ_RoomJCK_4JackEmerStopAla | 4 |  |  | 0 | $ComStatus , , | #Emergency Stop MLC 1
95 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | JackNutFaulAla | SIL0 | MODBUS:3:Read:Holding Registers | 2041 | 10 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10062 | 10 | 1 | deiJCKOMF05MLJ_RoomJCK_4JackNutFaulAla | 4 |  |  | 0 | $ComStatus , , | #Nut Fault MLC 1
96 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | JackObstAla | SIL0 | MODBUS:3:Read:Holding Registers | 2041 | 11 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10062 | 11 | 1 | deiJCKOMF05MLJ_RoomJCK_4JackObstAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Obstruction MLC 1
97 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | JackLoadMissAla | SIL0 | MODBUS:3:Read:Holding Registers | 2041 | 12 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10062 | 12 | 1 | deiJCKOMF05MLJ_RoomJCK_4JackLoadMissAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Load missing MLC 1
98 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | JackImpSensAla | SIL0 | MODBUS:3:Read:Holding Registers | 2041 | 13 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10062 | 13 | 1 | deiJCKOMF05MLJ_RoomJCK_4JackImpSensAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Impulse Sensor MLC 1
99 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | JackMotorAla | SIL0 | MODBUS:3:Read:Holding Registers | 2041 | 14 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10062 | 14 | 1 | deiJCKOMF05MLJ_RoomJCK_4JackMotorAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Motorprotection MLC 1
100 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | JackSyncAla | SIL0 | MODBUS:3:Read:Holding Registers | 2041 | 15 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10062 | 15 | 1 | deiJCKOMF05MLJ_RoomJCK_4JackSyncAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Synchronisation MLC 1
101 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | JackContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2042 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10066 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_4JackContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Contactor MLC 1
102 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_4 | 6 | JackFlooContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2042 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10066 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_4JackFlooContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Floor Contact MLC 1
103 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | Avail | SIL0 | MODBUS:3:Read:Holding Registers | 2051 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10072 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_5Avail | 4 |  |  | 0 | $ComStatus , , | #Power Supply MLC 1
104 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | LowLim | SIL0 | MODBUS:3:Read:Holding Registers | 2051 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10072 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_5LowLim | 4 |  |  | 0 | $ComStatus , , | #Park Position MLC 1
105 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | UpLim | SIL0 | MODBUS:3:Read:Holding Registers | 2051 | 2 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10072 | 2 | 1 | deiJCKOMF05MLJ_RoomJCK_5UpLim | 4 |  |  | 0 | $ComStatus , , | #Top Position MLC 1
106 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | LoadAvai | SIL0 | MODBUS:3:Read:Holding Registers | 2051 | 3 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10072 | 3 | 1 | deiJCKOMF05MLJ_RoomJCK_5LoadAvai | 4 |  |  | 0 | $ComStatus , , | #Load on MLC 1
107 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | JackRis | SIL0 | MODBUS:3:Read:Holding Registers | 2051 | 4 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10072 | 4 | 1 | deiJCKOMF05MLJ_RoomJCK_5JackRis | 4 |  |  | 0 | $ComStatus , , | #Rising MLC 1
108 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | JackDesc | SIL0 | MODBUS:3:Read:Holding Registers | 2051 | 5 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10072 | 5 | 1 | deiJCKOMF05MLJ_RoomJCK_5JackDesc | 4 |  |  | 0 | $ComStatus , , | #Descending MLC 1
109 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | JackStanOnFloo | SIL0 | MODBUS:3:Read:Holding Registers | 2051 | 6 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10072 | 6 | 1 | deiJCKOMF05MLJ_RoomJCK_5JackStanOnFloo | 4 |  |  | 0 | $ComStatus , , | #Standing on Floor MLC 1
110 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | JackHeighVal | SIL0 | MODBUS:3:Read:Holding Registers | 2053 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10073 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_5JackHeighVal | 4 |  |  | 0 | $ComStatus , , | #Height value MLC 1
111 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | JackRunTimMin | SIL0 | MODBUS:3:Read:Holding Registers | 5254 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10074 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_5JackRunTimMin | 4 |  |  | 0 | $ComStatus , , | #Running Time MIN MLC 1
112 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | JackRunTimHour | SIL0 | MODBUS:3:Read:Holding Registers | 2055 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10075 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_5JackRunTimHour | 4 |  |  | 0 | $ComStatus , , | #Running Time HOUR MLC 1
113 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | JackAla | SIL0 | MODBUS:3:Read:Holding Registers | 2051 | 7 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10072 | 7 | 1 | deiJCKOMF05MLJ_RoomJCK_5JackAla | 4 |  |  | 0 | $ComStatus , , | #Alarm MLC 1
114 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | JackServStatus | SIL0 | MODBUS:3:Read:Holding Registers | 2051 | 8 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10072 | 8 | 1 | deiJCKOMF05MLJ_RoomJCK_5JackServStatus | 4 |  |  | 0 | $ComStatus , , | #In service MLC 1
115 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | JackEmerStopAla | SIL0 | MODBUS:3:Read:Holding Registers | 2051 | 9 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10072 | 9 | 1 | deiJCKOMF05MLJ_RoomJCK_5JackEmerStopAla | 4 |  |  | 0 | $ComStatus , , | #Emergency Stop MLC 1
116 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | JackNutFaulAla | SIL0 | MODBUS:3:Read:Holding Registers | 2051 | 10 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10072 | 10 | 1 | deiJCKOMF05MLJ_RoomJCK_5JackNutFaulAla | 4 |  |  | 0 | $ComStatus , , | #Nut Fault MLC 1
117 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | JackObstAla | SIL0 | MODBUS:3:Read:Holding Registers | 2051 | 11 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10072 | 11 | 1 | deiJCKOMF05MLJ_RoomJCK_5JackObstAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Obstruction MLC 1
118 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | JackLoadMissAla | SIL0 | MODBUS:3:Read:Holding Registers | 2051 | 12 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10072 | 12 | 1 | deiJCKOMF05MLJ_RoomJCK_5JackLoadMissAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Load missing MLC 1
119 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | JackImpSensAla | SIL0 | MODBUS:3:Read:Holding Registers | 2051 | 13 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10072 | 13 | 1 | deiJCKOMF05MLJ_RoomJCK_5JackImpSensAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Impulse Sensor MLC 1
120 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | JackMotorAla | SIL0 | MODBUS:3:Read:Holding Registers | 2051 | 14 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10072 | 14 | 1 | deiJCKOMF05MLJ_RoomJCK_5JackMotorAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Motorprotection MLC 1
121 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | JackSyncAla | SIL0 | MODBUS:3:Read:Holding Registers | 2051 | 15 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10072 | 15 | 1 | deiJCKOMF05MLJ_RoomJCK_5JackSyncAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Synchronisation MLC 1
122 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | JackContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2052 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10076 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_5JackContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Contactor MLC 1
123 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_5 | 7 | JackFlooContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2052 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10076 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_5JackFlooContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Floor Contact MLC 1
124 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | Avail | SIL0 | MODBUS:3:Read:Holding Registers | 2061 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10082 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_6Avail | 4 |  |  | 0 | $ComStatus , , | #Power Supply MLC 1
125 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | LowLim | SIL0 | MODBUS:3:Read:Holding Registers | 2061 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10082 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_6LowLim | 4 |  |  | 0 | $ComStatus , , | #Park Position MLC 1
126 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | UpLim | SIL0 | MODBUS:3:Read:Holding Registers | 2061 | 2 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10082 | 2 | 1 | deiJCKOMF05MLJ_RoomJCK_6UpLim | 4 |  |  | 0 | $ComStatus , , | #Top Position MLC 1
127 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | LoadAvai | SIL0 | MODBUS:3:Read:Holding Registers | 2061 | 3 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10082 | 3 | 1 | deiJCKOMF05MLJ_RoomJCK_6LoadAvai | 4 |  |  | 0 | $ComStatus , , | #Load on MLC 1
128 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | JackRis | SIL0 | MODBUS:3:Read:Holding Registers | 2061 | 4 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10082 | 4 | 1 | deiJCKOMF05MLJ_RoomJCK_6JackRis | 4 |  |  | 0 | $ComStatus , , | #Rising MLC 1
129 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | JackDesc | SIL0 | MODBUS:3:Read:Holding Registers | 2061 | 5 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10082 | 5 | 1 | deiJCKOMF05MLJ_RoomJCK_6JackDesc | 4 |  |  | 0 | $ComStatus , , | #Descending MLC 1
130 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | JackStanOnFloo | SIL0 | MODBUS:3:Read:Holding Registers | 2061 | 6 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10082 | 6 | 1 | deiJCKOMF05MLJ_RoomJCK_6JackStanOnFloo | 4 |  |  | 0 | $ComStatus , , | #Standing on Floor MLC 1
131 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | JackHeighVal | SIL0 | MODBUS:3:Read:Holding Registers | 2063 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10083 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_6JackHeighVal | 4 |  |  | 0 | $ComStatus , , | #Height value MLC 1
132 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | JackRunTimMin | SIL0 | MODBUS:3:Read:Holding Registers | 2064 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10084 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_6JackRunTimMin | 4 |  |  | 0 | $ComStatus , , | #Running Time MIN MLC 1
133 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | JackRunTimHour | SIL0 | MODBUS:3:Read:Holding Registers | 2065 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10085 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_6JackRunTimHour | 4 |  |  | 0 | $ComStatus , , | #Running Time HOUR MLC 1
134 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | JackAla | SIL0 | MODBUS:3:Read:Holding Registers | 2061 | 7 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10082 | 7 | 1 | deiJCKOMF05MLJ_RoomJCK_6JackAla | 4 |  |  | 0 | $ComStatus , , | #Alarm MLC 1
135 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | JackServStatus | SIL0 | MODBUS:3:Read:Holding Registers | 2061 | 8 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10082 | 8 | 1 | deiJCKOMF05MLJ_RoomJCK_6JackServStatus | 4 |  |  | 0 | $ComStatus , , | #In service MLC 1
136 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | JackEmerStopAla | SIL0 | MODBUS:3:Read:Holding Registers | 2061 | 9 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10082 | 9 | 1 | deiJCKOMF05MLJ_RoomJCK_6JackEmerStopAla | 4 |  |  | 0 | $ComStatus , , | #Emergency Stop MLC 1
137 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | JackNutFaulAla | SIL0 | MODBUS:3:Read:Holding Registers | 2061 | 10 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10082 | 10 | 1 | deiJCKOMF05MLJ_RoomJCK_6JackNutFaulAla | 4 |  |  | 0 | $ComStatus , , | #Nut Fault MLC 1
138 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | JackObstAla | SIL0 | MODBUS:3:Read:Holding Registers | 2061 | 11 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10082 | 11 | 1 | deiJCKOMF05MLJ_RoomJCK_6JackObstAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Obstruction MLC 1
139 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | JackLoadMissAla | SIL0 | MODBUS:3:Read:Holding Registers | 2061 | 12 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10082 | 12 | 1 | deiJCKOMF05MLJ_RoomJCK_6JackLoadMissAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Load missing MLC 1
140 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | JackImpSensAla | SIL0 | MODBUS:3:Read:Holding Registers | 2061 | 13 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10082 | 13 | 1 | deiJCKOMF05MLJ_RoomJCK_6JackImpSensAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Impulse Sensor MLC 1
141 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | JackMotorAla | SIL0 | MODBUS:3:Read:Holding Registers | 2061 | 14 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10082 | 14 | 1 | deiJCKOMF05MLJ_RoomJCK_6JackMotorAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Motorprotection MLC 1
142 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | JackSyncAla | SIL0 | MODBUS:3:Read:Holding Registers | 2061 | 15 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10082 | 15 | 1 | deiJCKOMF05MLJ_RoomJCK_6JackSyncAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Synchronisation MLC 1
143 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | JackContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2062 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10086 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_6JackContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Contactor MLC 1
144 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_6 | 8 | JackFlooContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2062 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10086 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_6JackFlooContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Floor Contact MLC 1
145 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | Avail | SIL0 | MODBUS:3:Read:Holding Registers | 2071 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10092 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_7Avail | 4 |  |  | 0 | $ComStatus , , | #Power Supply MLC 1
146 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | LowLim | SIL0 | MODBUS:3:Read:Holding Registers | 2071 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10092 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_7LowLim | 4 |  |  | 0 | $ComStatus , , | #Park Position MLC 1
147 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | UpLim | SIL0 | MODBUS:3:Read:Holding Registers | 2071 | 2 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10092 | 2 | 1 | deiJCKOMF05MLJ_RoomJCK_7UpLim | 4 |  |  | 0 | $ComStatus , , | #Top Position MLC 1
148 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | LoadAvai | SIL0 | MODBUS:3:Read:Holding Registers | 2071 | 3 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10092 | 3 | 1 | deiJCKOMF05MLJ_RoomJCK_7LoadAvai | 4 |  |  | 0 | $ComStatus , , | #Load on MLC 1
149 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | JackRis | SIL0 | MODBUS:3:Read:Holding Registers | 2071 | 4 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10092 | 4 | 1 | deiJCKOMF05MLJ_RoomJCK_7JackRis | 4 |  |  | 0 | $ComStatus , , | #Rising MLC 1
150 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | JackDesc | SIL0 | MODBUS:3:Read:Holding Registers | 2071 | 5 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10092 | 5 | 1 | deiJCKOMF05MLJ_RoomJCK_7JackDesc | 4 |  |  | 0 | $ComStatus , , | #Descending MLC 1
151 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | JackStanOnFloo | SIL0 | MODBUS:3:Read:Holding Registers | 2071 | 6 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10092 | 6 | 1 | deiJCKOMF05MLJ_RoomJCK_7JackStanOnFloo | 4 |  |  | 0 | $ComStatus , , | #Standing on Floor MLC 1
152 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | JackHeighVal | SIL0 | MODBUS:3:Read:Holding Registers | 2073 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10093 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_7JackHeighVal | 4 |  |  | 0 | $ComStatus , , | #Height value MLC 1
153 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | JackRunTimMin | SIL0 | MODBUS:3:Read:Holding Registers | 2074 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10094 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_7JackRunTimMin | 4 |  |  | 0 | $ComStatus , , | #Running Time MIN MLC 1
154 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | JackRunTimHour | SIL0 | MODBUS:3:Read:Holding Registers | 2075 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10095 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_7JackRunTimHour | 4 |  |  | 0 | $ComStatus , , | #Running Time HOUR MLC 1
155 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | JackAla | SIL0 | MODBUS:3:Read:Holding Registers | 2071 | 7 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10092 | 7 | 1 | deiJCKOMF05MLJ_RoomJCK_7JackAla | 4 |  |  | 0 | $ComStatus , , | #Alarm MLC 1
156 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | JackServStatus | SIL0 | MODBUS:3:Read:Holding Registers | 2071 | 8 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10092 | 8 | 1 | deiJCKOMF05MLJ_RoomJCK_7JackServStatus | 4 |  |  | 0 | $ComStatus , , | #In service MLC 1
157 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | JackEmerStopAla | SIL0 | MODBUS:3:Read:Holding Registers | 2071 | 9 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10092 | 9 | 1 | deiJCKOMF05MLJ_RoomJCK_7JackEmerStopAla | 4 |  |  | 0 | $ComStatus , , | #Emergency Stop MLC 1
158 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | JackNutFaulAla | SIL0 | MODBUS:3:Read:Holding Registers | 2071 | 10 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10092 | 10 | 1 | deiJCKOMF05MLJ_RoomJCK_7JackNutFaulAla | 4 |  |  | 0 | $ComStatus , , | #Nut Fault MLC 1
159 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | JackObstAla | SIL0 | MODBUS:3:Read:Holding Registers | 2071 | 11 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10092 | 11 | 1 | deiJCKOMF05MLJ_RoomJCK_7JackObstAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Obstruction MLC 1
160 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | JackLoadMissAla | SIL0 | MODBUS:3:Read:Holding Registers | 2071 | 12 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10092 | 12 | 1 | deiJCKOMF05MLJ_RoomJCK_7JackLoadMissAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Load missing MLC 1
161 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | JackImpSensAla | SIL0 | MODBUS:3:Read:Holding Registers | 2071 | 13 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10092 | 13 | 1 | deiJCKOMF05MLJ_RoomJCK_7JackImpSensAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Impulse Sensor MLC 1
162 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | JackMotorAla | SIL0 | MODBUS:3:Read:Holding Registers | 2071 | 14 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10092 | 14 | 1 | deiJCKOMF05MLJ_RoomJCK_7JackMotorAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Motorprotection MLC 1
163 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | JackSyncAla | SIL0 | MODBUS:3:Read:Holding Registers | 2071 | 15 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10092 | 15 | 1 | deiJCKOMF05MLJ_RoomJCK_7JackSyncAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Synchronisation MLC 1
164 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | JackContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2072 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10096 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_7JackContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Contactor MLC 1
165 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_7 | 9 | JackFlooContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2072 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10096 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_7JackFlooContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Floor Contact MLC 1
166 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | Avail | SIL0 | MODBUS:3:Read:Holding Registers | 2081 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10102 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_8Avail | 4 |  |  | 0 | $ComStatus , , | #Power Supply MLC 1
167 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | LowLim | SIL0 | MODBUS:3:Read:Holding Registers | 2081 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10102 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_8LowLim | 4 |  |  | 0 | $ComStatus , , | #Park Position MLC 1
168 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | UpLim | SIL0 | MODBUS:3:Read:Holding Registers | 2081 | 2 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10102 | 2 | 1 | deiJCKOMF05MLJ_RoomJCK_8UpLim | 4 |  |  | 0 | $ComStatus , , | #Top Position MLC 1
169 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | LoadAvai | SIL0 | MODBUS:3:Read:Holding Registers | 2081 | 3 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10102 | 3 | 1 | deiJCKOMF05MLJ_RoomJCK_8LoadAvai | 4 |  |  | 0 | $ComStatus , , | #Load on MLC 1
170 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | JackRis | SIL0 | MODBUS:3:Read:Holding Registers | 2081 | 4 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10102 | 4 | 1 | deiJCKOMF05MLJ_RoomJCK_8JackRis | 4 |  |  | 0 | $ComStatus , , | #Rising MLC 1
171 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | JackDesc | SIL0 | MODBUS:3:Read:Holding Registers | 2081 | 5 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10102 | 5 | 1 | deiJCKOMF05MLJ_RoomJCK_8JackDesc | 4 |  |  | 0 | $ComStatus , , | #Descending MLC 1
172 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | JackStanOnFloo | SIL0 | MODBUS:3:Read:Holding Registers | 2081 | 6 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10102 | 6 | 1 | deiJCKOMF05MLJ_RoomJCK_8JackStanOnFloo | 4 |  |  | 0 | $ComStatus , , | #Standing on Floor MLC 1
173 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | JackHeighVal | SIL0 | MODBUS:3:Read:Holding Registers | 2083 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10103 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_8JackHeighVal | 4 |  |  | 0 | $ComStatus , , | #Height value MLC 1
174 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | JackRunTimMin | SIL0 | MODBUS:3:Read:Holding Registers | 2084 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10104 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_8JackRunTimMin | 4 |  |  | 0 | $ComStatus , , | #Running Time MIN MLC 1
175 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | JackRunTimHour | SIL0 | MODBUS:3:Read:Holding Registers | 2085 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10105 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_8JackRunTimHour | 4 |  |  | 0 | $ComStatus , , | #Running Time HOUR MLC 1
176 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | JackAla | SIL0 | MODBUS:3:Read:Holding Registers | 2081 | 7 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10102 | 7 | 1 | deiJCKOMF05MLJ_RoomJCK_8JackAla | 4 |  |  | 0 | $ComStatus , , | #Alarm MLC 1
177 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | JackServStatus | SIL0 | MODBUS:3:Read:Holding Registers | 2081 | 8 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10102 | 8 | 1 | deiJCKOMF05MLJ_RoomJCK_8JackServStatus | 4 |  |  | 0 | $ComStatus , , | #In service MLC 1
178 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | JackEmerStopAla | SIL0 | MODBUS:3:Read:Holding Registers | 2081 | 9 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10102 | 9 | 1 | deiJCKOMF05MLJ_RoomJCK_8JackEmerStopAla | 4 |  |  | 0 | $ComStatus , , | #Emergency Stop MLC 1
179 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | JackNutFaulAla | SIL0 | MODBUS:3:Read:Holding Registers | 2081 | 10 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10102 | 10 | 1 | deiJCKOMF05MLJ_RoomJCK_8JackNutFaulAla | 4 |  |  | 0 | $ComStatus , , | #Nut Fault MLC 1
180 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | JackObstAla | SIL0 | MODBUS:3:Read:Holding Registers | 2081 | 11 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10102 | 11 | 1 | deiJCKOMF05MLJ_RoomJCK_8JackObstAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Obstruction MLC 1
181 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | JackLoadMissAla | SIL0 | MODBUS:3:Read:Holding Registers | 2081 | 12 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10102 | 12 | 1 | deiJCKOMF05MLJ_RoomJCK_8JackLoadMissAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Load missing MLC 1
182 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | JackImpSensAla | SIL0 | MODBUS:3:Read:Holding Registers | 2081 | 13 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10102 | 13 | 1 | deiJCKOMF05MLJ_RoomJCK_8JackImpSensAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Impulse Sensor MLC 1
183 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | JackMotorAla | SIL0 | MODBUS:3:Read:Holding Registers | 2081 | 14 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10102 | 14 | 1 | deiJCKOMF05MLJ_RoomJCK_8JackMotorAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Motorprotection MLC 1
184 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | JackSyncAla | SIL0 | MODBUS:3:Read:Holding Registers | 2081 | 15 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10102 | 15 | 1 | deiJCKOMF05MLJ_RoomJCK_8JackSyncAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Synchronisation MLC 1
185 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | JackContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2082 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10106 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_8JackContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Contactor MLC 1
186 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_8 | 10 | JackFlooContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2082 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10106 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_8JackFlooContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Floor Contact MLC 1
187 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | Avail | SIL0 | MODBUS:3:Read:Holding Registers | 2091 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10112 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_9Avail | 4 |  |  | 0 | $ComStatus , , | #Power Supply MLC 1
188 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | LowLim | SIL0 | MODBUS:3:Read:Holding Registers | 2091 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10112 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_9LowLim | 4 |  |  | 0 | $ComStatus , , | #Park Position MLC 1
189 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | UpLim | SIL0 | MODBUS:3:Read:Holding Registers | 2091 | 2 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10112 | 2 | 1 | deiJCKOMF05MLJ_RoomJCK_9UpLim | 4 |  |  | 0 | $ComStatus , , | #Top Position MLC 1
190 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | LoadAvai | SIL0 | MODBUS:3:Read:Holding Registers | 2091 | 3 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10112 | 3 | 1 | deiJCKOMF05MLJ_RoomJCK_9LoadAvai | 4 |  |  | 0 | $ComStatus , , | #Load on MLC 1
191 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | JackRis | SIL0 | MODBUS:3:Read:Holding Registers | 2091 | 4 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10112 | 4 | 1 | deiJCKOMF05MLJ_RoomJCK_9JackRis | 4 |  |  | 0 | $ComStatus , , | #Rising MLC 1
192 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | JackDesc | SIL0 | MODBUS:3:Read:Holding Registers | 2091 | 5 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10112 | 5 | 1 | deiJCKOMF05MLJ_RoomJCK_9JackDesc | 4 |  |  | 0 | $ComStatus , , | #Descending MLC 1
193 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | JackStanOnFloo | SIL0 | MODBUS:3:Read:Holding Registers | 2091 | 6 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10112 | 6 | 1 | deiJCKOMF05MLJ_RoomJCK_9JackStanOnFloo | 4 |  |  | 0 | $ComStatus , , | #Standing on Floor MLC 1
194 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | JackHeighVal | SIL0 | MODBUS:3:Read:Holding Registers | 2093 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10113 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_9JackHeighVal | 4 |  |  | 0 | $ComStatus , , | #Height value MLC 1
195 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | JackRunTimMin | SIL0 | MODBUS:3:Read:Holding Registers | 2094 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10114 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_9JackRunTimMin | 4 |  |  | 0 | $ComStatus , , | #Running Time MIN MLC 1
196 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | JackRunTimHour | SIL0 | MODBUS:3:Read:Holding Registers | 2095 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10115 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_9JackRunTimHour | 4 |  |  | 0 | $ComStatus , , | #Running Time HOUR MLC 1
197 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | JackAla | SIL0 | MODBUS:3:Read:Holding Registers | 2091 | 7 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10112 | 7 | 1 | deiJCKOMF05MLJ_RoomJCK_9JackAla | 4 |  |  | 0 | $ComStatus , , | #Alarm MLC 1
198 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | JackServStatus | SIL0 | MODBUS:3:Read:Holding Registers | 2091 | 8 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10112 | 8 | 1 | deiJCKOMF05MLJ_RoomJCK_9JackServStatus | 4 |  |  | 0 | $ComStatus , , | #In service MLC 1
199 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | JackEmerStopAla | SIL0 | MODBUS:3:Read:Holding Registers | 2091 | 9 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10112 | 9 | 1 | deiJCKOMF05MLJ_RoomJCK_9JackEmerStopAla | 4 |  |  | 0 | $ComStatus , , | #Emergency Stop MLC 1
200 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | JackNutFaulAla | SIL0 | MODBUS:3:Read:Holding Registers | 2091 | 10 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10112 | 10 | 1 | deiJCKOMF05MLJ_RoomJCK_9JackNutFaulAla | 4 |  |  | 0 | $ComStatus , , | #Nut Fault MLC 1
201 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | JackObstAla | SIL0 | MODBUS:3:Read:Holding Registers | 2091 | 11 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10112 | 11 | 1 | deiJCKOMF05MLJ_RoomJCK_9JackObstAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Obstruction MLC 1
202 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | JackLoadMissAla | SIL0 | MODBUS:3:Read:Holding Registers | 2091 | 12 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10112 | 12 | 1 | deiJCKOMF05MLJ_RoomJCK_9JackLoadMissAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Load missing MLC 1
203 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | JackImpSensAla | SIL0 | MODBUS:3:Read:Holding Registers | 2091 | 13 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10112 | 13 | 1 | deiJCKOMF05MLJ_RoomJCK_9JackImpSensAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Impulse Sensor MLC 1
204 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | JackMotorAla | SIL0 | MODBUS:3:Read:Holding Registers | 2091 | 14 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10112 | 14 | 1 | deiJCKOMF05MLJ_RoomJCK_9JackMotorAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Motorprotection MLC 1
205 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | JackSyncAla | SIL0 | MODBUS:3:Read:Holding Registers | 2091 | 15 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10112 | 15 | 1 | deiJCKOMF05MLJ_RoomJCK_9JackSyncAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Synchronisation MLC 1
206 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | JackContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2092 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10116 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_9JackContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Contactor MLC 1
207 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_9 | 11 | JackFlooContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2092 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10116 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_9JackFlooContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Floor Contact MLC 1
208 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | Avail | SIL0 | MODBUS:3:Read:Holding Registers | 2101 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10122 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_10Avail | 4 |  |  | 0 | $ComStatus , , | #Power Supply MLC 1
209 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | LowLim | SIL0 | MODBUS:3:Read:Holding Registers | 2101 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10122 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_10LowLim | 4 |  |  | 0 | $ComStatus , , | #Park Position MLC 1
210 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | UpLim | SIL0 | MODBUS:3:Read:Holding Registers | 2101 | 2 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10122 | 2 | 1 | deiJCKOMF05MLJ_RoomJCK_10UpLim | 4 |  |  | 0 | $ComStatus , , | #Top Position MLC 1
211 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | LoadAvai | SIL0 | MODBUS:3:Read:Holding Registers | 2101 | 3 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10122 | 3 | 1 | deiJCKOMF05MLJ_RoomJCK_10LoadAvai | 4 |  |  | 0 | $ComStatus , , | #Load on MLC 1
212 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | JackRis | SIL0 | MODBUS:3:Read:Holding Registers | 2101 | 4 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10122 | 4 | 1 | deiJCKOMF05MLJ_RoomJCK_10JackRis | 4 |  |  | 0 | $ComStatus , , | #Rising MLC 1
213 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | JackDesc | SIL0 | MODBUS:3:Read:Holding Registers | 2101 | 5 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10122 | 5 | 1 | deiJCKOMF05MLJ_RoomJCK_10JackDesc | 4 |  |  | 0 | $ComStatus , , | #Descending MLC 1
214 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | JackStanOnFloo | SIL0 | MODBUS:3:Read:Holding Registers | 2101 | 6 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10122 | 6 | 1 | deiJCKOMF05MLJ_RoomJCK_10JackStanOnFloo | 4 |  |  | 0 | $ComStatus , , | #Standing on Floor MLC 1
215 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | JackHeighVal | SIL0 | MODBUS:3:Read:Holding Registers | 2103 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10123 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_10JackHeighVal | 4 |  |  | 0 | $ComStatus , , | #Height value MLC 1
216 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | JackRunTimMin | SIL0 | MODBUS:3:Read:Holding Registers | 2104 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10124 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_10JackRunTimMin | 4 |  |  | 0 | $ComStatus , , | #Running Time MIN MLC 1
217 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | JackRunTimHour | SIL0 | MODBUS:3:Read:Holding Registers | 2105 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10125 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_10JackRunTimHour | 4 |  |  | 0 | $ComStatus , , | #Running Time HOUR MLC 1
218 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | JackAla | SIL0 | MODBUS:3:Read:Holding Registers | 2101 | 7 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10122 | 7 | 1 | deiJCKOMF05MLJ_RoomJCK_10JackAla | 4 |  |  | 0 | $ComStatus , , | #Alarm MLC 1
219 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | JackServStatus | SIL0 | MODBUS:3:Read:Holding Registers | 2101 | 8 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10122 | 8 | 1 | deiJCKOMF05MLJ_RoomJCK_10JackServStatus | 4 |  |  | 0 | $ComStatus , , | #In service MLC 1
220 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | JackEmerStopAla | SIL0 | MODBUS:3:Read:Holding Registers | 2101 | 9 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10122 | 9 | 1 | deiJCKOMF05MLJ_RoomJCK_10JackEmerStopAla | 4 |  |  | 0 | $ComStatus , , | #Emergency Stop MLC 1
221 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | JackNutFaulAla | SIL0 | MODBUS:3:Read:Holding Registers | 2101 | 10 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10122 | 10 | 1 | deiJCKOMF05MLJ_RoomJCK_10JackNutFaulAla | 4 |  |  | 0 | $ComStatus , , | #Nut Fault MLC 1
222 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | JackObstAla | SIL0 | MODBUS:3:Read:Holding Registers | 2101 | 11 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10122 | 11 | 1 | deiJCKOMF05MLJ_RoomJCK_10JackObstAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Obstruction MLC 1
223 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | JackLoadMissAla | SIL0 | MODBUS:3:Read:Holding Registers | 2101 | 12 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10122 | 12 | 1 | deiJCKOMF05MLJ_RoomJCK_10JackLoadMissAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Load missing MLC 1
224 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | JackImpSensAla | SIL0 | MODBUS:3:Read:Holding Registers | 2101 | 13 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10122 | 13 | 1 | deiJCKOMF05MLJ_RoomJCK_10JackImpSensAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Impulse Sensor MLC 1
225 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | JackMotorAla | SIL0 | MODBUS:3:Read:Holding Registers | 2101 | 14 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10122 | 14 | 1 | deiJCKOMF05MLJ_RoomJCK_10JackMotorAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Motorprotection MLC 1
226 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | JackSyncAla | SIL0 | MODBUS:3:Read:Holding Registers | 2101 | 15 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10122 | 15 | 1 | deiJCKOMF05MLJ_RoomJCK_10JackSyncAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Synchronisation MLC 1
227 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | JackContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2102 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10126 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_10JackContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Contactor MLC 1
228 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_10 | 12 | JackFlooContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2102 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10126 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_10JackFlooContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Floor Contact MLC 1
229 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | Avail | SIL0 | MODBUS:3:Read:Holding Registers | 2111 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10132 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_11Avail | 4 |  |  | 0 | $ComStatus , , | #Power Supply MLC 1
230 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | LowLim | SIL0 | MODBUS:3:Read:Holding Registers | 2111 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10132 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_11LowLim | 4 |  |  | 0 | $ComStatus , , | #Park Position MLC 1
231 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | UpLim | SIL0 | MODBUS:3:Read:Holding Registers | 2111 | 2 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10132 | 2 | 1 | deiJCKOMF05MLJ_RoomJCK_11UpLim | 4 |  |  | 0 | $ComStatus , , | #Top Position MLC 1
232 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | LoadAvai | SIL0 | MODBUS:3:Read:Holding Registers | 2111 | 3 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10132 | 3 | 1 | deiJCKOMF05MLJ_RoomJCK_11LoadAvai | 4 |  |  | 0 | $ComStatus , , | #Load on MLC 1
233 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | JackRis | SIL0 | MODBUS:3:Read:Holding Registers | 2111 | 4 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10132 | 4 | 1 | deiJCKOMF05MLJ_RoomJCK_11JackRis | 4 |  |  | 0 | $ComStatus , , | #Rising MLC 1
234 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | JackDesc | SIL0 | MODBUS:3:Read:Holding Registers | 2111 | 5 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10132 | 5 | 1 | deiJCKOMF05MLJ_RoomJCK_11JackDesc | 4 |  |  | 0 | $ComStatus , , | #Descending MLC 1
235 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | JackStanOnFloo | SIL0 | MODBUS:3:Read:Holding Registers | 2111 | 6 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10132 | 6 | 1 | deiJCKOMF05MLJ_RoomJCK_11JackStanOnFloo | 4 |  |  | 0 | $ComStatus , , | #Standing on Floor MLC 1
236 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | JackHeighVal | SIL0 | MODBUS:3:Read:Holding Registers | 2113 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10133 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_11JackHeighVal | 4 |  |  | 0 | $ComStatus , , | #Height value MLC 1
237 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | JackRunTimMin | SIL0 | MODBUS:3:Read:Holding Registers | 2114 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10134 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_11JackRunTimMin | 4 |  |  | 0 | $ComStatus , , | #Running Time MIN MLC 1
238 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | JackRunTimHour | SIL0 | MODBUS:3:Read:Holding Registers | 2115 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10135 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_11JackRunTimHour | 4 |  |  | 0 | $ComStatus , , | #Running Time HOUR MLC 1
239 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | JackAla | SIL0 | MODBUS:3:Read:Holding Registers | 2111 | 7 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10132 | 7 | 1 | deiJCKOMF05MLJ_RoomJCK_11JackAla | 4 |  |  | 0 | $ComStatus , , | #Alarm MLC 1
240 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | JackServStatus | SIL0 | MODBUS:3:Read:Holding Registers | 2111 | 8 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10132 | 8 | 1 | deiJCKOMF05MLJ_RoomJCK_11JackServStatus | 4 |  |  | 0 | $ComStatus , , | #In service MLC 1
241 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | JackEmerStopAla | SIL0 | MODBUS:3:Read:Holding Registers | 2111 | 9 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10132 | 9 | 1 | deiJCKOMF05MLJ_RoomJCK_11JackEmerStopAla | 4 |  |  | 0 | $ComStatus , , | #Emergency Stop MLC 1
242 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | JackNutFaulAla | SIL0 | MODBUS:3:Read:Holding Registers | 2111 | 10 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10132 | 10 | 1 | deiJCKOMF05MLJ_RoomJCK_11JackNutFaulAla | 4 |  |  | 0 | $ComStatus , , | #Nut Fault MLC 1
243 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | JackObstAla | SIL0 | MODBUS:3:Read:Holding Registers | 2111 | 11 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10132 | 11 | 1 | deiJCKOMF05MLJ_RoomJCK_11JackObstAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Obstruction MLC 1
244 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | JackLoadMissAla | SIL0 | MODBUS:3:Read:Holding Registers | 2111 | 12 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10132 | 12 | 1 | deiJCKOMF05MLJ_RoomJCK_11JackLoadMissAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Load missing MLC 1
245 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | JackImpSensAla | SIL0 | MODBUS:3:Read:Holding Registers | 2111 | 13 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10132 | 13 | 1 | deiJCKOMF05MLJ_RoomJCK_11JackImpSensAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Impulse Sensor MLC 1
246 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | JackMotorAla | SIL0 | MODBUS:3:Read:Holding Registers | 2111 | 14 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10132 | 14 | 1 | deiJCKOMF05MLJ_RoomJCK_11JackMotorAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Motorprotection MLC 1
247 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | JackSyncAla | SIL0 | MODBUS:3:Read:Holding Registers | 2111 | 15 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10132 | 15 | 1 | deiJCKOMF05MLJ_RoomJCK_11JackSyncAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Synchronisation MLC 1
248 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | JackContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2112 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10136 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_11JackContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Contactor MLC 1
249 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_11 | 13 | JackFlooContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2112 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10136 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_11JackFlooContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Floor Contact MLC 1
250 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | Avail | SIL0 | MODBUS:3:Read:Holding Registers | 2121 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10142 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_12Avail | 4 |  |  | 0 | $ComStatus , , | #Power Supply MLC 1
251 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | LowLim | SIL0 | MODBUS:3:Read:Holding Registers | 2121 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10142 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_12LowLim | 4 |  |  | 0 | $ComStatus , , | #Park Position MLC 1
252 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | UpLim | SIL0 | MODBUS:3:Read:Holding Registers | 2121 | 2 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10142 | 2 | 1 | deiJCKOMF05MLJ_RoomJCK_12UpLim | 4 |  |  | 0 | $ComStatus , , | #Top Position MLC 1
253 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | LoadAvai | SIL0 | MODBUS:3:Read:Holding Registers | 2121 | 3 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10142 | 3 | 1 | deiJCKOMF05MLJ_RoomJCK_12LoadAvai | 4 |  |  | 0 | $ComStatus , , | #Load on MLC 1
254 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | JackRis | SIL0 | MODBUS:3:Read:Holding Registers | 2121 | 4 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10142 | 4 | 1 | deiJCKOMF05MLJ_RoomJCK_12JackRis | 4 |  |  | 0 | $ComStatus , , | #Rising MLC 1
255 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | JackDesc | SIL0 | MODBUS:3:Read:Holding Registers | 2121 | 5 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10142 | 5 | 1 | deiJCKOMF05MLJ_RoomJCK_12JackDesc | 4 |  |  | 0 | $ComStatus , , | #Descending MLC 1
256 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | JackStanOnFloo | SIL0 | MODBUS:3:Read:Holding Registers | 2121 | 6 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10142 | 6 | 1 | deiJCKOMF05MLJ_RoomJCK_12JackStanOnFloo | 4 |  |  | 0 | $ComStatus , , | #Standing on Floor MLC 1
257 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | JackHeighVal | SIL0 | MODBUS:3:Read:Holding Registers | 2123 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10143 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_12JackHeighVal | 4 |  |  | 0 | $ComStatus , , | #Height value MLC 1
258 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | JackRunTimMin | SIL0 | MODBUS:3:Read:Holding Registers | 2124 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10144 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_12JackRunTimMin | 4 |  |  | 0 | $ComStatus , , | #Running Time MIN MLC 1
259 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | JackRunTimHour | SIL0 | MODBUS:3:Read:Holding Registers | 2125 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10145 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_12JackRunTimHour | 4 |  |  | 0 | $ComStatus , , | #Running Time HOUR MLC 1
260 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | JackAla | SIL0 | MODBUS:3:Read:Holding Registers | 2121 | 7 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10142 | 7 | 1 | deiJCKOMF05MLJ_RoomJCK_12JackAla | 4 |  |  | 0 | $ComStatus , , | #Alarm MLC 1
261 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | JackServStatus | SIL0 | MODBUS:3:Read:Holding Registers | 2121 | 8 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10142 | 8 | 1 | deiJCKOMF05MLJ_RoomJCK_12JackServStatus | 4 |  |  | 0 | $ComStatus , , | #In service MLC 1
262 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | JackEmerStopAla | SIL0 | MODBUS:3:Read:Holding Registers | 2121 | 9 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10142 | 9 | 1 | deiJCKOMF05MLJ_RoomJCK_12JackEmerStopAla | 4 |  |  | 0 | $ComStatus , , | #Emergency Stop MLC 1
263 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | JackNutFaulAla | SIL0 | MODBUS:3:Read:Holding Registers | 2121 | 10 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10142 | 10 | 1 | deiJCKOMF05MLJ_RoomJCK_12JackNutFaulAla | 4 |  |  | 0 | $ComStatus , , | #Nut Fault MLC 1
264 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | JackObstAla | SIL0 | MODBUS:3:Read:Holding Registers | 2121 | 11 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10142 | 11 | 1 | deiJCKOMF05MLJ_RoomJCK_12JackObstAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Obstruction MLC 1
265 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | JackLoadMissAla | SIL0 | MODBUS:3:Read:Holding Registers | 2121 | 12 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10142 | 12 | 1 | deiJCKOMF05MLJ_RoomJCK_12JackLoadMissAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Load missing MLC 1
266 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | JackImpSensAla | SIL0 | MODBUS:3:Read:Holding Registers | 2121 | 13 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10142 | 13 | 1 | deiJCKOMF05MLJ_RoomJCK_12JackImpSensAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Impulse Sensor MLC 1
267 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | JackMotorAla | SIL0 | MODBUS:3:Read:Holding Registers | 2121 | 14 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10142 | 14 | 1 | deiJCKOMF05MLJ_RoomJCK_12JackMotorAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Motorprotection MLC 1
268 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | JackSyncAla | SIL0 | MODBUS:3:Read:Holding Registers | 2121 | 15 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10142 | 15 | 1 | deiJCKOMF05MLJ_RoomJCK_12JackSyncAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Synchronisation MLC 1
269 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | JackContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2122 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10146 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_12JackContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Contactor MLC 1
270 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_12 | 14 | JackFlooContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2122 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10146 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_12JackFlooContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Floor Contact MLC 1
271 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | Avail | SIL0 | MODBUS:3:Read:Holding Registers | 2131 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10152 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_13Avail | 4 |  |  | 0 | $ComStatus , , | #Power Supply MLC 1
272 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | LowLim | SIL0 | MODBUS:3:Read:Holding Registers | 2131 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10152 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_13LowLim | 4 |  |  | 0 | $ComStatus , , | #Park Position MLC 1
273 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | UpLim | SIL0 | MODBUS:3:Read:Holding Registers | 2131 | 2 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10152 | 2 | 1 | deiJCKOMF05MLJ_RoomJCK_13UpLim | 4 |  |  | 0 | $ComStatus , , | #Top Position MLC 1
274 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | LoadAvai | SIL0 | MODBUS:3:Read:Holding Registers | 2131 | 3 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10152 | 3 | 1 | deiJCKOMF05MLJ_RoomJCK_13LoadAvai | 4 |  |  | 0 | $ComStatus , , | #Load on MLC 1
275 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | JackRis | SIL0 | MODBUS:3:Read:Holding Registers | 2131 | 4 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10152 | 4 | 1 | deiJCKOMF05MLJ_RoomJCK_13JackRis | 4 |  |  | 0 | $ComStatus , , | #Rising MLC 1
276 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | JackDesc | SIL0 | MODBUS:3:Read:Holding Registers | 2131 | 5 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10152 | 5 | 1 | deiJCKOMF05MLJ_RoomJCK_13JackDesc | 4 |  |  | 0 | $ComStatus , , | #Descending MLC 1
277 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | JackStanOnFloo | SIL0 | MODBUS:3:Read:Holding Registers | 2131 | 6 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10152 | 6 | 1 | deiJCKOMF05MLJ_RoomJCK_13JackStanOnFloo | 4 |  |  | 0 | $ComStatus , , | #Standing on Floor MLC 1
278 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | JackHeighVal | SIL0 | MODBUS:3:Read:Holding Registers | 2133 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10153 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_13JackHeighVal | 4 |  |  | 0 | $ComStatus , , | #Height value MLC 1
279 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | JackRunTimMin | SIL0 | MODBUS:3:Read:Holding Registers | 2134 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10154 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_13JackRunTimMin | 4 |  |  | 0 | $ComStatus , , | #Running Time MIN MLC 1
280 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | JackRunTimHour | SIL0 | MODBUS:3:Read:Holding Registers | 2135 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10155 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_13JackRunTimHour | 4 |  |  | 0 | $ComStatus , , | #Running Time HOUR MLC 1
281 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | JackAla | SIL0 | MODBUS:3:Read:Holding Registers | 2131 | 7 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10152 | 7 | 1 | deiJCKOMF05MLJ_RoomJCK_13JackAla | 4 |  |  | 0 | $ComStatus , , | #Alarm MLC 1
282 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | JackServStatus | SIL0 | MODBUS:3:Read:Holding Registers | 2131 | 8 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10152 | 8 | 1 | deiJCKOMF05MLJ_RoomJCK_13JackServStatus | 4 |  |  | 0 | $ComStatus , , | #In service MLC 1
283 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | JackEmerStopAla | SIL0 | MODBUS:3:Read:Holding Registers | 2131 | 9 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10152 | 9 | 1 | deiJCKOMF05MLJ_RoomJCK_13JackEmerStopAla | 4 |  |  | 0 | $ComStatus , , | #Emergency Stop MLC 1
284 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | JackNutFaulAla | SIL0 | MODBUS:3:Read:Holding Registers | 2131 | 10 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10152 | 10 | 1 | deiJCKOMF05MLJ_RoomJCK_13JackNutFaulAla | 4 |  |  | 0 | $ComStatus , , | #Nut Fault MLC 1
285 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | JackObstAla | SIL0 | MODBUS:3:Read:Holding Registers | 2131 | 11 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10152 | 11 | 1 | deiJCKOMF05MLJ_RoomJCK_13JackObstAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Obstruction MLC 1
286 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | JackLoadMissAla | SIL0 | MODBUS:3:Read:Holding Registers | 2131 | 12 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10152 | 12 | 1 | deiJCKOMF05MLJ_RoomJCK_13JackLoadMissAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Load missing MLC 1
287 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | JackImpSensAla | SIL0 | MODBUS:3:Read:Holding Registers | 2131 | 13 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10152 | 13 | 1 | deiJCKOMF05MLJ_RoomJCK_13JackImpSensAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Impulse Sensor MLC 1
288 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | JackMotorAla | SIL0 | MODBUS:3:Read:Holding Registers | 2131 | 14 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10152 | 14 | 1 | deiJCKOMF05MLJ_RoomJCK_13JackMotorAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Motorprotection MLC 1
289 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | JackSyncAla | SIL0 | MODBUS:3:Read:Holding Registers | 2131 | 15 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10152 | 15 | 1 | deiJCKOMF05MLJ_RoomJCK_13JackSyncAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Synchronisation MLC 1
290 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | JackContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2132 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10156 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_13JackContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Contactor MLC 1
291 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_13 | 15 | JackFlooContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2132 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10156 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_13JackFlooContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Floor Contact MLC 1
292 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | Avail | SIL0 | MODBUS:3:Read:Holding Registers | 2141 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10162 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_14Avail | 4 |  |  | 0 | $ComStatus , , | #Power Supply MLC 1
293 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | LowLim | SIL0 | MODBUS:3:Read:Holding Registers | 2141 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10162 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_14LowLim | 4 |  |  | 0 | $ComStatus , , | #Park Position MLC 1
294 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | UpLim | SIL0 | MODBUS:3:Read:Holding Registers | 2141 | 2 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10162 | 2 | 1 | deiJCKOMF05MLJ_RoomJCK_14UpLim | 4 |  |  | 0 | $ComStatus , , | #Top Position MLC 1
295 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | LoadAvai | SIL0 | MODBUS:3:Read:Holding Registers | 2141 | 3 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10162 | 3 | 1 | deiJCKOMF05MLJ_RoomJCK_14LoadAvai | 4 |  |  | 0 | $ComStatus , , | #Load on MLC 1
296 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | JackRis | SIL0 | MODBUS:3:Read:Holding Registers | 2141 | 4 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10162 | 4 | 1 | deiJCKOMF05MLJ_RoomJCK_14JackRis | 4 |  |  | 0 | $ComStatus , , | #Rising MLC 1
297 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | JackDesc | SIL0 | MODBUS:3:Read:Holding Registers | 2141 | 5 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10162 | 5 | 1 | deiJCKOMF05MLJ_RoomJCK_14JackDesc | 4 |  |  | 0 | $ComStatus , , | #Descending MLC 1
298 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | JackStanOnFloo | SIL0 | MODBUS:3:Read:Holding Registers | 2141 | 6 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10162 | 6 | 1 | deiJCKOMF05MLJ_RoomJCK_14JackStanOnFloo | 4 |  |  | 0 | $ComStatus , , | #Standing on Floor MLC 1
299 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | JackHeighVal | SIL0 | MODBUS:3:Read:Holding Registers | 2143 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10163 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_14JackHeighVal | 4 |  |  | 0 | $ComStatus , , | #Height value MLC 1
300 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | JackRunTimMin | SIL0 | MODBUS:3:Read:Holding Registers | 2144 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10164 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_14JackRunTimMin | 4 |  |  | 0 | $ComStatus , , | #Running Time MIN MLC 1
301 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | JackRunTimHour | SIL0 | MODBUS:3:Read:Holding Registers | 2145 | 0 | 16 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | AEIV | 3 | 1 | 10165 | 0 | 16 | aeiJCKOMF05MLJ_RoomJCK_14JackRunTimHour | 4 |  |  | 0 | $ComStatus , , | #Running Time HOUR MLC 1
302 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | JackAla | SIL0 | MODBUS:3:Read:Holding Registers | 2141 | 7 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10162 | 7 | 1 | deiJCKOMF05MLJ_RoomJCK_14JackAla | 4 |  |  | 0 | $ComStatus , , | #Alarm MLC 1
303 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | JackServStatus | SIL0 | MODBUS:3:Read:Holding Registers | 2141 | 8 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10162 | 8 | 1 | deiJCKOMF05MLJ_RoomJCK_14JackServStatus | 4 |  |  | 0 | $ComStatus , , | #In service MLC 1
304 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | JackEmerStopAla | SIL0 | MODBUS:3:Read:Holding Registers | 2141 | 9 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10162 | 9 | 1 | deiJCKOMF05MLJ_RoomJCK_14JackEmerStopAla | 4 |  |  | 0 | $ComStatus , , | #Emergency Stop MLC 1
305 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | JackNutFaulAla | SIL0 | MODBUS:3:Read:Holding Registers | 2141 | 10 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10162 | 10 | 1 | deiJCKOMF05MLJ_RoomJCK_14JackNutFaulAla | 4 |  |  | 0 | $ComStatus , , | #Nut Fault MLC 1
306 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | JackObstAla | SIL0 | MODBUS:3:Read:Holding Registers | 2141 | 11 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10162 | 11 | 1 | deiJCKOMF05MLJ_RoomJCK_14JackObstAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Obstruction MLC 1
307 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | JackLoadMissAla | SIL0 | MODBUS:3:Read:Holding Registers | 2141 | 12 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10162 | 12 | 1 | deiJCKOMF05MLJ_RoomJCK_14JackLoadMissAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Load missing MLC 1
308 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | JackImpSensAla | SIL0 | MODBUS:3:Read:Holding Registers | 2141 | 13 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10162 | 13 | 1 | deiJCKOMF05MLJ_RoomJCK_14JackImpSensAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Impulse Sensor MLC 1
309 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | JackMotorAla | SIL0 | MODBUS:3:Read:Holding Registers | 2141 | 14 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10162 | 14 | 1 | deiJCKOMF05MLJ_RoomJCK_14JackMotorAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Motorprotection MLC 1
310 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | JackSyncAla | SIL0 | MODBUS:3:Read:Holding Registers | 2141 | 15 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10162 | 15 | 1 | deiJCKOMF05MLJ_RoomJCK_14JackSyncAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Synchronisation MLC 1
311 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | JackContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2142 | 0 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10166 | 0 | 1 | deiJCKOMF05MLJ_RoomJCK_14JackContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Contactor MLC 1
312 | OMF09_RTU | JCK:OMF05 | MLJ_Room | JCK | JCK_14 | 16 | JackFlooContAla | SIL0 | MODBUS:3:Read:Holding Registers | 2142 | 1 | 1 |  |  | OMF05-SIL0 | JCK | OMF09_RTU.dat | DEIV | 3 | 1 | 10166 | 1 | 1 | deiJCKOMF05MLJ_RoomJCK_14JackFlooContAla | 4 |  |  | 0 | $ComStatus , , | #Jacks Floor Contact MLC 1
-END-

## A-Validation Data list
RTU_Protocol_Operation_Code | Memory_Block | RTU_Protocol | Operation Code List | Association with Memory Block | RTU_Undefined_Operation_Code | RTU_Undefined_Operation_Code | RTU_Modbus_Operation_Code | Modbus_Memory_Block | RTU_IEC104_Operation_Code | IEC104_Memory_Block | RTU_Data_Check_Function | RTU_Data_Translation_Function | Bit_Position
MODBUS:1:Read:Coils | MODBUS:MEMBLOCK01 | MODBUS-TCP | SE_RTU_Modbus_Operation_Code | SE_RTU_Modbus_Table |  |  | MODBUS:1:Read:Coils | MODBUS:MEMBLOCK01 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | cfRANGE | tfNOT | 0
MODBUS:2:Read:Discrete Inputs | MODBUS:MEMBLOCK02 | MODBUS-RTU | SE_RTU_Modbus_Operation_Code | SE_RTU_Modbus_Table |  |  | MODBUS:2:Read:Discrete Inputs | MODBUS:MEMBLOCK02 | IEC104:M_DP_NA_1 | IEC104:MEMBLOCK01 |  | tfLIN | 1
MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | IEC60870-5-104 | SE_RTU_IEC104_Operation_Code | SE_RTU_IEC104_Table |  |  | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 |  | BTL32 | 2
MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | IEC60870-5-101 | SE_RTU_IEC104_Operation_Code | SE_RTU_IEC104_Table |  |  | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | IEC104:M_ME_NB_1 | IEC104:MEMBLOCK01 |  | LTB16 | 3
MODBUS:5:Write:Coil | MODBUS:MEMBLOCK01 | DNP3.0 | SE_RTU_Undefined_Operation_Code | SE_RTU_Undefined_Table |  |  | MODBUS:5:Write:Coil | MODBUS:MEMBLOCK01 | IEC104:M_ME_NC_1 | IEC104:MEMBLOCK01 |  | USHORT | 4
MODBUS:6:Write:Holding Register | MODBUS:MEMBLOCK03 | BACNET-TCP | SE_RTU_Undefined_Operation_Code | SE_RTU_Undefined_Table |  |  | MODBUS:6:Write:Holding Register | MODBUS:MEMBLOCK03 | IEC104:M_IT_NA_1 | IEC104:MEMBLOCK01 |  |  | 5
MODBUS:15:Write:Coils | MODBUS:MEMBLOCK01 |  | SE_RTU_Undefined_Operation_Code | SE_RTU_Undefined_Table |  |  | MODBUS:15:Write:Coils | MODBUS:MEMBLOCK01 | IEC104:M_SP_TB_1 | IEC104:MEMBLOCK01 |  |  | 6
MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [5 empty] | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | IEC104:M_DP_TB_1 | IEC104:MEMBLOCK01 |  |  | 7
IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SC_NA_1 | IEC104:MEMBLOCK01 |  |  | 8
IEC104:M_DP_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 |  |  | 9
IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_RC_NA_1 | IEC104:MEMBLOCK01 |  |  | 10
IEC104:M_ME_NB_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SE_NA_1 | IEC104:MEMBLOCK01 |  |  | 11
IEC104:M_ME_NC_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SE_NB_1 | IEC104:MEMBLOCK01 |  |  | 12
IEC104:M_IT_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SE_NC_1 | IEC104:MEMBLOCK01 |  |  | 13
IEC104:M_SP_TB_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_IC_NA_1 | IEC104:MEMBLOCK01 |  |  | 14
IEC104:M_DP_TB_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_CI_NA_1 | IEC104:MEMBLOCK01 |  |  | 15
IEC104:C_SC_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_RD_NA_1 | IEC104:MEMBLOCK01 |  |  | 16
IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 17
IEC104:C_RC_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 18
IEC104:C_SE_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 19
IEC104:C_SE_NB_1 | IEC104:MEMBLOCK01 | [11 empty] | 20
IEC104:C_SE_NC_1 | IEC104:MEMBLOCK01 | [11 empty] | 21
IEC104:C_IC_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 22
IEC104:C_CI_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 23
IEC104:C_RD_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 24
25
|  | Check of Validation Lists | [10 empty] | 26
|  | PLC Protocol | Available Operation Code | [9 empty] | 27
|  | IEC60870-5-104 | IEC104:M_ME_NA_1 | [9 empty] | 28
|  | MODBUS-RTU | MODBUS:4:Read:Input Registers | [9 empty] | 29
30
31
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
Note on E1: BERNARD Olivier: This column identifies the list to the associated operation codes. This list is defined through a name (Excel Formula name)

## B-Address Qty
FC / Class Name | MLJ | JCK
MODBUS:1:Read:Coils | 40;1000 | 40;1000
MODBUS:2:Read:Discrete Inputs | 40;5000 | 40;5000
MODBUS:3:Read:Holding Registers | 10;10000 | 10;10000
MODBUS:4:Read:Input Registers | 10;20000 | 10;20000
MODBUS:5:Write:Coil | 20;1000 | 20;1000
MODBUS:6:Write:Holding Register | 20;10000 | 20;10000
MODBUS:15:Write:Coils | 20;1000 | 20;1000
MODBUS:16:Write:Holding Registers | 20;10000 | 20;10000
IEC104:M_SP_NA_1 | 40;1000 | 40;1000
IEC104:M_DP_NA_1 | 40;4000 | 40;4000
IEC104:M_ME_NA_1 | 40;7000 | 40;7000
IEC104:M_ME_NB_1 | 40;10000 | 40;10000
IEC104:M_ME_NC_1 | 40;13000 | 40;13000
IEC104:M_IT_NA_1 | 40;16000 | 40;16000
IEC104:M_SP_TB_1 | 40;17000 | 40;17000
IEC104:M_DP_TB_1 | 40;20000 | 40;20000
IEC104:C_SC_NA_1 | 20;23000 | 20;23000
IEC104:C_DC_NA_1 | 20;25000 | 20;25000
IEC104:C_RC_NA_1 | 20;27000 | 20;27000
IEC104:C_SE_NA_1 | 20;28000 | 20;28000
IEC104:C_SE_NB_1 | 20;29000 | 20;29000
IEC104:C_SE_NC_1 | 20;30000 | 20;30000
IEC104:C_IC_NA_1 | 20;31000 | 20;31000
IEC104:C_CI_NA_1
IEC104:C_RD_NA_1