## Revision
Revision
Date | Version | Author | Observations
42418 | v0 | C.CAMARA | Creation (from v4.2) | CHANGE TO :
42476 | A- | C.CAMARA | Updated version following QVDC Comment
42901 | A1 | T.MARTINEZ | Updated version with new templates
43074 | A2 | T.MARTINEZ | Update with v0.36 template Update with DSFS statuses
43080 | A2 | Klein | Update DSFS Status
43108 | A2 | T.MARTINEZ | -Update DSFS status - Generate Swcode ID -Generate Adresses Modbus -Filled column BH to BK.
43109 | A2 | T.MARTINEZ | -Change modbus Function code from 4 to 3
43125 | A2 | Klein | Update chapter: 10-PLC Points: column "point-address", "start_bit", "nb_bits"
43149 | B- | T.MARTINEZ | Align on Template v0.37
43299 | B- | J.LAW | Class List 1. Update Default Value 2. Shorten the long Point Description
Partners view

## Introduction
Introduction
For all ICD relative to equipment monitoring & control , this ECI (Equipment Classes & Instances) file template must be used as appendix to define: - the equipment classes, from an I/O point of view - all instances relative to each class
Recommandations
1 | Use one ECI file for each ICD document (one ICD=one subsystem)
2 | Do not change the organisation of the ECI file:
- Sheet "Equipment classes" : define all classes for the relative subsystem (see meaning of each field in the "Definitions" sheet)
- Sheet "Equipment instances" : define all instances for the relative subsystem (see meaning of each field in the "Definitions" sheet)
3 | For each sheet, do not change the organisation of the sheet (does not remove any column) in order to be able to use the standard export/import tools
4 | Create the necessary number of classes: for example, if similar equipment have different numbers of DI, DO, AI, create one class for each case
5 | Define, if possible, contiguous addresses for equipments/points within the same class.
Use the internal macro (### to be implemented in next release ###) to check the consistency of all data included in the sheet "Equipment classes" and "Equipment instances"
Notes
Issues to be addressed in future release
## Use appropriate point & bit value descriptions to create alarm label (DI) #####
### define rules for separators

## Definitions
Subsystem TVS - Equipment classes & instances
Definitions
1-Class List
Column Class | Column Name | Column Description | Values
| Revision | Identifiy the IO revision in witch the information was added , deleted or modified | version (string)
| isAComment | Specify whether the line is a comment or not | Y or N
EQUIPMENT CLASSES
| System | Define the trigram of the system's name in which the equipment is included | XXX
| Sub-system | Define the trigram of the sub-system's name in which the equipment is included | XXX
| Class name | Short equipment name on XXX characters number (minimum 3 characters - maximum 12 characters)
| CSS Point Name | Normalized name, used within the SCADA
EXTERNAL SYSTEM DATA
| Point Name | Name of equipment point from supplier
| Point Description | Any useful documentation on the point
| Point Type | Point can be qualified as Event or Alarm. Operational are not sent to MMS, Technical and Meter are sent to MMS. Hence, supported values are | Operational Event |  | Event which are from the nominal mode of the equipment. For exmaple open/close, locked/unlocked …
|  |  | Operational Alarm |  | Alarm that are from the nominal operation mode of the equipment. For example operator changing mode which put the equipment in Alarm state or equipment changing its status triggering an alarm.
|  |  | Technical Alarm |  | Alarm that deviated from the nominal operation mode. For example all detect fault. These are not part of the system nominal behavior
|  |  | Meter |  | Event which are needed for maintenance procedures.
Command
| Frequency | Time interval between data transmissions from SCADA to MMS | Daily
Weekly
Monthly
| Data Type | Digital Input | DI | 1 | bit
|  |  | DI2 | 2 | bits
|  | Digital Output | DO | 1 | bits
|  |  | DO2 | 2 | bits
|  | Analog Input | AI | 16 | bits
|  |  | AI2 | 32 | bits
|  | Analog Output | AO | 16 | bits
|  |  | AO2 | 32 | bits
EXTERNAL SYSTEM DATA DETAILS
| SIL Level | Identify the SIL level for the equipment point which can be | SIL0
SIL2_Monitoring
SIL2_Control
| Protocol | Applicable protocol: may be Modbus or IEC104
| Operation code | Operation code needed to manage the point at protocol level
| Memory Block | TODO
DI POINT
| DI/DI2 Value = 0 | For a DI or DI2, definition of the supervised status when the value is set to 0
| DI/DI2 Value = 1 | For a DI or DI2, definition of the supervised status when the value is set to 1
| DI2 Value = 2 | For a DI2, definition of the supervised status when the value is set to 2
| DI2 Value = 3 | For a DI2, definition of the supervised status when the value is set to 3
| Default value | Default value of the equipment point
| Alarm severity | Define the alarm severity for each value with the format (value1: severity label 1, value2: severity label 2, etc) Severity labels are: - None for events - Min for Minor alarms - Maj for Major alarms - Crit for Critical alarms Example: - 0: None, 1: Maj - 0: None, 1: None
| Alarm label | This label will be presented to the operators on the HMI for english language. It consists of: CCS Point Name: DI value when=0 / DI value when=1 / …
DO POINT
| DO/DO2 Value = 0 | For a DO or DO2, definition of the supervised status when the value is set to 0
| DO/DO2 Value = 1 | For a DO or DO2, definition of the supervised status when the value is set to 1
| DO2 Value = 2 | For a DO2, definition of the supervised status when the value is set to 2
| DO2 Value = 3 | For a DO2, definition of the supervised status when the value is set to 3
| Default value | Define the default value of the equipment point
| Output duration (ms) | Give the properties of the output signal command in ms: <empty>: continuous signal integer value: temporal duration of the pulse (in ms)
| Timeout for reaction (s) | Expected response time between the command sending and the modification of the associated status
| Initial condition | Pre-condition to be checked before sending the command
| Final condition | Post-condition to be checked to make sure the command is successful
| Associated return status | Return equipment status associated with the command
AI POINT
| Unit | Give the measurement unity of the analog data
| Min value | Define the minimum value of the data
| Max value | Define the maximum value of the data
| Limit 1 (optional) | Threshold in order to add range of the supervised value between min and max values
| Limit 2 (optional) | Threshold in order to add range of the supervised value between min and max values
In the template, alarm thresholds are defined through two value limits plus a minimum value and a maximum value. As shown in the figure on the right, this defines 5 ranges for which an alarm may be defined
| Range <i> alarm severity | Define the alarm severity for a range Severity labels are: - None for events - Min for Minor alarms - Maj for Major alarms - Crit for Critical alarms
| Range <i> alarm label | Define the alarm label for a range
| Dead band | Define the tolerance of variation around a threshold
| Default value | Define the default value of the equipment point
| Alarm label | This label will be presented to the operators on the HMI. It consists on: Equipment description (displayed in HMI): under Min value / under Max value / etc.
AO POINT
| Unit | Give the measurement unity of the analog data
| Range Min value | Define the minimum range of the command value
| Range Max value | Define the maximum range of the command value
| Output duration (ms) | Give the properties of the output signal command in ms: Nothing to fill: continuous signal XXX: temporal duration of the pulse
| Timeout for reaction (s) | Response time between the command and the associated status modification on the equipment
| Initial condition | Conditions to verify before sending the command
| Final condition | Conditions to verify after the sending of the command
| Associated return status | Return equipment status associated with the command
2-Instance List
Column Class | Column Name | Column Description
| Revision | Identifiy the IO revision in witch the information was added , deleted or modified
| GBS Code | TBC
| LBS Code (LRT) | TBC
| LBS Code (QRC) | TBC
| Description | Textual description or precision about the Location/sublocation of the equipment instance
| Location | Define in a short designation the geographical location in which the equipment is based
| Sublocation | Define in a short designation the sublocation (Subsystem / Level / Building / room) in which the equipment is based
| Class name | Class name identical to the class name defined in the "1-Class List" tab
| Equipment name | Give the instance name of the equipment.
| RTU Name | Name of the concentrator (as viewed in the SCADA subsystem) for the equipment
| PLC Name | Name of the partner PLC
| InvalidVar1 | name of the first external variable used to invalidate this equipement (usually comStatus of the gateway or PRTU)
| InvalidVar2 | name of the second external variable used to invalidate this equipement (usually comStatus of the gateway or PRTU)
| InvalidVar3 | name of the third external variable used to invalidate this equipement (usually comStatus of the gateway or PRTU)

## Generation
Execute |  | To do before Generation => Check that there are no ROW filters set in the Class and instance worksheets
Tool version | v2.0
Generation Time: | 1/9/2018 at 5:14:07 PM
Found Classes: | 7
Found Errors: | 0
Found Warnings: | 0
Not Found Classes: | 0
Generate Points
Fill Code & Index Address

## 1-Class List
|  | EQUIPMENT CLASSES |  |  |  | EXTERNAL SYSTEM DATA |  |  |  |  | EXTERNAL SYSTEM DATA DETAILS |  |  |  | DI or DI2 | [6 empty] | DO | [8 empty] | AI | [17 empty] | AO | [8 empty] | MMS | SE Engineering |  |  |  | SW Engineering | HMI details (dictionnaries)
Revision | isAComment | System | Sub-system | Class name | CSS Point Name | Point Name | Point Description | Point Type | Frequency | Data Type | SIL Level | Protocol | Operation code (FC, ASDU, ...) | Memory Block | DI or DI2 value = 0 (00) | DI or DI2 value = 1(01) | DI2 value = 2 (10) | DI2 value = 3 (11) | Default value | Alarm severity | Alarm label | DO or DO2 value = 0 (00) | DO or DO2 value = 1(01) | DO2 value = 2 (10) | DO2 value = 3 (11) | Output duration (ms) | Timeout for reaction (s) | Initial condition | Final condition | Associated return status | Unit | Min value | Max value | Limit 1 (optional) | Limit 2 (optional) | Range 1 alarm severity ] -∞,min value] | Range 1 alarm label ] -∞,min value] | Range 2 alarm severity ]min value,limit1] | Range 2 alarm label ]min value,limit1] | Range 3 alarm severity ]limit1,limit2] | Range 3 alarm label ]limit1,limit2] | Range 4 alarm severity ]limit2,max value] | Range 4 alarm label ]limit2,max value] | Range 5 alarm severity ]max value,+∞[ | Range 5 alarm label ]max value,+∞[ | Dead band | Default value | Formula | Unit | Range Min value | Range Max value | Output duration (ms) | Timeout for reaction (s) | Initial condition | Final condition | Associated return status | Formula | [Lusail] PBS code | Data Length | Index Address | Bit position | IsAnimated | Code | System (Native language) | Sub-system (Native language) | Class name (Native language) | Equipment description (displayed in HMI) (Native language) | Description (Details of description) (Native language)
| Y | This part should be filled up by System Engineering and gives the indication on how to modelize prototypes
| Y |  |  |  | Filter System
A1.2 | N | DSFS | DSFS | FSY | emergency off filter | emergency off filter | emergency off filter | Technical Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Inactive | Active |  |  | Inactive | 0: None, 1: Crit | emergency off filter: Inactive / Active | [37 empty] | 1 | 0 | 0 | NO | EmeOffFil
A1.2 | N | DSFS | DSFS | FSY | repair switch vibrator off | repair switch vibrator off | repair switch vibrator off | Technical Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Inactive | Active |  |  | Inactive | 0: None, 1: Maj | repair switch vibrator off: Inactive / Active | [37 empty] | 1 | 0 | 1 | NO | RepSwiVibOff
A1.2 | N | DSFS | DSFS | FSY | repair switch ventilator off | emergency off filter | repair switch ventilator off | Technical Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Inactive | Active |  |  | Inactive | 0: None, 1: Maj | emergency off filter: Inactive / Active | [37 empty] | 1 | 0 | 2 | NO | RepSwiVenOff
A1.2 | N | DSFS | DSFS | FSY | Malfunction vibration drive(motor protection switch tripped) | Malfunction vibration drive(motor protection switch tripped) | Malfunction vibration drive(motor protection switch tripped) | Technical Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Normal | Alarm |  |  | Normal | 0: None, 1: Maj | Malfunction vibration drive(motor protection switch tripped): Normal / Alarm | [37 empty] | 1 | 0 | 3 | NO | MalVibDri
A1.2 | N | DSFS | DSFS | FSY | Malfunction vibration drive(motor protection switch tripped) | Malfunction vibration drive(motor protection switch tripped) | Malfunction vibration drive(motor protection switch tripped) | Technical Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Normal | Alarm |  |  | Normal | 0: None, 1: Maj | Malfunction vibration drive(motor protection switch tripped): Normal / Alarm | [37 empty] | 1 | 0 | 4 | NO | MalVenDri
| Y |  |  |  | Switch Cabinet: power supply and sub-distribution
A1.2 | N | DSFS | DSFS | SWCA | Main power status | control voltage on-off | control voltage on-off |  |  | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | OFF | ON |  |  | ON | 0: Crit, 1: None | control voltage on-off: OFF / ON | [37 empty] | 1 | 1 | 0 | NO | MaiPowSta
A1.2 | N | DSFS | DSFS | SWCA | Emergency off switch cabinet | emergency off switch cabinet | emergency off switch cabinet |  |  | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Inactive | Active |  |  | Inactive | 0: None, 1: Crit | emergency off switch cabinet: Inactive / Active | [37 empty] | 1 | 1 | 1 | NO | EmeOffSwi
| Y |  |  |  | Switch Cabinet: PLC
A1.2 | N | DSFS | DSFS | PLC | Sand-plant power status | sand-plant off-on | sand-plant off-on | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | OFF | ON |  |  | ON | 0: Min, 1: None | sand-plant off-on: OFF / ON | [37 empty] | 1 | 2 | 0 | NO | SanPltPow
A1.2 | N | DSFS | DSFS | PLC | Compressed air existing | compressed air existing | compressed air existing | Technical Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Inactive | Active |  |  | Active | 0: Crit, 1: None | compressed air existing: Inactive / Active | [37 empty] | 1 | 2 | 1 | NO | ComAirExi
A1.2 | N | DSFS | DSFS | PLC | Collection fault | collection fault | collection fault | Technical Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Inactive | Active |  |  | Inactive | 0: None, 1: Crit | collection fault: Inactive / Active | [37 empty] | 1 | 2 | 2 | NO | ColFau
A1.2 | N | DSFS | DSFS | PLC | Sand filling conveyor counter cycle 1 | sand filling conveyor counter cycle 1 | sand filling conveyor counter cycle 1 | Meter | Daily | AI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | [16 empty] | Count | 0 | 65635 | [25 empty] | 16 | 3 | 0 | NO | SanFilCon1
A1.2 | N | DSFS | DSFS | PLC | Sand filling conveyor counter cycle 2 | sand filling conveyor counter cycle 2 | sand filling conveyor counter cycle 2 | Meter | Daily | AI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | [16 empty] | Count | 0 | 65635 | [25 empty] | 16 | 4 | 0 | NO | SanFilCon2
| Y |  |  |  | Silo Installation
A1.2 | N | DSFS | DSFS | SILO | Pre lock open silo filling | pre lock open silo filling | pre lock open silo filling | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Inactive | Active |  |  | Inactive | 0: None, 1: None | pre lock open silo filling: Inactive / Active | [37 empty] | 1 | 5 | 0 | NO | PreLokOp
A1.2 | N | DSFS | DSFS | SILO | Pre lock closed silo filling | pre lock closed silo filling | pre lock closed silo filling | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Inactive | Active |  |  | Active | 0: None, 1: None | pre lock closed silo filling: Inactive / Active | [37 empty] | 1 | 5 | 1 | NO | PreLokClo
A1.2 | N | DSFS | DSFS | SILO | Filling level request | filling level request | filling level request | Technical Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Inactive | Active |  |  | Active | 0: Maj, 1: None | filling level request: Inactive / Active | [37 empty] | 1 | 5 | 2 | NO | FilLevReq
A1.2 | N | DSFS | DSFS | SILO | filling level max | filling level max | filling level max | Technical Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Active | Inactive |  |  | Inactive | 0: Maj, 1: None | filling level max: Active / Inactive | [37 empty] | 1 | 5 | 3 | NO | FilLevMax
A1.2 | N | DSFS | DSFS | SILO | filling level min | filling level min | filling level min | Technical Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Inactive | Active |  |  | Active | 0: Crit, 1: None | filling level min: Inactive / Active | [37 empty] | 1 | 5 | 4 | NO | FilLevMin
A1.2 | N | DSFS | DSFS | SILO | limit switch filling nozzle | limit switch filling nozzle | limit switch filling nozzle | Technical Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Inactive | Active |  |  | Inactive | 0: None, 1: Maj | limit switch filling nozzle: Inactive / Active | [37 empty] | 1 | 5 | 5 | NO | LimSwiFilNoz
| Y |  |  |  | Pneumatic conveyor
A1.2 | N | DSFS | DSFS | PNCO | Collection conveyor status | collection fault conveyor 1 | collection fault conveyor 1 | Technical Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | Normal | Faulty |  |  | Normal | 0: None, 1: Maj | collection fault conveyor 1: Normal / Faulty | [37 empty] | 1 | 6 | 0 | NO | ColConSta
| Y |  |  |  | Sand Filling station 1
A1.2 | N | DSFS | DSFS | SFST | Sand level in station | filling level max station 1 | filling level max station 1 | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | MIN | MAX |  |  | Active (sand is present) | 0: None, 1: None | filling level max station 1: MIN / MAX | [37 empty] | 1 | 7 | 0 | NO | SanLevSta
Note on T6: Jason Law: Inactive (repair switch vibrator is on)
Note on T7: Jason Law: Inactive (repair switch ventilator is on)
Note on T8: Jason Law: Inactive (motor protection switch is on)
Note on T9: Jason Law: Inactive (motor protection switch is on)
Note on T11: Jason Law: Active (control voltage on)
Note on T14: Jason Law: Active (sand plant is on)
Note on T15: Jason Law: Active (compressed air existing)
Note on H17: Jason Law: sand filling conveyor counter cycle 1 will be incremented (+1) when the conveyor has transported one charge to the sand filling stations
Note on H18: Jason Law: sand filling conveyor counter cycle 1 will be incremented by (+1) when the conveyor has transported one charge to the sand filling stations
Note on T20: Jason Law: Inactive (closed)
Note on T21: Jason Law: Active (closed)
Note on T22: Jason Law: Active (sand is present)
Note on T23: Jason Law: Inactive (Sand is not present)
Note on T24: Jason Law: Active (sand is present)
Note on T27: Jason Law: Inactive
Note on T29: Jason Law: Active (sand is present)

## 2-Instance List
|  | LRT/QRC DESIGNATION |  |  |  | EQUIPMENT INSTANCES | [9 empty] | PRTU Configuration
Revision | isAComment | [Lusail] GBS Code | [Lusail] LBS Code LRT Designation Code | [Lusail] LBS Code QRC Designation Code | Description | Location | Sublocation | Class name | Equipment name | RTU Name | PLC Name | InvalidVar1 | InvalidVar2 | InvalidVar3 | Avalanche Condition | Instance Id | External System Name | Device Unit Id | FEP Name | FEP instance Id | Short name | hvId | SCADA Transfert function (Internal THALES) | Address | Description (Native language) | ToBeInstantiated
B.3 | Y |  |  |  |  | ROOT Location | [19 empty] | N
B.3 | Y |  |  |  | root node | DPT |  | Hierarchy | [17 empty] | N
B.3 | Y |  |  |  |  | Depot building OMF04 | [19 empty] | N
B.3 | Y |  |  |  |  | Hierarchy and locations (everything but equipments) | [19 empty] | N
B.3 | Y |  |  |  | root node |  |  | Hierarchy |  | - | [10 empty] | - | OMF04 |  |  |  | N
B.3 | Y |  |  |  | Depot Sanding Filling system | OMF04 | DSFS | FunctionalCat | DSFS | - | [10 empty] | - | OMF04:DSFS |  |  |  | N
B.3 | Y |  |  |  | ModBus Terminal Unit | OMF09 |  | FunctionalCat | MBT | - | [10 empty] | - |  |  |  |  | N
B.3 | Y |  |  |  |  | PRTU | [19 empty] | N
B.3 | Y |  |  |  | Modbus interface | OMF09 | MBT | RTU | Daccom | OMF09_RTU | [5 empty] | 1 | RTU | 1 |  |  | DacCom IEC |  |  |  |  | N
B.3 | Y |  |  |  |  | Depot Sanding Filling System (DSFS) | [19 empty] | N
B.3 | Y | ` |  |  |  | Filter System | [19 empty] | N
B.3 | N |  |  |  | DSFS | DSFS:OMF04 | DSFS_Room | FSY | FSY_1 | OMF09_RTU | [5 empty] | 2 | DSFS | 1 |  |  | &FSY-1 | DSFS_OMF04_DSFS_Room_FSY_1 |  |  |  | Y
B.3 | Y |  |  |  |  | Depot Sanding Filling System (DSFS) | [19 empty] | N
B.3 | N |  |  |  | DSFS | DSFS:OMF04 | DSFS_Room | SWCA | SWCA_1 | OMF09_RTU | [5 empty] | 3 | DSFS | 1 |  |  | &SWCA-1 | DSFS_OMF04_DSFS_Room_SWCA_1 |  |  |  | Y
B.3 | Y |  |  |  |  | Depot Sanding Filling System (DSFS) | [19 empty] | N
B.3 | N |  |  |  | DSFS | DSFS:OMF04 | DSFS_Room | PLC | PLC_1 | OMF09_RTU | [5 empty] | 4 | DSFS | 1 |  |  | &PLC-1 | DSFS_OMF04_DSFS_Room_PLC_1 |  |  |  | Y
B.3 | Y |  |  |  |  | Depot Sanding Filling System (DSFS) | [19 empty] | N
B.3 | N |  |  |  | DSFS | DSFS:OMF04 | DSFS_Room | SILO | SILO_1 | OMF09_RTU | [5 empty] | 5 | DSFS | 1 |  |  | &SILO-1 | DSFS_OMF04_DSFS_Room_SILO_1 |  |  |  | Y
B.3 | Y |  |  |  |  | Depot Sanding Filling System (DSFS) | [19 empty] | N
B.3 | N |  |  |  | DSFS | DSFS:OMF04 | DSFS_Room | PNCO | PNCO_1 | OMF09_RTU | [5 empty] | 6 | DSFS | 1 |  |  | &PNCO-1 | DSFS_OMF04_DSFS_Room_PNCO_1 |  |  |  | Y
B.3 | N |  |  |  | DSFS | DSFS:OMF04 | DSFS_Room | PNCO | PNCO_2 | OMF09_RTU | [5 empty] | 7 | DSFS | 1 |  |  | &PNCO-2 | DSFS_OMF04_DSFS_Room_PNCO_2 |  |  |  | Y
B.3 | Y |  |  |  |  | Depot Sanding Filling System (DSFS) | [19 empty] | N
B.3 | N |  |  |  | DSFS | DSFS:OMF04 | DSFS_Room | SFST | SFST_1 | OMF09_RTU | [5 empty] | 8 | DSFS | 1 |  |  | &SFST-1 | DSFS_OMF04_DSFS_Room_SFST_1 |  |  |  | Y
B.3 | N |  |  |  | DSFS | DSFS:OMF04 | DSFS_Room | SFST | SFST_2 | OMF09_RTU | [5 empty] | 9 | DSFS | 1 |  |  | &SFST-2 | DSFS_OMF04_DSFS_Room_SFST_2 |  |  |  | Y
B.3 | N |  |  |  | DSFS | DSFS:OMF04 | DSFS_Room | SFST | SFST_3 | OMF09_RTU | [5 empty] | 10 | DSFS | 1 |  |  | &SFST-3 | DSFS_OMF04_DSFS_Room_SFST_3 |  |  |  | Y
B.3 | N |  |  |  | DSFS | DSFS:OMF04 | DSFS_Room | SFST | SFST_4 | OMF09_RTU | [5 empty] | 11 | DSFS | 1 |  |  | &SFST-4 | DSFS_OMF04_DSFS_Room_SFST_4 |  |  |  | Y
B.3 | N |  |  |  | DSFS | DSFS:OMF04 | DSFS_Room | SFST | SFST_5 | OMF09_RTU | [5 empty] | 12 | DSFS | 1 |  |  | &SFST-5 | DSFS_OMF04_DSFS_Room_SFST_5 |  |  |  | Y
B.3 | N |  |  |  | DSFS | DSFS:OMF04 | DSFS_Room | SFST | SFST_6 | OMF09_RTU | [5 empty] | 13 | DSFS | 1 |  |  | &SFST-6 | DSFS_OMF04_DSFS_Room_SFST_6 |  |  |  | Y
B.3 | N |  |  |  | DSFS | DSFS:OMF04 | DSFS_Room | SFST | SFST_7 | OMF09_RTU | [5 empty] | 14 | DSFS | 1 |  |  | &SFST-7 | DSFS_OMF04_DSFS_Room_SFST_7 |  |  |  | Y
B.3 | N |  |  |  | DSFS | DSFS:OMF04 | DSFS_Room | SFST | SFST_8 | OMF09_RTU | [5 empty] | 15 | DSFS | 1 |  |  | &SFST-8 | DSFS_OMF04_DSFS_Room_SFST_8 |  |  |  | Y
B.3 | N |  |  |  | DSFS | DSFS:OMF04 | DSFS_Room | SFST | SFST_9 | OMF09_RTU | [5 empty] | 16 | DSFS | 1 |  |  | &SFST-9 | DSFS_OMF04_DSFS_Room_SFST_9 |  |  |  | Y
B.3 | N |  |  |  | DSFS | DSFS:OMF04 | DSFS_Room | SFST | SFST_10 | OMF09_RTU | [5 empty] | 17 | DSFS | 1 |  |  | &SFST-10 | DSFS_OMF04_DSFS_Room_SFST_10 |  |  |  | Y
B.3 | N |  |  |  | DSFS | DSFS:OMF04 | DSFS_Room | SFST | SFST_11 | OMF09_RTU | [5 empty] | 18 | DSFS | 1 |  |  | &SFST-11 | DSFS_OMF04_DSFS_Room_SFST_11 |  |  |  | Y
B.3 | N |  |  |  | DSFS | DSFS:OMF04 | DSFS_Room | SFST | SFST_12 | OMF09_RTU | [5 empty] | 19 | DSFS | 1 |  |  | &SFST-12 | DSFS_OMF04_DSFS_Room_SFST_12 |  |  |  | Y

## 3-Class Mapping
Class name | Prototype | Aggregate name | Object type | isAComment | Scstype | Abbreviated Class name
FSY | LusialHK:LusDsfsFsy |  |  | N | LusDsfsFsyType | FSY
SWCA | LusialHK:LusDsfsSwca |  |  | N | LusDsfsSwcaType | SWCA
PLC | LusialHK:LusDsfsPlc |  |  | N | LusDsfsPlcType | PLC
SILO | LusialHK:LusDsfsSilo |  |  | N | LusDsfsSiloType | SILO
PNCO | LusialHK:LusDsfsPnco |  |  | N | LusDsfsPncoType | PNCO
SFST | LusialHK:LusDsfsSfst |  |  | N | LusDsfsSfstType | SFST

## 4-External Variables
Class name | iopath | vetype | ve_basename | description | address | EVGroup | Concentrator Suffix | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
FSY | dci-EmeOffFil:dac | DEIV | EmeOffFil | emergency off filter | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
FSY | dci-RepSwiVibOff:dac | DEIV | RepSwiVibOff | repair switch vibrator off | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
FSY | dci-RepSwiVenOff:dac | DEIV | RepSwiVenOff | repair switch ventilator off | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
FSY | dci-MalVibDri:dac | DEIV | MalVibDri | Malfunction vibration drive(motor protection switch tripped) | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
FSY | dci-MalVenDri:dac | DEIV | MalVenDri | Malfunction vibration drive(motor protection switch tripped) | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
SWCA | dci-MaiPowSta:dac | DEIV | MaiPowSta | control voltage on-off | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
SWCA | dci-EmeOffSwi:dac | DEIV | EmeOffSwi | emergency off switch cabinet | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
PLC | dci-SanPltPow:dac | DEIV | SanPltPow | sand-plant off-on | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
PLC | dci-ComAirExi:dac | DEIV | ComAirExi | compressed air existing | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
PLC | dci-ColFau:dac | DEIV | ColFau | collection fault | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
PLC | aci-SanFilCon1:aac | AEIV | SanFilCon1 | sand filling conveyor counter cycle 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
PLC | aci-SanFilCon2:aac | AEIV | SanFilCon2 | sand filling conveyor counter cycle 2 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
SILO | dci-PreLokOp:dac | DEIV | PreLokOp | pre lock open silo filling | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
SILO | dci-PreLokClo:dac | DEIV | PreLokClo | pre lock closed silo filling | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
SILO | dci-FilLevReq:dac | DEIV | FilLevReq | filling level request | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
SILO | dci-FilLevMax:dac | DEIV | FilLevMax | filling level max | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
SILO | dci-FilLevMin:dac | DEIV | FilLevMin | filling level min | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
SILO | dci-LimSwiFilNoz:dac | DEIV | LimSwiFilNoz | limit switch filling nozzle | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
PNCO | dci-ColConSta:dac | DEIV | ColConSta | collection fault conveyor 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
SFST | dci-SanLevSta:dac | DEIV | SanLevSta | filling level max station 1 | $VOID | VEE_SCADA1 | _S0 | 0 |  |  |  | 4 |  |  | N
Note on F1: HILDEBERT Rene: To be calculated from the instance List
Note on E12: Jason Law: sand filling conveyor counter cycle 1 will be incremented (+1) when the conveyor has transported one charge to the sand filling stations
Note on E13: Jason Law: sand filling conveyor counter cycle 1 will be incremented by (+1) when the conveyor has transported one charge to the sand filling stations

## 4-External Variables - SIL0
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
Note on F1: HILDEBERT Rene: To be calculated from the instance List

## 4-External Variables - SIL2MON
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
Note on F1: HILDEBERT Rene: To be calculated from the instance List

## 4-External Variables - SIL2CON
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
Note on F1: HILDEBERT Rene: To be calculated from the instance List

## 10-PLC Points
row_id | concentrator | location | sub_location | class_name | eqp_name | instance_id | attribute_code | sil_channel | operation_type | point_address | start_bit | nb_bits | Warning | Error | PRTU Name | SWC Name | Daccom Source File | Daccom Variable Type | FC Code / ASDU Type | Daccom Type Num | Protocol Address | Start Bit | Nb Bits | Daccom External Variable Name | field1 | field2 | field3 | field4 | field5 | External Var Comment
1 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | FSY | FSY_1 | 2 | EmeOffFil | SIL0 | MODBUS:3:Read:Holding Registers | 40001 | 0 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40001 | 0 | 1 | deiDSFSOMF04DSFS_RoomFSY_1EmeOffFil | 4 |  |  | 0 | $ComStatus , , | #emergency off filter
2 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | FSY | FSY_1 | 2 | RepSwiVibOff | SIL0 | MODBUS:3:Read:Holding Registers | 40001 | 1 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40001 | 1 | 1 | deiDSFSOMF04DSFS_RoomFSY_1RepSwiVibOff | 4 |  |  | 0 | $ComStatus , , | #repair switch vibrator off
3 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | FSY | FSY_1 | 2 | RepSwiVenOff | SIL0 | MODBUS:3:Read:Holding Registers | 40001 | 2 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40001 | 2 | 1 | deiDSFSOMF04DSFS_RoomFSY_1RepSwiVenOff | 4 |  |  | 0 | $ComStatus , , | #repair switch ventilator off
4 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | FSY | FSY_1 | 2 | MalVibDri | SIL0 | MODBUS:3:Read:Holding Registers | 40001 | 3 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40001 | 3 | 1 | deiDSFSOMF04DSFS_RoomFSY_1MalVibDri | 4 |  |  | 0 | $ComStatus , , | #malfunction vibration drive (motor protection switch has tripped)
5 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | FSY | FSY_1 | 2 | MalVenDri | SIL0 | MODBUS:3:Read:Holding Registers | 40001 | 4 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40001 | 4 | 1 | deiDSFSOMF04DSFS_RoomFSY_1MalVenDri | 4 |  |  | 0 | $ComStatus , , | #malfunction ventilator drive (motor protection switch has tripped)
6 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SWCA | SWCA_1 | 3 | MaiPowSta | SIL0 | MODBUS:3:Read:Holding Registers | 40001 | 5 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40001 | 5 | 1 | deiDSFSOMF04DSFS_RoomSWCA_1MaiPowSta | 4 |  |  | 0 | $ComStatus , , | #control voltage on-off
7 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SWCA | SWCA_1 | 3 | EmeOffSwi | SIL0 | MODBUS:3:Read:Holding Registers | 40001 | 6 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40001 | 6 | 1 | deiDSFSOMF04DSFS_RoomSWCA_1EmeOffSwi | 4 |  |  | 0 | $ComStatus , , | #emergency off switch cabinet
8 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | PLC | PLC_1 | 4 | SanPltPow | SIL0 | MODBUS:3:Read:Holding Registers | 40001 | 7 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40001 | 7 | 1 | deiDSFSOMF04DSFS_RoomPLC_1SanPltPow | 4 |  |  | 0 | $ComStatus , , | #sand-plant off-on
9 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | PLC | PLC_1 | 4 | ComAirExi | SIL0 | MODBUS:3:Read:Holding Registers | 40002 | 0 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40002 | 0 | 1 | deiDSFSOMF04DSFS_RoomPLC_1ComAirExi | 4 |  |  | 0 | $ComStatus , , | #compressed air existing
10 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | PLC | PLC_1 | 4 | ColFau | SIL0 | MODBUS:3:Read:Holding Registers | 40002 | 1 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40002 | 1 | 1 | deiDSFSOMF04DSFS_RoomPLC_1ColFau | 4 |  |  | 0 | $ComStatus , , | #collection fault
11 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | PLC | PLC_1 | 4 | SanFilCon1 | SIL0 | MODBUS:3:Read:Holding Registers | 40029 | 0 | 16 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | AEIV | 3 | 1 | 40029 | 0 | 16 | aeiDSFSOMF04DSFS_RoomPLC_1SanFilCon1 | 4 |  |  | 0 | $ComStatus , , | #sand filling conveyor counter cycle 1 will be incremented (+1), when the conveyor has transported one charge to the sand filling stations
12 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | PLC | PLC_1 | 4 | SanFilCon2 | SIL0 | MODBUS:3:Read:Holding Registers | 40031 | 0 | 16 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | AEIV | 3 | 1 | 40031 | 0 | 16 | aeiDSFSOMF04DSFS_RoomPLC_1SanFilCon2 | 4 |  |  | 0 | $ComStatus , , | #sand filling conveyor counter cycle 2 will be incremented (+1), when the conveyor has transported one charge to the sand filling stations
13 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SILO | SILO_1 | 5 | PreLokOp | SIL0 | MODBUS:3:Read:Holding Registers | 40002 | 2 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40002 | 2 | 1 | deiDSFSOMF04DSFS_RoomSILO_1PreLokOp | 4 |  |  | 0 | $ComStatus , , | #pre lock open silo filling
14 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SILO | SILO_1 | 5 | PreLokClo | SIL0 | MODBUS:3:Read:Holding Registers | 40002 | 3 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40002 | 3 | 1 | deiDSFSOMF04DSFS_RoomSILO_1PreLokClo | 4 |  |  | 0 | $ComStatus , , | #pre lock closed silo filling
15 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SILO | SILO_1 | 5 | FilLevReq | SIL0 | MODBUS:3:Read:Holding Registers | 40002 | 4 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40002 | 4 | 1 | deiDSFSOMF04DSFS_RoomSILO_1FilLevReq | 4 |  |  | 0 | $ComStatus , , | #filling level request
16 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SILO | SILO_1 | 5 | FilLevMax | SIL0 | MODBUS:3:Read:Holding Registers | 40002 | 5 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40002 | 5 | 1 | deiDSFSOMF04DSFS_RoomSILO_1FilLevMax | 4 |  |  | 0 | $ComStatus , , | #filling level max
17 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SILO | SILO_1 | 5 | FilLevMin | SIL0 | MODBUS:3:Read:Holding Registers | 40002 | 6 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40002 | 6 | 1 | deiDSFSOMF04DSFS_RoomSILO_1FilLevMin | 4 |  |  | 0 | $ComStatus , , | #filling level min
18 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SILO | SILO_1 | 5 | LimSwiFilNoz | SIL0 | MODBUS:3:Read:Holding Registers | 40002 | 7 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40002 | 7 | 1 | deiDSFSOMF04DSFS_RoomSILO_1LimSwiFilNoz | 4 |  |  | 0 | $ComStatus , , | #limit switch filling nozzle
19 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | PNCO | PNCO_1 | 6 | ColConSta | SIL0 | MODBUS:3:Read:Holding Registers | 40003 | 0 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40003 | 0 | 1 | deiDSFSOMF04DSFS_RoomPNCO_1ColConSta | 4 |  |  | 0 | $ComStatus , , | #collection fault conveyor 1
20 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | PNCO | PNCO_2 | 7 | ColConSta | SIL0 | MODBUS:3:Read:Holding Registers | 40003 | 1 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40003 | 1 | 1 | deiDSFSOMF04DSFS_RoomPNCO_2ColConSta | 4 |  |  | 0 | $ComStatus , , | #collection fault conveyor 1
21 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SFST | SFST_1 | 8 | SanLevSta | SIL0 | MODBUS:3:Read:Holding Registers | 40005 | 0 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40005 | 0 | 1 | deiDSFSOMF04DSFS_RoomSFST_1SanLevSta | 4 |  |  | 0 | $ComStatus , , | #filling level max station 1
22 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SFST | SFST_2 | 9 | SanLevSta | SIL0 | MODBUS:3:Read:Holding Registers | 40007 | 0 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40007 | 0 | 1 | deiDSFSOMF04DSFS_RoomSFST_2SanLevSta | 4 |  |  | 0 | $ComStatus , , | #filling level max station 1
23 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SFST | SFST_3 | 10 | SanLevSta | SIL0 | MODBUS:3:Read:Holding Registers | 40009 | 0 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40009 | 0 | 1 | deiDSFSOMF04DSFS_RoomSFST_3SanLevSta | 4 |  |  | 0 | $ComStatus , , | #filling level max station 1
24 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SFST | SFST_4 | 11 | SanLevSta | SIL0 | MODBUS:3:Read:Holding Registers | 40011 | 0 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40011 | 0 | 1 | deiDSFSOMF04DSFS_RoomSFST_4SanLevSta | 4 |  |  | 0 | $ComStatus , , | #filling level max station 1
25 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SFST | SFST_5 | 12 | SanLevSta | SIL0 | MODBUS:3:Read:Holding Registers | 40013 | 0 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40013 | 0 | 1 | deiDSFSOMF04DSFS_RoomSFST_5SanLevSta | 4 |  |  | 0 | $ComStatus , , | #filling level max station 1
26 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SFST | SFST_6 | 13 | SanLevSta | SIL0 | MODBUS:3:Read:Holding Registers | 40015 | 0 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40015 | 0 | 1 | deiDSFSOMF04DSFS_RoomSFST_6SanLevSta | 4 |  |  | 0 | $ComStatus , , | #filling level max station 1
27 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SFST | SFST_7 | 14 | SanLevSta | SIL0 | MODBUS:3:Read:Holding Registers | 40017 | 0 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40017 | 0 | 1 | deiDSFSOMF04DSFS_RoomSFST_7SanLevSta | 4 |  |  | 0 | $ComStatus , , | #filling level max station 1
28 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SFST | SFST_8 | 15 | SanLevSta | SIL0 | MODBUS:3:Read:Holding Registers | 40019 | 0 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40019 | 0 | 1 | deiDSFSOMF04DSFS_RoomSFST_8SanLevSta | 4 |  |  | 0 | $ComStatus , , | #filling level max station 1
29 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SFST | SFST_9 | 16 | SanLevSta | SIL0 | MODBUS:3:Read:Holding Registers | 40021 | 0 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40021 | 0 | 1 | deiDSFSOMF04DSFS_RoomSFST_9SanLevSta | 4 |  |  | 0 | $ComStatus , , | #filling level max station 1
30 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SFST | SFST_10 | 17 | SanLevSta | SIL0 | MODBUS:3:Read:Holding Registers | 40023 | 0 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40023 | 0 | 1 | deiDSFSOMF04DSFS_RoomSFST_10SanLevSta | 4 |  |  | 0 | $ComStatus , , | #filling level max station 1
31 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SFST | SFST_11 | 18 | SanLevSta | SIL0 | MODBUS:3:Read:Holding Registers | 40025 | 0 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40025 | 0 | 1 | deiDSFSOMF04DSFS_RoomSFST_11SanLevSta | 4 |  |  | 0 | $ComStatus , , | #filling level max station 1
32 | OMF09_RTU | DSFS:OMF04 | DSFS_Room | SFST | SFST_12 | 19 | SanLevSta | SIL0 | MODBUS:3:Read:Holding Registers | 40027 | 0 | 1 |  |  | OMF04-SIL0 | DSFS | OMF09_RTU.dat | DEIV | 3 | 1 | 40027 | 0 | 1 | deiDSFSOMF04DSFS_RoomSFST_12SanLevSta | 4 |  |  | 0 | $ComStatus , , | #filling level max station 1
-END-

## A-Validation Data list
RTU_Protocol_Operation_Code | Memory_Block | RTU_Protocol | Operation Code List | Association with Memory Block | RTU_Undefined_Operation_Code | RTU_Undefined_Operation_Code | RTU_Modbus_Operation_Code | Modbus_Memory_Block | RTU_IEC104_Operation_Code | IEC104_Memory_Block | RTU_Data_Check_Function | RTU_Data_Translation_Function | Bit_Position
MODBUS:1:Read:Coils | MODBUS:MEMBLOCK01 | MODBUS-TCP | SE_RTU_Modbus_Operation_Code | SE_RTU_Modbus_Table |  |  | MODBUS:1:Read:Coils | MODBUS:MEMBLOCK01 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | cfRANGE | tfNOT | 0
MODBUS:2:Read:Discrete Inputs | MODBUS:MEMBLOCK02 | MODBUS-RTU | SE_RTU_Modbus_Operation_Code | SE_RTU_Modbus_Table |  |  | MODBUS:2:Read:Discrete Inputs | MODBUS:MEMBLOCK02 | IEC104:M_DP_NA_1 | IEC104:MEMBLOCK01 |  | tfLIN | 1
MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | IEC60870-5-104 | SE_RTU_IEC104_Operation_Code | SE_RTU_IEC104_Table |  |  | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 |  | BTL32 | 2
MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | IEC60870-5-101 | SE_RTU_IEC104_Operation_Code | SE_RTU_IEC104_Table |  |  | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | IEC104:M_ME_NB_1 | IEC104:MEMBLOCK01 |  | LTB16 | 3
MODBUS:5:Write:Coil | MODBUS:MEMBLOCK01 | DNP3.0 | SE_RTU_Undefined_Operation_Code | SE_RTU_Undefined_Table |  |  | MODBUS:5:Write:Coil | MODBUS:MEMBLOCK01 | IEC104:M_ME_NC_1 | IEC104:MEMBLOCK01 |  | USHORT | 4
MODBUS:6:Write:Holding Register | MODBUS:MEMBLOCK03 | BACNET-TCP | SE_RTU_Undefined_Operation_Code | SE_RTU_Undefined_Table |  |  | MODBUS:6:Write:Holding Register | MODBUS:MEMBLOCK03 | IEC104:M_IT_NA_1 | IEC104:MEMBLOCK01 |  |  | 5
MODBUS:15:Write:Coils | MODBUS:MEMBLOCK01 |  | SE_RTU_Undefined_Operation_Code | SE_RTU_Undefined_Table |  |  | MODBUS:15:Write:Coils | MODBUS:MEMBLOCK01 | IEC104:M_SP_TB_1 | IEC104:MEMBLOCK01 |  |  | 6
MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [5 empty] | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | IEC104:M_DP_TB_1 | IEC104:MEMBLOCK01 |  |  | 7
IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SC_NA_1 | IEC104:MEMBLOCK01 |  |  | 8
IEC104:M_DP_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 |  |  | 9
IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_RC_NA_1 | IEC104:MEMBLOCK01 |  |  | 10
IEC104:M_ME_NB_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SE_NA_1 | IEC104:MEMBLOCK01 |  |  | 11
IEC104:M_ME_NC_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SE_NB_1 | IEC104:MEMBLOCK01 |  |  | 12
IEC104:M_IT_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SE_NC_1 | IEC104:MEMBLOCK01 |  |  | 13
IEC104:M_SP_TB_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_IC_NA_1 | IEC104:MEMBLOCK01 |  |  | 14
IEC104:M_DP_TB_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_CI_NA_1 | IEC104:MEMBLOCK01 |  |  | 15
IEC104:C_SC_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_RD_NA_1 | IEC104:MEMBLOCK01 |  |  | 16
IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 17
IEC104:C_RC_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 18
IEC104:C_SE_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 19
IEC104:C_SE_NB_1 | IEC104:MEMBLOCK01 | [11 empty] | 20
IEC104:C_SE_NC_1 | IEC104:MEMBLOCK01 | [11 empty] | 21
IEC104:C_IC_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 22
IEC104:C_CI_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 23
IEC104:C_RD_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 24
25
|  | Check of Validation Lists | [10 empty] | 26
|  | PLC Protocol | Available Operation Code | [9 empty] | 27
|  | IEC60870-5-104 | IEC104:M_ME_NA_1 | [9 empty] | 28
|  | MODBUS-RTU | MODBUS:4:Read:Input Registers | [9 empty] | 29
30
31
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
Note on E1: BERNARD Olivier: This column identifies the list to the associated operation codes. This list is defined through a name (Excel Formula name)

## B-Address Qty
FC / Class Name | UFWL | FSY | SWCA | PLC | SILO | PNCO | SFST
MODBUS:1:Read:Coils | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000
MODBUS:2:Read:Discrete Inputs | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000
MODBUS:3:Read:Holding Registers | 10;10000 | 10;10000 | 10;10000 | 10;10000 | 10;10000 | 10;10000 | 10;10000
MODBUS:4:Read:Input Registers | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000
MODBUS:5:Write:Coil | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000
MODBUS:6:Write:Holding Register | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000
MODBUS:15:Write:Coils | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000
MODBUS:16:Write:Holding Registers | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000
IEC104:M_SP_NA_1 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000
IEC104:M_DP_NA_1 | 40;4000 | 40;4000 | 40;4000 | 40;4000 | 40;4000 | 40;4000 | 40;4000
IEC104:M_ME_NA_1 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000
IEC104:M_ME_NB_1 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000
IEC104:M_ME_NC_1 | 40;13000 | 40;13000 | 40;13000 | 40;13000 | 40;13000 | 40;13000 | 40;13000
IEC104:M_IT_NA_1 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000
IEC104:M_SP_TB_1 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000
IEC104:M_DP_TB_1 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000
IEC104:C_SC_NA_1 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000
IEC104:C_DC_NA_1 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000
IEC104:C_RC_NA_1 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000
IEC104:C_SE_NA_1 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000
IEC104:C_SE_NB_1 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000
IEC104:C_SE_NC_1 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000
IEC104:C_IC_NA_1 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000
IEC104:C_CI_NA_1
IEC104:C_RD_NA_1