## Revision
Revision
Date | Version | Author | Observations
12-Feb-2015 | A2 | F. BLAISE | Creation | CHANGE TO :
30-Mar-2016 | A3-A5 | C. CAMARA | Update IO class based on typical ios for BPS single busbar including SIL 2
06-Apr-2017 | A6 | T.MARTINEZ | Update according to new Template.
06-Jul-2017 | A7 | T.MARTINEZ | Update according to template v0.35 update RTU name. in instance list Added in instance list PM instances Added in class list PM class Changed SIl2M to SIL2C for DI2 channel Replaced Alarm seveirty of Thales by Alarm severity of Alstom (tagged A7) Changed naming of SIL2 functionnality (confirmed -> Execute Ack) DO duration updated and typo duration for DI deleted DO "associated return status" column updated according to the DI linked
10-Aug-2017 | A7 | H.SALIHEDDINE | IO class Update: - BB_OST instead of 66KV_BB_OST and 33KV_BB_OST - VM instead ofVT - BIS and ES instead of IES - BB_Bay instaed of 66KV_BB_BS_Bay and 33KV_BB_BS_Bay - CMN_Bay instead of66KV_BB_Bay and 33KV_BB_Bay - Feeder_Bay_CL instead of 33KV_BB_Feeder_Bay and 66KV_BB_Feeder_Bay the new class name were reported in instance List Update of point type and interface to for : LVAC_FEED, LVAC_INC, BS_Bay, CB_Prot, CMN_Bay , Feeder_Bay_CL
18/9/2017 | A8 | HK Team | Class List: - Change DO of class CB from SIL0 to SIL2 - Update data type, operation code, DI/DO value table for class CB, BIS, SF6CB - Update operation code for class ES, CB_OST - Fix class name VT - Mergerd with LRT-QSTT-XX-ICD-SCC-GEN00-371055-A7-ICD SCADA -BPS-CL_Appendix_C_ATT1 updated04Sept2017 - Add VTIS class - Watchdog coded over 16 bits - Add GTW class for Gateway Instance List: - Remove duplicate instance for class Feeder_Bay_CL - Change location from "PWR:BPC-CL" to "PWR:BPS:CL" - Remove space bar in sublocation for class CMN_Bay - Included update of LRT-QSTT-XX-ICD-SCC-BPS01-371055-A7-ICD SCADA -BPS-CL_Appendix_C_ATT1 updated04Sept2017 - RTU name: "BLC04_RTU" replaced with "BPS01_RTU" - Rename equipment with shorter names - Fill the PLC name column - Add watchdog - Add VT Isolator B1064 and B2064 - E18/28CNTxx replaced by E18/28NCTxx - B120 renamed in B210 - Add Gateway
2017-10-19 | A8 | F. BLAISE | Column Description in Instance List updated Addition of two classes for measurement value: - BMV for Feeder Bay and Bus section Bay - BBMV for Busbar Classes not used any more: - CT - PM - VT Correction of some equipment with wrong classes: - B101, B201, B10M1, B10M2, B111, B211, B1241, B1246 (ES instead of BIS)
2017-12-20 | A9 | F. BLAISE | Classs List - acknowledgement for SIL2 command : DI2 instead of DI, add initial & final conditions - Circuit breaker status and Earth swith status: DI2 instead of DI - min/max measurement value update (xxMV classes) - BBMV, CB_OST, CD_PROT,CT, PM classes removed - ES replaced by ESST, ESSM added for monitoring only - VT replaced by 33KVVM et 66KVVM (for Voltage Measurement) No control of 66kV: - new classes: SF6CBM, BISM. Update initial and final conditions for DO2 Update to template v0.37
2018-02-26 | A9.1 | M. TENA | Class List - Bay Control Authority Class added. - AVR Control Class added. Instance List - Bay Control Authority Instances added (33kV). - AVR Control Instances added for E18 & E28.
2018-03-09 | B | F. BLAISE | Classs List - Feeder_Bay_CL replaced by new classes: 66kVIFBA, 33KVIFBA, 66KVBSBA, 33KVBSBA, 66KVHVBA, 33KVSTBA, 33KVOFBA - Merged class: LVAC_MDB, LVAC_FEED & LVAC_INC -> LVAC - Removed classes: SF6CB, SF6CBM, CD_PROT, CT, PM, BS_Bay - CBOF replaced by new classes 66KVIFPR, 33KVIFPR, 66KVBSPR, 33KVBSPR, 66KVHVPR, 33KVSTPR, 33KVOFPR - BB_OST replaced by BBAL - XF_AUX replaced by AUXTF and POWTF - new classes: BSCP, BBPR Class name changed: - BIS -> ISST, BISM- > BIST - ES -> ESST, ESSM added for monitoring only - VT -> VM - AVR Removed. 3 DO 2 added to POWTF - SIL Double Command Update Instance List - add instances of CB_OST (for monitoring only) - add instances of VM Migration to template v0.37 Update following RAMS manager review - CB & ISST: Open command is SIL 2 - VTIS: Isolator position is SIL 2 - ESST status is SIL 0
2018-06-04 | B.1 | Jason | 1-Class List -Update duplicated CSS Point Name within same class (ESST, 66KVBATC) 3-Class Mapping Update Class Mapping 4-External Variables Update external variables
|  | E.TAI | Update marco to V2.2
|  | E.TAI | According the confirmation from Olivier's email on 10 April, items are updated as follow: 1-Class List - Operation code (column N) from IEC104:M_SP_NA_1 to IEC104:M_DP_NA_1 for class CB_OST and ESSM - Data Length (column BH) from 1 to 2 for class POWTF
|  | Jason | Class List: Update Column "Code" Instance List: Remove "," in column - Description for row 227,228,242,243 and 244
Partners view

## Introduction
Introduction
For all ICD relative to equipment monitoring & control , this ECI (Equipment Classes & Instances) file template must be used as appendix to define: - the equipment classes, from an I/O point of view - all instances relative to each class
Recommandations
1 | Use one ECI file for each ICD document (one ICD=one subsystem)
2 | Do not change the organisation of the ECI file:
- Sheet "Equipment classes" : define all classes for the relative subsystem (see meaning of each field in the "Definitions" sheet)
- Sheet "Equipment instances" : define all instances for the relative subsystem (see meaning of each field in the "Definitions" sheet)
3 | For each sheet, do not change the organisation of the sheet (does not remove any column) in order to be able to use the standard export/import tools
4 | Create the necessary number of classes: for example, if similar equipment have different numbers of DI, DO, AI, create one class for each case
5 | Define, if possible, contiguous addresses for equipments/points within the same class.
Use the internal macro (### to be implemented in next release ###) to check the consistency of all data included in the sheet "Equipment classes" and "Equipment instances"
Notes
Issues to be addressed in future release
## Use appropriate point & bit value descriptions to create alarm label (DI) #####
### define rules for separators

## Definitions
Subsystem TVS - Equipment classes & instances
Definitions
1-Class List
Column Class | Column Name | Column Description | Values
| Revision | Identifiy the IO revision in witch the information was added , deleted or modified | version (string)
| isAComment | Specify whether the line is a comment or not | Y or N
EQUIPMENT CLASSES
| System | Define the trigram of the system's name in which the equipment is included | XXX
| Sub-system | Define the trigram of the sub-system's name in which the equipment is included | XXX
| Class name | Short equipment name on XXX characters number (minimum 3 characters - maximum 12 characters)
| CSS Point Name | Normalized name, used within the SCADA
EXTERNAL SYSTEM DATA
| Point Name | Name of equipment point from supplier
| Point Description | Any useful documentation on the point
| Point Type | Point can be qualified as Event or Alarm. Hence, supported values are | Operational event
Operational alarm
Technical alarm
Meter
Command
| Interface To | Identifies the target subsystem which can be: | daily
weekly
| Data Type | Digital Input | DI | 1 | bit
|  |  | DI2 | 2 | bits
|  | Digital Output | DO | 1 | bits
|  |  | DO2 | 2 | bits
|  | Analog Input | AI | 16 | bits
|  |  | AI2 | 32 | bits
|  | Analog Output | AO | 16 | bits
|  |  | AO2 | 32 | bits
EXTERNAL SYSTEM DATA DETAILS
| SIL Level | Identify the SIL level for the equipment point which can be | SIL0
SIL2_Monitoring
SIL2_Control
| Protocol | Applicable protocol: may be Modbus or IEC104
| Operation code | Operation code needed to manage the point at protocol level
| Memory Block | TODO
DI POINT
| DI/DI2 Value = 0 | For a DI or DI2, definition of the supervised status when the value is set to 0
| DI/DI2 Value = 1 | For a DI or DI2, definition of the supervised status when the value is set to 1
| DI2 Value = 2 | For a DI2, definition of the supervised status when the value is set to 2
| DI2 Value = 3 | For a DI2, definition of the supervised status when the value is set to 3
| Default value | Default value of the equipment point
| Alarm severity | Define the alarm severity for each value with the format (value1: severity label 1, value2: severity label 2, etc) Severity labels are: - None for events - Min for Minor alarms - Maj for Major alarms - Crit for Critical alarms Example: - 0: None, 1: Maj - 0: None, 1: None
| Alarm label | This label will be presented to the operators on the HMI for english language. It consists of: CCS Point Name: DI value when=0 / DI value when=1 / …
DO POINT
| DO/DO2 Value = 0 | For a DO or DO2, definition of the supervised status when the value is set to 0
| DO/DO2 Value = 1 | For a DO or DO2, definition of the supervised status when the value is set to 1
| DO2 Value = 2 | For a DO2, definition of the supervised status when the value is set to 2
| DO2 Value = 3 | For a DO2, definition of the supervised status when the value is set to 3
| Default value | Define the default value of the equipment point
| Output duration (ms) | Give the properties of the output signal command in ms: <empty>: continuous signal integer value: temporal duration of the pulse (in ms)
| Timeout for reaction (s) | Expected response time between the command sending and the modification of the associated status
| Initial condition | Pre-condition to be checked before sending the command
| Final condition | Post-condition to be checked to make sure the command is successful
| Associated return status | Return equipment status associated with the command
AI POINT
| Unit | Give the measurement unity of the analog data
| Min value | Define the minimum value of the data
| Max value | Define the maximum value of the data
| Limit 1 (optional) | Threshold in order to add range of the supervised value between min and max values
| Limit 2 (optional) | Threshold in order to add range of the supervised value between min and max values
In the template, alarm thresholds are defined through two value limits plus a minimum value and a maximum value. As shown in the figure on the right, this defines 5 ranges for which an alarm may be defined
| Range <i> alarm severity | Define the alarm severity for a range Severity labels are: - None for events - Min for Minor alarms - Maj for Major alarms - Crit for Critical alarms
| Range <i> alarm label | Define the alarm label for a range
| Dead band | Define the tolerance of variation around a threshold
| Default value | Define the default value of the equipment point
| Alarm label | This label will be presented to the operators on the HMI. It consists on: Equipment description (displayed in HMI): under Min value / under Max value / etc.
AO POINT
| Unit | Give the measurement unity of the analog data
| Range Min value | Define the minimum range of the command value
| Range Max value | Define the maximum range of the command value
| Output duration (ms) | Give the properties of the output signal command in ms: Nothing to fill: continuous signal XXX: temporal duration of the pulse
| Timeout for reaction (s) | Response time between the command and the associated status modification on the equipment
| Initial condition | Conditions to verify before sending the command
| Final condition | Conditions to verify after the sending of the command
| Associated return status | Return equipment status associated with the command
2-Instance List
Column Class | Column Name | Column Description
| Revision | Identifiy the IO revision in witch the information was added , deleted or modified
| isAComment | Specify whether the line is a comment or not
| GBS Code | TBC
| LBS Code (LRT) | TBC
| LBS Code (QRC) | TBC
| Description | Textual description or precision about the Location/sublocation of the equipment instance
| Location | Define in a short designation the geographical location in which the equipment is based
| Sublocation | Define in a short designation the sublocation (Subsystem / Level / Building / room) in which the equipment is based
| Class name | Class name identical to the class name defined in the "1-Class List" tab
| Equipment name | Give the instance name of the equipment.
| RTU Name | Name of the concentrator (as viewed in the SCADA subsystem) for the equipment
| PLC Name | Name of the partner PLC
| InvalidVar1 | name of the first external variable used to invalidate this equipement (usually comStatus of the gateway or PRTU)
| InvalidVar2 | name of the second external variable used to invalidate this equipement (usually comStatus of the gateway or PRTU)
| InvalidVar3 | name of the third external variable used to invalidate this equipement (usually comStatus of the gateway or PRTU)
| Remark | For variables used as Invalidation Variables, the value 0 needs to correspond to the invalidation state
i.e. Communication Status must be equal to 0 when communication is lost to invalidate associated points
| Avalanche Condition | Syntax is <external variable name> = <value> - external variable that is used to identify avalanche condition - value considered for the avalanche condition
| Example: | deiPWRTPSTPS16_PowerStatus = 0

## Generation
Execute |  | To do before Generation => Check that there are no ROW filters set in the Class and instance worksheets
Tool version | v2.2
Generation Time: | 4/11/2018 at 11:34:13 AM
Found Classes: | 44
Found Errors: | 0
Found Warnings: | 0
Not Found Classes: | 0
Generate Points
Fill Code & Index Address

## 1-Class List
|  | EQUIPMENT CLASSES |  |  |  | EXTERNAL SYSTEM DATA |  |  |  |  | EXTERNAL SYSTEM DATA DETAILS |  |  |  | DI or DI2 | [6 empty] | DO | [8 empty] | AI | [17 empty] | AO | [8 empty] | MMS | SE Engineering |  |  |  | SW Engineering | HMI details (dictionnaries)
Revision | isAComment | System | Sub-system | Class name | CSS Point Name | Point Name | Point Description | Point Type | Frequency | Data Type | SIL Level | Protocol | Operation code (FC, ASDU, ...) | Memory Block | DI or DI2 value = 0 (00) | DI or DI2 value = 1(01) | DI2 value = 2 (10) | DI2 value = 3 (11) | Default value | Alarm severity | Alarm label | DO or DO2 value = 0 (00) | DO or DO2 value = 1(01) | DO2 value = 2 (10) | DO2 value = 3 (11) | Output duration (ms) | Timeout for reaction (s) | Initial condition | Final condition | Associated return status | Unit | Min value | Max value | Limit 1 (optional) | Limit 2 (optional) | Range 1 alarm severity ] -∞,min value] | Range 1 alarm label ] -∞,min value] | Range 2 alarm severity ]min value,limit1] | Range 2 alarm label ]min value,limit1] | Range 3 alarm severity ]limit1,limit2] | Range 3 alarm label ]limit1,limit2] | Range 4 alarm severity ]limit2,max value] | Range 4 alarm label ]limit2,max value] | Range 5 alarm severity ]max value,+∞[ | Range 5 alarm label ]max value,+∞[ | Dead band | Default value | Formula | Unit | Range Min value | Range Max value | Output duration (ms) | Timeout for reaction (s) | Initial condition | Final condition | Associated return status | Formula | [Lusail] PBS code | Data Length | Index Address | Bit position | IsAnimated | Code | System (Native language) | Sub-system (Native language) | Class name (Native language) | Equipment description (displayed in HMI) (Native language) | Description (Details of description) (Native language)
B | Y |  |  |  |  | Main 66Kv Busbar Operational Status, Main 33Kv Busbar Operational Status
B | N | PWR | BPS-CL | BBPZ | Busbar Protection M1 Zone Trip | Busbar Protection M1 Zone Trip | [BM1O] Busbar Protection M1 Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Crit | [BM1O] Busbar Protection M1 Trip : Clear/Trip | [37 empty] | 1 | 0 |  | NO | Trip1
B | N | PWR | BPS-CL | BBPZ | Busbar Protection M2 Zone Trip | Busbar Protection M2 Zone Trip | [BM2O] Busbar Protection M2 Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Crit | [BM2O] Busbar Protection M2 Trip : Clear/Trip | [37 empty] | 1 | 1 |  | NO | Trip2
B | N | PWR | BPS-CL | BBPZ | Busbar Protection Operated | Busbar Protection Operated | [CBFO] Busbar Protection Operated | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Crit | [CBFO] Busbar Protection Operated : Clear/Trip | [37 empty] | 1 | 2 |  | NO | Operated
B | Y |  |  |  |  | 66KV Bus Bar Alarms, 33KV Bus Bar Alarms
B | N | PWR | BPS-CL | BBAL | Busbar Protection Out of Service | Busbar Protection Out of Service | [BPOS] : Busbar Protection Out of Service | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Min | [BPOS] : Busbar Protection Out of Service : Clear/Appear | [37 empty] | 1 | 0 |  | YES | OutofServ
B | N | PWR | BPS-CL | BBAL | Busbar Protection Disturbed | Busbar Protection Disturbed | [BPU1] : Busbar Protection Disturbed | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Min | [BPU1] : Busbar Protection Disturbed : Clear/Appear | [37 empty] | 1 | 1 |  | YES | Disturbed
B | N | PWR | BPS-CL | BBAL | All Protection Blocked | All Protection Blocked | [BBPB] : All Protection Blocked | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [BBPB] : All Protection Blocked : Clear/Appear | [37 empty] | 1 | 2 |  | YES | Blocked
B | N | PWR | BPS-CL | BBAL | CB Failure Stage 2 M1 Zone | CB Failure Stage 2 M1 Zone | [CBFO] : CB Failure Stage 2 M1 Zone | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [CBFO] : CB Failure Stage 2 M1 Zone : Clear/Appear | [37 empty] | 1 | 3 |  | YES | Zone1
B | N | PWR | BPS-CL | BBAL | CB Failure Stage 2 M2 Zone | CB Failure Stage 2 M2 Zone | [CBFO] : CB Failure Stage 2 M2 Zone | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [CBFO] : CB Failure Stage 2 M2 Zone : Clear/Appear | [37 empty] | 1 | 4 |  | YES | Zone2
B | N | PWR | BPS-CL | BBAL | Breaker Failure Operated | Breaker Failure Operated | [CBFO] : Breaker Failure Operated | Operational Alarm |  | DI | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Crit | [CBFO] : Breaker Failure Operated : Clear/Trip | [37 empty] | 1 | 5 |  | YES | Operated
B | N | PWR | BPS-CL | BBAL | Busbar Protection M1 Zone Trip | Busbar Protection M1 Zone Trip | [BPU1] Busbar Protection M1 Zone | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | OUT | IN |  |  | OUT | 0: None, 1: Crit | [BPU1] Busbar Protection M1 Zone : OUT/IN | [37 empty] | 1 | 6 |  | YES | ZoneTrp1
B | N | PWR | BPS-CL | BBAL | Busbar Protection M2 Zone Trip | Busbar Protection M2 Zone Trip | [BPU1] Busbar Protection M2 Zone | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | OUT | IN |  |  | OUT | 0: None, 1: Crit | [BPU1] Busbar Protection M2 Zone : OUT/IN | [37 empty] | 1 | 7 |  | YES | ZoneTrp2
B | N | PWR | BPS-CL | BBAL | Busbar Protection Blocked M1 Zone | Busbar Protection Blocked M1 Zone | [BPU1] Busbar Protection Blocked M1 Zone | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [BPU1] Busbar Protection Blocked M1 Zone : Clear/Appear | [37 empty] | 1 | 8 |  | YES | BlockedZone1
B | N | PWR | BPS-CL | BBAL | Busbar Protection Blocked M2 Zone | Busbar Protection Blocked M2 Zone | [BPU1] Busbar Protection Blocked M2 Zone | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [BPU1] Busbar Protection Blocked M2 Zone : Clear/Appear | [37 empty] | 1 | 9 |  | YES | BlcokedZone2
B | Y |  |  |  |  | 66KV Bus Bar Protection, 33KV Bus Bar Protection
B | N | PWR | BPS-CL | BBPR | Breaker Failure Stage-1 Operated | Breaker Failure Stage-1 Operated | [CBFO] : Breaker Failure Stage-1 Operated | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Min | [CBFO] : Breaker Failure Stage-1 Operated : Clear/Appear | [37 empty] | 1 | 0 |  | YES | Stg1
B | N | PWR | BPS-CL | BBPR | Breaker Failure Stage-2 Operated | Breaker Failure Stage-2 Operated | [CBFO] : Breaker Failure Stage-2 Operated | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Min | [CBFO] : Breaker Failure Stage-2 Operated : Clear/Appear | [37 empty] | 1 | 1 |  | YES | Stg2
B | Y |  |  |  |  | Bus Isolator
B | N | PWR | BPS-CL | ISST | Bus Isolator Status | Bus Isolator Status | [ISST] : Bus Isolator Status | Technical alarm |  | DI2 | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_DP_NA_1 | IEC104:MEMBLOCK01 | NA | OPEN | CLOSE | NA | OPEN | 0: Maj, 1: None, 2: None, 3: Maj | [ISST] : Bus Isolator Status : NA/OPEN/CLOSE/NA | [37 empty] | 2 | 0 |  | YES | IsoSts
B | N | PWR | BPS-CL | ISST | Bus Isolator Open Order Select | Bus Isolator Control Open | [ISST] : Bus Isolator Control Open | Command |  | DO2 | SIL2_Control | IEC60870-5-104 | IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | NA | SELECT OPEN | NA | NA | NA | 5 | Bus Isolator Status = CLOSE |  | Bus Isolator Open Order Select Ack = ACKNOWLEDGE | [28 empty] | 2 | 0 |  | NO | CmdSelOpen
B | N | PWR | BPS-CL | ISST | Bus Isolator Open Order Select Ack | Bus Isolator Open Order Selection Ack | [ISST] : Bus Isolator Control Select Open Ack | Operational event |  | DI2 | SIL2_Control | IEC60870-5-104 | IEC104:C_DC_NA_RESULT_1 | IEC104:MEMBLOCK01 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: Event, 1: Event, 2: Crit, 3: Crit | [ISST] : Bus Isolator Control Select Open Ack : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 0 | 4 | NO | AckSelOpen
B | N | PWR | BPS-CL | ISST | Bus Isolator Open Order Execute | Bus Isolator Control Select Open | [ISST] : Bus Isolator Control Select Open | Command |  | DO2 | SIL2_Control | IEC60870-5-104 | IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | NA | EXECUTE OPEN | NA | NA | NA | 5 | Bus Isolator Status = CLOSE | Bus Isolator Status = OPEN | Bus Isolator Open Order Execute Ack = ACKNOWLEDGE | [28 empty] | 2 | 0 |  | NO | CmdExeOpen
B | N | PWR | BPS-CL | ISST | Bus Isolator Open Order Execute Ack | Bus Isolator Open Order Execute Ack | [ISST] : Bus Isolator Control Execute Open Ack | Operational event |  | DI2 | SIL2_Control | IEC60870-5-104 | IEC104:C_DC_NA_RESULT_1 | IEC104:MEMBLOCK01 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: Event, 1: Event, 2: Crit, 3: Crit | [ISST] : Bus Isolator Control Execute Open Ack : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 0 | 2 | NO | AckExeOpen
B | N | PWR | BPS-CL | ISST | Bus Isolator Close Order Select | Bus Isolator Control Close | [ISST] : Bus Isolator Control Close | Command |  | DO2 | SIL2_Control | IEC60870-5-104 | IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | NA | NA | SELECT CLOSE | NA | NA | 5 | Bus Isolator Status = OPEN |  | Bus Isolator Close Order Select Ack = ACKNOWLEDGE | [28 empty] | 2 | 0 |  | NO | CmdSelClose
B | N | PWR | BPS-CL | ISST | Bus Isolator Close Order Select Ack | Bus Isolator Close Order Selection Ack | [ISST] : Bus Isolator Control Select Close Ack | Operational event |  | DI2 | SIL2_Control | IEC60870-5-104 | IEC104:C_DC_NA_RESULT_1 | IEC104:MEMBLOCK01 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: Event, 1: Event, 2: Crit, 3: Crit | [ISST] : Bus Isolator Control Select Close Ack : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 0 | 4 | NO | AckSelClose
B | N | PWR | BPS-CL | ISST | Bus Isolator Close Order Execute | Bus Isolator Control Select Close | [ISST] : Bus Isolator Control Select Close | Command |  | DO2 | SIL2_Control | IEC60870-5-104 | IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | NA | NA | EXECUTE CLOSE | NA | NA | 5 | Bus Isolator Status = OPEN | Bus Isolator Status = CLOSE | Bus Isolator Close Order Execute Ack = ACKNOWLEDGE | [28 empty] | 2 | 0 |  | NO | CmdExeClose
B | N | PWR | BPS-CL | ISST | Bus Isolator Close Order Execute Ack | Bus Isolator Close Order Execute Ack | [ISST] : Bus Isolator Control Execute Close Ack | Operational event |  | DI2 | SIL2_Control | IEC60870-5-104 | IEC104:C_DC_NA_RESULT_1 | IEC104:MEMBLOCK01 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: Event, 1: Event, 2: Crit, 3: Crit | [ISST] : Bus Isolator Control Execute Close Ack : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 0 | 2 | NO | AckExeClose
B | Y |  |  |  |  | Bus Isolator (for 66kV monitoring only)
B | N | PWR | BPS-CL | BIST | Bus Isolator Status | Bus Isolator Status | [ISST] : Bus Isolator Status | Technical alarm |  | DI2 | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_DP_NA_1 | IEC104:MEMBLOCK01 | NA | OPEN | CLOSE | NA | OPEN | 0: Maj, 1: None, 2: None, 3: Maj | [ISST] : Bus Isolator Status : NA/OPEN/CLOSE/NA | [37 empty] | 2 | 0 |  | YES | IsoSts
A6 | Y |  |  |  |  | Q0 Circuit Breaker
A9 | N | PWR | BPS-CL | CB | Circuit Breaker Status | Circuit Breaker Status | [CBST] : Circuit Breaker Status | Technical alarm |  | DI2 | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_DP_NA_1 | IEC104:MEMBLOCK01 | NA | OPEN | CLOSE | NA | CLOSE | 0: Maj, 1: None, 2: None, 3: Maj | [CBST] : Circuit Breaker Status : NA/OPEN/CLOSE/NA | [37 empty] | 2 | 0 |  | YES | CirBrkStatus
B | N | PWR | BPS-CL | CB | Circuit Breaker Open Order Select | Circuit Breaker Control Open | [CBST] : Circuit Breaker Control Open | Command |  | DO2 | SIL2_Control | IEC60870-5-104 | IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | NA | SELECT OPEN | NA | NA | NA | 5 | Circuit Breaker Status = CLOSE |  | Circuit Breaker Open Order Select Ack = ACKNOWLEDGE | [28 empty] | 2 | 0 |  | NO | CmdSelOpen
B | N | PWR | BPS-CL | CB | Circuit Breaker Open Order Select Ack | Circuit Breaker Open Order Selection Ack | [CBST] : Circuit Breaker Control Select Open Ack | Operational event |  | DI2 | SIL2_Control | IEC60870-5-104 | IEC104:C_DC_NA_RESULT_1 | IEC104:MEMBLOCK01 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: Event, 1: Event, 2: Crit, 3: Crit | [CBST] : Circuit Breaker Control Select Open Ack : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 0 | 4 | NO | AckSelOpen
B | N | PWR | BPS-CL | CB | Circuit Breaker Open Order Execute | Circuit Breaker Control Select Open | [CBST] : Circuit Breaker Control Select Open | Command |  | DO2 | SIL2_Control | IEC60870-5-104 | IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | NA | EXECUTE OPEN | NA | NA | NA | 5 | Circuit Breaker Status = CLOSE | Circuit Breaker Status = OPEN | Circuit Breaker Open Order Execute Ack = ACKNOWLEDGE | [28 empty] | 2 | 0 |  | NO | CmdExeOpen
B | N | PWR | BPS-CL | CB | Circuit Breaker Open Order Execute Ack | Circuit Breaker Open Order Execute Ack | [CBST] : Circuit Breaker Control Execute Open Ack | Operational event |  | DI2 | SIL2_Control | IEC60870-5-104 | IEC104:C_DC_NA_RESULT_1 | IEC104:MEMBLOCK01 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: Event, 1: Event, 2: Crit, 3: Crit | [CBST] : Circuit Breaker Control Execute Open Ack : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 0 | 2 | NO | AckExeOpen
B | N | PWR | BPS-CL | CB | Circuit Breaker Close Order Select | Circuit Breaker Control Close | [CBST] : Circuit Breaker Control Close | Command |  | DO2 | SIL2_Control | IEC60870-5-104 | IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | NA | NA | SELECT CLOSE | NA | NA | 5 | Circuit Breaker Status = OPEN |  | Circuit Breaker Close Order Select Ack = ACKNOWLEDGE | [28 empty] | 2 | 0 |  | NO | CmdSelClose
B | N | PWR | BPS-CL | CB | Circuit Breaker Close Order Select Ack | Circuit Breaker Close Order Selection Ack | [CBST] : Circuit Breaker Control Select Close Ack | Operational event |  | DI2 | SIL2_Control | IEC60870-5-104 | IEC104:C_DC_NA_RESULT_1 | IEC104:MEMBLOCK01 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: Event, 1: Event, 2: Crit, 3: Crit | [CBST] : Circuit Breaker Control Select Close Ack : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 0 | 4 | NO | AckSelClose
B | N | PWR | BPS-CL | CB | Circuit Breaker Close Order Execute | Circuit Breaker Control Select Close | [CBST] : Circuit Breaker Control Select Close | Command |  | DO2 | SIL2_Control | IEC60870-5-104 | IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | NA | NA | EXECUTE CLOSE | NA | NA | 5 | Circuit Breaker Status = OPEN | Circuit Breaker Status = CLOSE | Circuit Breaker Close Order Execute Ack = ACKNOWLEDGE | [28 empty] | 2 | 0 |  | NO | CmdExeClose
B | N | PWR | BPS-CL | CB | Circuit Breaker Close Order Execute Ack | Circuit Breaker Close Order Execute Ack | [CBST] : Circuit Breaker Control Execute Close Ack | Operational event |  | DI2 | SIL2_Control | IEC60870-5-104 | IEC104:C_DC_NA_RESULT_1 | IEC104:MEMBLOCK01 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: Event, 1: Event, 2: Crit, 3: Crit | [CBST] : Circuit Breaker Control Execute Close Ack : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 0 | 2 | NO | AckExeClose
A6 | Y |  |  |  |  | Q0 Circuit Breaker Status / for Monitoring Only
A9 | N | PWR | BPS-CL | CB_OST | Circuit Breaker Status | Circuit Breaker Status | [CBST] : Circuit Breaker Status | Technical alarm |  | DI2 | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_DP_NA_1 | IEC104:MEMBLOCK01 | NA | OPEN | CLOSE | NA | CLOSE | 0: Maj, 1: None, 2: None, 3: Maj | [CBST] : Circuit Breaker Status : NA/OPEN/CLOSE/NA | [37 empty] | 2 | 0 |  | YES | Status
B | Y |  |  |  |  | 66KV Bus Bar Protection - Bus section, 33KV Bus Bar Protection - Bus section
A9 | N | PWR | BPS-CL | BSCP | Breaker Failure Stage-1 Operated - M1 | Breaker Failure Stage-1 Operated - M1 | [CBFO] : Breaker Failure Stage-1 Operated - M1 | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Min | [CBFO] : Breaker Failure Stage-1 Operated - M1 : Clear/Appear | [37 empty] | 1 | 0 |  | YES | Stg1Oper1
B | N | PWR | BPS-CL | BSCP | Breaker Failure Stage-2 Operated - M1 | Breaker Failure Stage-2 Operated - M1 | [CBFO] : Breaker Failure Stage-2 Operated - M1 | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Min | [CBFO] : Breaker Failure Stage-2 Operated - M1 : Clear/Appear | [37 empty] | 1 | 1 |  | YES | Stg2Oper1
B | N | PWR | BPS-CL | BSCP | Breaker Failure Stage-1 Operated - M2 | Breaker Failure Stage-1 Operated - M2 | [CBFO] : Breaker Failure Stage-1 Operated - M2 | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Min | [CBFO] : Breaker Failure Stage-1 Operated - M2 : Clear/Appear | [37 empty] | 1 | 2 |  | YES | Stg1Oper2
B | N | PWR | BPS-CL | BSCP | Breaker Failure Stage-2 Operated - M2 | Breaker Failure Stage-2 Operated - M2 | [CBFO] : Breaker Failure Stage-2 Operated - M2 | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Min | [CBFO] : Breaker Failure Stage-2 Operated - M2 : Clear/Appear | [37 empty] | 1 | 3 |  | YES | Stg2Oper2
B | Y |  |  |  |  | 66kV Incoming Feeder Protection
B | N | PWR | BPS-CL | 66KVIFPR | T11 DC Supply Fail | T11 DC Supply Fail | [DCAB] : T11 DC Supply Fail | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [DCAB] : T11 DC Supply Fail : Clear/Appear | [37 empty] | 1 | 0 |  | YES | SupFail11
B | N | PWR | BPS-CL | 66KVIFPR | T21 DC Supply Fail | T21 DC Supply Fail | [DCAB] : T12 DC Supply Fail | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [DCAB] : T12 DC Supply Fail : Clear/Appear | [37 empty] | 1 | 1 |  | YES | SupFaill21
B | N | PWR | BPS-CL | 66KVIFPR | Diff Communication Fail Ch-1 | Diff Communication Fail Ch-1 | [CDFA] : Diff Communication Fail Ch-1 | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [CDFA] : Diff Communication Fail Ch-1 : Clear/Appear | [37 empty] | 1 | 2 |  | YES | FailCh1
B | N | PWR | BPS-CL | 66KVIFPR | Diff Communication Fail Ch-2 | Diff Communication Fail Ch-2 | [CDFA] : Diff Communication Fail Ch-2 | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [CDFA] : Diff Communication Fail Ch-2 : Clear/Appear | [37 empty] | 1 | 3 |  | YES | FailCh2
B | N | PWR | BPS-CL | 66KVIFPR | Main-1 Dist Protection Trip | Main-1 Dist Protection Trip | [nDIO] : Main-1 Dist Protection Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [nDIO] : Main-1 Dist Protection Trip : Clear/Trip | [37 empty] | 1 | 4 |  | YES | ProtTrip
B | N | PWR | BPS-CL | 66KVIFPR | Main-1 110% of Full Load Current | Main-1 110% of Full Load Current | [BEFL] : 110% of Full Load Current | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [BEFL] : 110% of Full Load Current : Clear/Appear | [37 empty] | 1 | 5 |  | YES | LoadCurr
B | N | PWR | BPS-CL | 66KVIFPR | Main-1 SOTF Trip | Main-1 SOTF Trip | [SOTF] : SOTF Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [SOTF] : SOTF Trip : Clear/Trip | [37 empty] | 1 | 6 |  | YES | SoftTrip
B | N | PWR | BPS-CL | 66KVIFPR | Main-1 Power Swing Block | Main-1 Power Swing Block | [nDIP] : Power Swing Block | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [nDIP] : Power Swing Block : Clear/Appear | [37 empty] | 1 | 7 |  | YES | Swing
B | N | PWR | BPS-CL | 66KVIFPR | Main-1 VT Fuse Failure / MCB Trip | Main-1 VT Fuse Failure / MCB Trip | [nVTF] : VT Fuse Failure / MCB Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [nVTF] : VT Fuse Failure / MCB Trip : Clear/Appear | [37 empty] | 1 | 8 |  | YES | McbTrip
B | N | PWR | BPS-CL | 66KVIFPR | Backup Overcurrent I>Trip | Backup Overcurrent I>Trip | [OCPO] : Backup Overcurrent I>Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [OCPO] : Backup Overcurrent I>Trip : Clear/Trip | [37 empty] | 1 | 9 |  | YES | OverCurrTrip
B | N | PWR | BPS-CL | 66KVIFPR | Intertrip Received Channel-1 | Intertrip Received Channel-1 | [INTR] : Intertrip Received Channel-1 | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [INTR] : Intertrip Received Channel-1 : Clear/Appear | [37 empty] | 1 | 10 |  | YES | ReceCh1
B | N | PWR | BPS-CL | 66KVIFPR | Intertrip Received Channel-2 | Intertrip Received Channel-2 | [INTR] : Intertrip Received Channel-2 | Operational alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [INTR] : Intertrip Received Channel-2 : Clear/Appear | [37 empty] | 1 | 11 |  | YES | ReceCh2
B | N | PWR | BPS-CL | 66KVIFPR | Intertrip Sent Channel-1 | Intertrip Sent Channel-1 | [INTS] : Intertrip Sent Channel-1 | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [INTS] : Intertrip Sent Channel-1 : Clear/Appear | [37 empty] | 1 | 12 |  | YES | SentCh1
B | N | PWR | BPS-CL | 66KVIFPR | Intertrip Sent Channel-2 | Intertrip Sent Channel-2 | [INTS] : Intertrip Sent Channel-2 | Operational alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [INTS] : Intertrip Sent Channel-2 : Clear/Appear | [37 empty] | 1 | 13 |  | YES | SentCh2
B | Y |  |  |  |  | 33kV Incoming Feeder Protection
B | N | PWR | BPS-CL | 33KVIFPR | Dir Overcurrent I>Trip | Dir Overcurrent I>Trip | [DOEP] : Dir Overcurrent I>Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [DOEP] : Dir Overcurrent I>Trip : Clear/Trip | [37 empty] | 1 | 0 |  | YES | DirTrip
B | N | PWR | BPS-CL | 33KVIFPR | 40MVA-T1 LV REF Trip | 40MVA-T1 LV REF Trip | [REPO] : 40MVA-T1 LV REF Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [REPO] : 40MVA-T1 LV REF Trip : Clear/Trip | [37 empty] | 1 | 1 |  | YES | RefTrip
B | N | PWR | BPS-CL | 33KVIFPR | Standby EF In>St-1 Trip | Standby EF In>St-1 Trip | [SBE1] : Standby EF In>St-1 Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [SBE1] : Standby EF In>St-1 Trip : Clear/Trip | [37 empty] | 1 | 2 |  | YES | EfTrip1
B | N | PWR | BPS-CL | 33KVIFPR | Standby EF In>St-2 Trip | Standby EF In>St-2 Trip | [SBE2] : Standby EF In>St-2 Trip | Operational alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [SBE2] : Standby EF In>St-2 Trip : Clear/Trip | [37 empty] | 1 | 3 |  | YES | EfTrip2
B | N | PWR | BPS-CL | 33KVIFPR | Standby EF In>Start | Standby EF In>Start | [SBES] : Standby EF In>Start | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [SBES] : Standby EF In>Start : Clear/Appear | [37 empty] | 1 | 4 |  | YES | Start
B | N | PWR | BPS-CL | 33KVIFPR | NER Faulty | NER Faulty | [NERF] : NER Faulty | Operational alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [NERF] : NER Faulty : Clear/Appear | [37 empty] | 1 | 5 |  | YES | Faulty
B | N | PWR | BPS-CL | 33KVIFPR | NER Ground Fault | NER Ground Fault | [NERG] : NER Ground Fault | Operational alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [NERG] : NER Ground Fault : Clear/Appear | [37 empty] | 1 | 6 |  | YES | GroundFault
B | N | PWR | BPS-CL | 33KVIFPR | NER Monitor Unhealthy | NER Monitor Unhealthy | [NERM] : NER Monitor Unhealthy | Operational alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [NERM] : NER Monitor Unhealthy : Clear/Appear | [37 empty] | 1 | 7 |  | YES | Unhealthy
B | Y |  |  |  |  | 66kV Bus Section Bay Protection
B | N | PWR | BPS-CL | 66KVBSPR | General Trip | General Trip | [OEPO] : General Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [OEPO] : General Trip : Clear/Trip | [37 empty] | 1 | 0 |  | YES | GenTrip
B | Y |  |  |  |  | 33kV Bus Section Bay Protection
B | N | PWR | BPS-CL | 33KVBSPR | Over Current Trip | Over Current Trip | [OEPO] : Over Current Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [OEPO] : Over Current Trip : Clear/Trip | [37 empty] | 1 | 0 |  | YES | OverCurTrip
B | Y |  |  |  |  | 66kV HV IBT Bay Protection
B | N | PWR | BPS-CL | 66KVHVPR | 40MVA-T1 Main-1 Diff Prot Trip | 40MVA-T1 Main-1 Diff Prot Trip | [TDPO] : 40MVA-T1 Main-1 Diff Prot Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [TDPO] : 40MVA-T1 Main-1 Diff Prot Trip : Clear/Trip | [37 empty] | 1 | 0 |  | YES | DiffTrip
B | N | PWR | BPS-CL | 66KVHVPR | 40MVA-T1 Diff Prot High Set St2 | 40MVA-T1 Diff Prot High Set St2 | [TDP1] : 40MVA-T1 Diff Prot High Set St2 | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [TDP1] : 40MVA-T1 Diff Prot High Set St2 : Clear/Trip | [37 empty] | 1 | 1 |  | YES | ProtHigh
B | N | PWR | BPS-CL | 66KVHVPR | General Trip | General Trip | [OEPO] : General Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [OEPO] : General Trip : Clear/Trip | [37 empty] | 1 | 2 |  | YES | GenTrip
B | Y |  |  |  |  | 33kV ST.TX Protection
B | N | PWR | BPS-CL | 33KVSTPR | General Trip | General Trip | [ETOO] : General Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [ETOO] : General Trip : Clear/Trip | [37 empty] | 1 | 0 |  | YES | GenTrip
B | N | PWR | BPS-CL | 33KVSTPR | 1000kVA AT-1 LV REF Trip | 1000kVA AT-1 LV REF Trip | [REPO] : 1000kVA AT-1 LV REF Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [REPO] : 1000kVA AT-1 LV REF Trip : Clear/Trip | [37 empty] | 1 | 1 |  | YES | RefTrip
B | Y |  |  |  |  | 33kV Outgoing Feeder Bay Protection
B | N | PWR | BPS-CL | 33KVOFPR | General Trip | General Trip | [ETOO] : General Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [ETOO] : General Trip : Clear/Trip | [37 empty] | 1 | 0 |  | YES | GenTrip
B | N | PWR | BPS-CL | 33KVOFPR | Differential Protection Trip | Differential Protection Trip | [CDPT] : Diff. Prot. Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [CDPT] : Diff. Prot. Trip : Clear/Trip | [37 empty] | 1 | 1 |  | YES | DiffProtTrip
B | N | PWR | BPS-CL | 33KVOFPR | Thermal Overload Alarm St-1 | Thermal Overload Alarm St-1 | [QAFA] : Thermal Overload Alarm St-1 | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [QAFA] : Thermal Overload Alarm St-1 : Clear/Appear | [37 empty] | 1 | 2 |  | YES | OverloadAlarm
B | N | PWR | BPS-CL | 33KVOFPR | Diff Communication Fail | Diff Communication Fail | [CDFA] : Diff Communication Fail | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [CDFA] : Diff Communication Fail : Clear/Appear | [37 empty] | 1 | 3 |  | YES | CommFail
B | N | PWR | BPS-CL | 33KVOFPR | VT Fuse Failure / MCB Trip | VT Fuse Failure / MCB Trip | [1VTF] : VT Fuse Failure / MCB Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [1VTF] : VT Fuse Failure / MCB Trip : Clear/Appear | [37 empty] | 1 | 4 |  | YES | FuseFail
B | N | PWR | BPS-CL | 33KVOFPR | Backup Overcurrent I>Trip | Backup Overcurrent I>Trip | [OCPO] : Backup Overcurrent I>Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [OCPO] : Backup Overcurrent I>Trip : Clear/Trip | [37 empty] | 1 | 5 |  | YES | OvercurrTrip
B | N | PWR | BPS-CL | 33KVOFPR | Intertrip Received | Intertrip Received | [INTR] : Intertrip Received | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [INTR] : Intertrip Received : Clear/Appear | [37 empty] | 1 | 6 |  | YES | Received
B | N | PWR | BPS-CL | 33KVOFPR | Intertrip Sent | Intertrip Sent | [INTS] : Intertrip Sent | Operational alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [INTS] : Intertrip Sent : Clear/Appear | [37 empty] | 1 | 7 |  | YES | Sent
B | Y |  |  |  |  | Earth Switch
B | N | PWR | BPS-CL | ESST | Earth Switch Status | Earth Switch Status | [ESST] : Earth Switch Status | Technical alarm |  | DI2 | SIL0 | IEC60870-5-104 | IEC104:M_DP_NA_1 | IEC104:MEMBLOCK01 | NA | OPEN | CLOSE | NA | OPEN | 0: Maj, 1: None, 2: None, 3: Maj | [ESST] : Earth Switch Status : NA/OPEN/CLOSE/NA | [37 empty] | 2 | 0 |  | YES | SwitchSts
B | N | PWR | BPS-CL | ESST | Earth Switch Control 1 | Earth Switch Control | [ESST] : Earth Switch Control Open | Command |  | DO2 | SIL0 | IEC60870-5-104 | IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 | [8 empty] | OPEN |  |  | NA | 5 | ES Status = Close | ES Status = Open | NA | [28 empty] | 2 | 0 |  | NO | CmdOpen
B | N | PWR | BPS-CL | ESST | Earth Switch Control 2 | Earth Switch Control | [ESST] : Earth Switch Control Close | Command |  | DO2 | SIL0 | IEC60870-5-104 | IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 | [9 empty] | CLOSE |  | NA | 5 | ES Status = Open | ES Status = Close | NA | [28 empty] | 2 | 0 |  | NO | CmdClose
B | Y |  |  |  |  | 66kV Earth Switch for monitoring only
B | N | PWR | BPS-CL | ESSM | Earth Switch Status | Earth Switch Status | [ESST] : Earth Switch Status | Technical alarm |  | DI2 | SIL0 | IEC60870-5-104 | IEC104:M_DP_NA_1 | IEC104:MEMBLOCK01 | NA | OPEN | CLOSE | NA | CLOSE | 0: Maj, 1: None, 2: None, 3: Maj | Earth Switch Status : NA/OPEN/CLOSE/NA | [37 empty] | 2 | 0 |  | YES | SwitchSts
B | Y |  |  |  |  | 66KV Incoming Feeder Bay Operational Status
B | N | PWR | BPS-CL | 66KVIFBA | AC Fail Relay Panel / LCC | AC Fail Relay Panel / LCC | [ACFL] : AC Fail Relay Panel / LCC | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Min | [ACFL] : AC Fail Relay Panel / LCC : Clear/Appear | [37 empty] | 1 | 0 |  | NO | AcPanel
B | N | PWR | BPS-CL | 66KVIFBA | DC Fail Relay Panel | DC Fail Relay Panel | [DCAB] : DC Fail Relay Panel | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [DCAB] : DC Fail Relay Panel : Clear/Appear | [37 empty] | 1 | 1 |  | NO | DcPanel
B | N | PWR | BPS-CL | 66KVIFBA | DC Fail LCC | DC Fail LCC | [DCFA] : DC Fail LCC | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [DCFA] : DC Fail LCC : Clear/Appear | [37 empty] | 1 | 2 |  | NO | LccPanel
B | N | PWR | BPS-CL | 66KVIFBA | Gas Pressure Stage 1 | Gas Pressure Stage 1 | [GAS1] : Gas Pressure Stage 1 | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [GAS1] : Gas Pressure Stage 1 : Clear/Appear | [37 empty] | 1 | 3 |  | NO | Stage1
B | N | PWR | BPS-CL | 66KVIFBA | Gas Pressure Stage 2 | Gas Pressure Stage 2 | [GAS2] : Gas Pressure Stage 2 | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [GAS2] : Gas Pressure Stage 2 : Clear/Appear | [37 empty] | 1 | 4 |  | NO | Stage2
B | N | PWR | BPS-CL | 66KVIFBA | MasterTrip relay operated | Master Trip relay operated | [MTRO] : Master Trip relay operated | Technical alarm |  | DI | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [MTRO] : Master Trip relay operated : Clear/Appear | [37 empty] | 1 | 5 |  | NO | Operated
B | N | PWR | BPS-CL | 66KVIFBA | IED WatchDog | IED WatchDog | [WDOG] : IED WatchDog | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG] : IED WatchDog : Clear/Appear | [37 empty] | 1 | 6 |  | NO | IedWtdg
B | N | PWR | BPS-CL | 66KVIFBA | BCU WatchDog | BCU WatchDog | [WDOG] : BCU Watchdog | Operational Alarm |  | DI | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG] : BCU Watchdog : Clear/Appear | [37 empty] | 1 | 7 |  | NO | BcuWtdg
B | N | PWR | BPS-CL | 66KVIFBA | Voltage Transformer Fuse Fail | Voltage Transformer Fuse Fail | [VTFA] : Voltage Transformer Fuse Fail | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [VTFA] : Voltage Transformer Fuse Fail : Clear/Appear | [37 empty] | 1 | 8 |  | NO | FuseFail
B | N | PWR | BPS-CL | 66KVIFBA | Thermal over load Alarm | Thermal over load Alarm | [QAFA] : Thermal over load Alarm | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [QAFA] : Thermal over load Alarm : Clear/Appear | [37 empty] | 1 | 9 |  | NO | OverloadAlarm
B | N | PWR | BPS-CL | 66KVIFBA | BCU Card Fail | BCU Card Fail | [WDOG] : BCU Card Fail | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG] : BCU Card Fail : Clear/Appear | [37 empty] | 1 | 10 |  | NO | CardFail
B | Y |  |  |  |  | 33KV Incomer Operational Status
B | N | PWR | BPS-CL | 33KVIFBA | AC Fail Relay Panel / LCC | AC Fail Relay Panel / LCC | [ACFL] : AC Fail Relay Panel / LCC | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Min | [ACFL] : AC Fail Relay Panel / LCC : Clear/Appear | [37 empty] | 1 | 0 |  | NO | AcPanel
B | N | PWR | BPS-CL | 33KVIFBA | DC Fail Relay Panel | DC Fail Relay Panel | [DCAB] : DC Fail Relay Panel | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [DCAB] : DC Fail Relay Panel : Clear/Appear | [37 empty] | 1 | 1 |  | NO | DcPanel
B | N | PWR | BPS-CL | 33KVIFBA | DC Fail Cell | DC Fail Cell | [DCFA] : DC Fail Cell | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [DCFA] : DC Fail Cell : Clear/Appear | [37 empty] | 1 | 2 |  | NO | FailCell
B | N | PWR | BPS-CL | 33KVIFBA | IED WatchDog | IED WatchDog | [WDOG] : IED WatchDog | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG] : IED WatchDog : Clear/Appear | [37 empty] | 1 | 3 |  | NO | IedWtdg
B | N | PWR | BPS-CL | 33KVIFBA | BCU WatchDog | BCU WatchDog | [WDOG] : BCU Watchdog | Operational Alarm |  | DI | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG] : BCU Watchdog : Clear/Appear | [37 empty] | 1 | 4 |  | NO | BcuWtdg
B | N | PWR | BPS-CL | 33KVIFBA | Voltage Transformer Fault alarm | Voltage Transformer Fault alarm | [VTFA] : Voltage Transformer Fault alarm | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [VTFA] : Voltage Transformer Fault alarm : Clear/Appear | [37 empty] | 1 | 5 |  | NO | FaultAlarm
B | N | PWR | BPS-CL | 33KVIFBA | 40MVA T-1 Winding Temp Trip | 40MVA T-1 Winding Temp Trip | [WGTT] : 40MVA T-1 Winding Temperature Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [WGTT] : 40MVA T-1 Winding Temperature Trip : Clear/Trip | [37 empty] | 1 | 6 |  | NO | TempTrip
B | N | PWR | BPS-CL | 33KVIFBA | 40MVA T-1 Winding Temp Alarm | 40MVA T-1 Winding Temp Alarm | [WGTA] : 40MVA T-1 Winding Temperature Alarm | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WGTA] : 40MVA T-1 Winding Temperature Alarm : Clear/Appear | [37 empty] | 1 | 7 |  | NO | TempAlarm
B | N | PWR | BPS-CL | 33KVIFBA | Tap Changer Limit | Tap Changer Limit | [TCER] : Tap Changer Limit | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Set |  |  | Clear | 0: None, 1: Maj | [TCER] : Tap Changer Limit : Clear/Set | [37 empty] | 1 | 8 |  | NO | Limit
B | N | PWR | BPS-CL | 33KVIFBA | Main Transformer Oil Level Alarm | Main Transformer Oil Level Alarm | [MTOA] : Main Transformer Oil Level Alarm | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [MTOA] : Main Transformer Oil Level Alarm : Clear/Appear | [37 empty] | 1 | 9 |  | NO | OilLvAlarm
B | N | PWR | BPS-CL | 33KVIFBA | Tap Changer Oil Level Alarm | Tap Changer Oil Level Alarm | [TOLA] : Tap Changer Oil Level Alarm | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [TOLA] : Tap Changer Oil Level Alarm : Clear/Appear | [37 empty] | 1 | 10 |  | NO | CoolerAlarm
B | N | PWR | BPS-CL | 33KVIFBA | Transformer Fan Cooler Alarm | Transformer Fan Cooler Alarm | [FACA] : Transformer Fan Cooler Alarm | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [FACA] : Transformer Fan Cooler Alarm : Clear/Appear | [37 empty] | 1 | 11 |  | NO | FanAlarm
B | N | PWR | BPS-CL | 33KVIFBA | 40MVA T-1 Main Dehydrating Alarm | 40MVA T-1 Main Dehydrating Alarm | [SSBA] : 40MVA T-1 Dehydrating Alarm | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [SSBA] : 40MVA T-1 Dehydrating Alarm : Clear/Appear | [37 empty] | 1 | 12 |  | NO | DehyAlarm
B | N | PWR | BPS-CL | 33KVIFBA | BCU Card Fail | BCU Card Fail | [WDOG] : BCU Card Fail | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG] : BCU Card Fail : Clear/Appear | [37 empty] | 1 | 13 |  | NO | CardFail
B | Y |  |  |  |  | 66/33KV HV IBT Bay Operational Status
B | N | PWR | BPS-CL | 66KVHVBA | AC Fail Relay Panel / LCC | AC Fail Relay Panel / LCC | [ACFL] : AC Fail Relay Panel / LCC | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Min | [ACFL] : AC Fail Relay Panel / LCC : Clear/Appear | [37 empty] | 1 | 0 |  | NO | AcPanel
B | N | PWR | BPS-CL | 66KVHVBA | DC Fail Relay Panel | DC Fail Relay Panel | [DCAB] : DC Fail Relay Panel | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [DCAB] : DC Fail Relay Panel : Clear/Appear | [37 empty] | 1 | 1 |  | NO | DcPanel
B | N | PWR | BPS-CL | 66KVHVBA | DC Fail LCC Panel | DC Fail LCC Panel | [DCFA] : DC Fail LCC Panel | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [DCFA] : DC Fail LCC Panel : Clear/Appear | [37 empty] | 1 | 2 |  | NO | LccPanel
B | N | PWR | BPS-CL | 66KVHVBA | SF6 Gas Pressure Stage 1 | SF6 Gas Pressure Stage 1 | [GAS1] : SF6 Gas Pressure Stage 1 | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [GAS1] : SF6 Gas Pressure Stage 1 : Clear/Appear | [37 empty] | 1 | 3 |  | NO | Stage1
B | N | PWR | BPS-CL | 66KVHVBA | SF6 Gas Pressure Stage 2 | SF6 Gas Pressure Stage 2 | [GAS2] : SF6 Gas Pressure Stage 2 | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [GAS2] : SF6 Gas Pressure Stage 2 : Clear/Appear | [37 empty] | 1 | 4 |  | NO | Stage2
B | N | PWR | BPS-CL | 66KVHVBA | MasterTrip relay operated | Master Trip relay operated | [MTRO] : Master Trip relay operated | Technical alarm |  | DI | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Crit | [MTRO] : Master Trip relay operated : Clear/Trip | [37 empty] | 1 | 5 |  | NO | Operated
B | N | PWR | BPS-CL | 66KVHVBA | IED WatchDog | IED WatchDog | [WDOG] : IED WatchDog | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG] : IED WatchDog : Clear/Appear | [37 empty] | 1 | 6 |  | NO | IedWtdg
B | N | PWR | BPS-CL | 66KVHVBA | BCU WatchDog | BCU WatchDog | [WDOG] : BCU Watchdog | Operational Alarm |  | DI | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG] : BCU Watchdog : Clear/Appear | [37 empty] | 1 | 7 |  | NO | BcuWtdg
B | N | PWR | BPS-CL | 66KVHVBA | OC/EF Protection Operated | OC/EF Protection Operated | [OEPE] : OC/EF Protection Operated | Operational Alarm |  | DI | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [OEPE] : OC/EF Protection Operated : Clear/Appear | [37 empty] | 1 | 8 |  | NO | ProtOperated
B | N | PWR | BPS-CL | 66KVHVBA | BCU Card Fail | BCU Card Fail | [WDOG] : BCU Card Fail | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG] : BCU Card Fail : Clear/Appear | [37 empty] | 1 | 9 |  | NO | CardFail
B | Y |  |  |  |  | 33kV ST.TX Bay Operational Status
B | N | PWR | BPS-CL | 33KVSTBA | AC Fail Relay Panel / SWGR | AC Fail Relay Panel / SWGR | [ACFL] : AC Fail Relay Panel / SWGR | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Min | [ACFL] : AC Fail Relay Panel / SWGR : Clear/Appear | [37 empty] | 1 | 0 |  | NO | AcPanel
B | N | PWR | BPS-CL | 33KVSTBA | DC Fail Relay Panel | DC Fail Relay Panel | [DCAB] : DC Fail Relay Panel | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [DCAB] : DC Fail Relay Panel : Clear/Appear | [37 empty] | 1 | 1 |  | NO | DcPanel
B | N | PWR | BPS-CL | 33KVSTBA | DC Fail SWGR | DC Fail SWGR | [DCFA] : DC Fail SWGR | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [DCFA] : DC Fail SWGR : Clear/Appear | [37 empty] | 1 | 2 |  | NO | FailSwgr
B | N | PWR | BPS-CL | 33KVSTBA | IED WatchDog | IED WatchDog | [WDOG] : IED WatchDog | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG] : IED WatchDog : Clear/Appear | [37 empty] | 1 | 3 |  | NO | IedWtdg
B | N | PWR | BPS-CL | 33KVSTBA | BCU WatchDog | BCU WatchDog | [WDOG] : BCU Watchdog | Operational Alarm |  | DI | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG] : BCU Watchdog : Clear/Appear | [37 empty] | 1 | 4 |  | NO | BcuWtdg
B | N | PWR | BPS-CL | 33KVSTBA | Voltage Transformer Fault alarm | Voltage Transformer Fault alarm | [VTFA] : Voltage Transformer Fault alarm | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [VTFA] : Voltage Transformer Fault alarm : Clear/Appear | [37 empty] | 1 | 5 |  | NO | FaultAlarm
B | N | PWR | BPS-CL | 33KVSTBA | BCU Card Fail | BCU Card Fail | [WDOG] : BCU Card Fail | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG] : BCU Card Fail : Clear/Appear | [37 empty] | 1 | 6 |  | NO | CardFail
B | Y |  |  |  |  | 66KV Bus Section Bay Operational Status
B | N | PWR | BPS-CL | 66KVBSBA | AC Fail Relay Panel / LCC | AC Fail Relay Panel / LCC | [ACFL] : AC Fail Relay Panel / LCC | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Min | [ACFL] : AC Fail Relay Panel / LCC : Clear/Appear | [37 empty] | 1 | 0 |  | NO | AcPanel
B | N | PWR | BPS-CL | 66KVBSBA | DC Fail Relay Panel | DC Fail Relay Panel | [DCAB] : DC Fail Relay Panel | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [DCAB] : DC Fail Relay Panel : Clear/Appear | [37 empty] | 1 | 1 |  | NO | DcPanel
B | N | PWR | BPS-CL | 66KVBSBA | DC Fail LCC Panel | DC Fail LCC Panel | [DCFA] : DC Fail LCC Panel | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [DCFA] : DC Fail LCC Panel : Clear/Appear | [37 empty] | 1 | 2 |  | NO | LccPanel
B | N | PWR | BPS-CL | 66KVBSBA | SF6 Gas Pressure 1st Stage | SF6 Gas Pressure 1st Stage | [GAS1] : SF6 Gas Pressure 1st Stage | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [GAS1] : SF6 Gas Pressure 1st Stage : Clear/Appear | [37 empty] | 1 | 3 |  | NO | Stage1
B | N | PWR | BPS-CL | 66KVBSBA | SF6 Gas Pressure 2nd Stage | SF6 Gas Pressure 2nd Stage | [GAS2] : SF6 Gas Pressure 2nd Stage | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [GAS2] : SF6 Gas Pressure 2nd Stage : Clear/Appear | [37 empty] | 1 | 4 |  | NO | Stage2
B | N | PWR | BPS-CL | 66KVBSBA | MasterTrip relay operated | Master Trip relay operated | [MTRO] : Master Trip relay operated | Technical alarm |  | DI | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [MTRO] : Master Trip relay operated : Clear/Appear | [37 empty] | 1 | 5 |  | NO | Operated
B | N | PWR | BPS-CL | 66KVBSBA | IED WatchDog | IED WatchDog | [WDOG**] : IED WatchDog | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG**] : IED WatchDog : Clear/Appear | [37 empty] | 1 | 6 |  | NO | IedWtdg
B | N | PWR | BPS-CL | 66KVBSBA | BCU WatchDog | BCU WatchDog | [WDOG**] : BCU Watchdog | Operational Alarm |  | DI | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG**] : BCU Watchdog : Clear/Appear | [37 empty] | 1 | 7 |  | NO | BcuWtdg
B | N | PWR | BPS-CL | 66KVBSBA | Voltage Transformer Fault alarm | Voltage Transformer Fault alarm | [VTFA] : Voltage Transformer Fault alarm | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [VTFA] : Voltage Transformer Fault alarm : Clear/Appear | [37 empty] | 1 | 8 |  | NO | FaultAlarm
B | N | PWR | BPS-CL | 66KVBSBA | Breaker failure stage 1 | Breaker failure stage 1 | [CBFO] : Breaker failure stage 1 | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [CBFO] : Breaker failure stage 1 : Clear/Appear | [37 empty] | 1 | 9 |  | NO | BrkStage1
B | N | PWR | BPS-CL | 66KVBSBA | Breaker failure stage 2 | Breaker failure stage 2 | [CBFO] : Breaker failure stage 2 | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [CBFO] : Breaker failure stage 2 : Clear/Appear | [37 empty] | 1 | 10 |  | NO | BrkStage2
B | N | PWR | BPS-CL | 66KVBSBA | BCU Card Fail | BCU Card Fail | [WDOG] : BCU Card Fail | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG] : BCU Card Fail : Clear/Appear | [37 empty] | 1 | 11 |  | NO | CardFail
B | Y |  |  |  |  | 33KV Bus Section Bay Operational Status
B | N | PWR | BPS-CL | 33KVBSBA | AC Fail Relay Panel / Cell | AC Fail Relay Panel / Cell | [ACFL] : AC Fail Relay Panel / Cell | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Min | [ACFL] : AC Fail Relay Panel / Cell : Clear/Appear | [37 empty] | 1 | 0 |  | NO | AcPanel
B | N | PWR | BPS-CL | 33KVBSBA | DC Fail Relay Panel | DC Fail Relay Panel | [DCAB] : DC Fail Relay Panel | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [DCAB] : DC Fail Relay Panel : Clear/Appear | [37 empty] | 1 | 1 |  | NO | DcPanel
B | N | PWR | BPS-CL | 33KVBSBA | DC Fail Cell | DC Fail Cell | [DCFA] : DC Fail Cell | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [DCFA] : DC Fail Cell : Clear/Appear | [37 empty] | 1 | 2 |  | NO | FailCell
B | N | PWR | BPS-CL | 33KVBSBA | MasterTrip relay operated | Master Trip relay operated | [MTRO] : Master Trip relay operated | Technical alarm |  | DI | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [MTRO] : Master Trip relay operated : Clear/Appear | [37 empty] | 1 | 3 |  | NO | Operated
B | N | PWR | BPS-CL | 33KVBSBA | IED WatchDog | IED WatchDog | [WDOG**] : IED WatchDog | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG**] : IED WatchDog : Clear/Appear | [37 empty] | 1 | 4 |  | NO | IedWtdg
B | N | PWR | BPS-CL | 33KVBSBA | BCU WatchDog | BCU WatchDog | [WDOG**] : BCU Watchdog | Operational Alarm |  | DI | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG**] : BCU Watchdog : Clear/Appear | [37 empty] | 1 | 5 |  | NO | BcuWtdg
B | N | PWR | BPS-CL | 33KVBSBA | Voltage Transformer Fault alarm | Voltage Transformer Fault alarm | [VTFA] : Voltage Transformer Fault alarm | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [VTFA] : Voltage Transformer Fault alarm : Clear/Appear | [37 empty] | 1 | 6 |  | NO | FaultAlarm
B | N | PWR | BPS-CL | 33KVBSBA | Synchronisation Fail | Synchronisation Fail | [SYCO] : Synchronisation Fail | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [SYCO] : Synchronisation Fail : Clear/Appear | [37 empty] | 1 | 7 |  | NO | SyncFail
B | N | PWR | BPS-CL | 33KVBSBA | BCU Card Fail | BCU Card Fail | [WDOG] : BCU Card Fail | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG] : BCU Card Fail : Clear/Appear | [37 empty] | 1 | 8 |  | NO | CardFail
B | Y |  |  |  |  | 33KV Outgoing Feeder Bay Operational Status
B | N | PWR | BPS-CL | 33KVOFBA | AC Fail Relay Panel / SWGR | AC Fail Relay Panel / SWGR | [ACFL] : AC Fail Relay Panel / SWGR | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Min | [ACFL] : AC Fail Relay Panel / SWGR : Clear/Appear | [37 empty] | 1 | 0 |  | NO | AcPanel
B | N | PWR | BPS-CL | 33KVOFBA | DC Fail Relay Panel | DC Fail Relay Panel | [DCAB] : DC Fail Relay Panel | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [DCAB] : DC Fail Relay Panel : Clear/Appear | [37 empty] | 1 | 1 |  | NO | DcPanel
B | N | PWR | BPS-CL | 33KVOFBA | DC Fail SWGR | DC Fail SWGR | [DCFA] : DC Fail SWGR | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [DCFA] : DC Fail SWGR : Clear/Appear | [37 empty] | 1 | 2 |  | NO | FailSwgr
B | N | PWR | BPS-CL | 33KVOFBA | IED WatchDog | IED WatchDog | [WDOG**] : IED WatchDog | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG**] : IED WatchDog : Clear/Appear | [37 empty] | 1 | 3 |  | NO | IedWtdg
B | N | PWR | BPS-CL | 33KVOFBA | BCU WatchDog | BCU WatchDog | [WDOG**] : BCU Watchdog | Operational Alarm |  | DI | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG**] : BCU Watchdog : Clear/Appear | [37 empty] | 1 | 4 |  | NO | BcuWtdg
B | N | PWR | BPS-CL | 33KVOFBA | Voltage Transformer Fault alarm | Voltage Transformer Fault alarm | [VTFA] : Voltage Transformer Fault alarm | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [VTFA] : Voltage Transformer Fault alarm : Clear/Appear | [37 empty] | 1 | 5 |  | NO | FaultAlarm
B | N | PWR | BPS-CL | 33KVOFBA | BCU Card Fail | BCU Card Fail | [WDOG] : BCU Card Fail | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WDOG] : BCU Card Fail : Clear/Appear | [37 empty] | 1 | 6 |  | NO | CardFail
A7 | Y |  |  |  |  | 66kV General Status HV LVAC
A9 | N | PWR | BPS-CL | GTW | [GTW]: Connection Status | [GTW]: Connection Status | [GTW]: Connection Status | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | OK | FAIL |  |  | OK | 0: None, 1: Maj | [GTW]: Connection Status : OK/FAIL | [37 empty] | 1 | 1 |  | N | ConnSts
B | Y |  |  |  |  | 66kV General Status HV LVAC
B | N | PWR | BPS-CL | 66KVLVAC | Incomer 1 Breaker Trip | Incomer 1 Breaker Trip | [IN1T] : Incomer 1 Breaker Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [IN1T] : Incomer 1 Breaker Trip : Clear/Trip | [37 empty] | 1 | 0 |  | NO | BrkTrip1
B | N | PWR | BPS-CL | 66KVLVAC | Incomer 2 Breaker Trip | Incomer 2 Breaker Trip | [IN2T] : Incomer 2 Breaker Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [IN2T] : Incomer 2 Breaker Trip : Clear/Trip | [37 empty] | 1 | 1 |  | NO | BrkTrip2
B | N | PWR | BPS-CL | 66KVLVAC | Bus Section Breaker Trip | Bus Section Breaker Trip | [BUST] : Bus Section Breaker Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [BUST] : Bus Section Breaker Trip : Clear/Trip | [37 empty] | 1 | 2 |  | NO | SecBrkTrip
B | N | PWR | BPS-CL | 66KVLVAC | Bus-1 Feeder Fault | Bus-1 Feeder Fault | [FALB] : Bus-1 Feeder Fault | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [FALB] : Bus-1 Feeder Fault : Clear/Appear | [37 empty] | 1 | 3 |  | NO | Fault1
B | N | PWR | BPS-CL | 66KVLVAC | Bus-2 Feeder Fault | Bus-2 Feeder Fault | [FALR] : Bus-2 Feeder Fault | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [FALR] : Bus-2 Feeder Fault : Clear/Appear | [37 empty] | 1 | 4 |  | NO | Fault2
B | N | PWR | BPS-CL | 66KVLVAC | AC Control MCB Off/Trip | AC Control MCB Off/Trip | [TRAS] : AC Control MCB Off/Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [TRAS] : AC Control MCB Off/Trip : Clear/Appear | [37 empty] | 1 | 5 |  | NO | AcOff
B | N | PWR | BPS-CL | 66KVLVAC | DC Control MCB Off/Trip | DC Control MCB Off/Trip | [LVDC] : DC Control MCB Off/Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [LVDC] : DC Control MCB Off/Trip : Clear/Appear | [37 empty] | 1 | 6 |  | NO | DcOff
B | Y |  |  |  |  | 66kV DC Battery Charger
B | N | PWR | BPS-CL | 66KVBATC | Charger Fault | Charger Fault | [CH1F] : Charger Fault | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [CH1F] : Charger Fault : Clear/Appear | [37 empty] | 1 | 0 |  | NO | ChargerFault
B | N | PWR | BPS-CL | 66KVBATC | AC Supply Failure 1 | AC Supply Failure | [C1AS] : AC Supply Failure | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [C1AS] : AC Supply Failure : Clear/Appear | [37 empty] | 1 | 1 |  | NO | AcFail1
B | N | PWR | BPS-CL | 66KVBATC | AC Supply Failure 2 | AC Supply Failure | [CH1F] : Battery Charger Fail | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [CH1F] : Battery Charger Fail : Clear/Appear | [37 empty] | 1 | 2 |  | NO | AcFail2
B | N | PWR | BPS-CL | 66KVBATC | Charger on Equalizer Charge | Charger on Equalizer Charge | [CHBA] : Charger on Equalizer Charge | Operational event |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Reset | Set |  |  | Reset | 0: None, 1: None | [CHBA] : Charger on Equalizer Charge : Reset/Set | [37 empty] | 1 | 3 |  | NO | EqualizerCharge
B | N | PWR | BPS-CL | 66KVBATC | Charger Under Voltage | Charger Under Voltage | [C1UV] : Charger Under Voltage | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [C1UV] : Charger Under Voltage : Clear/Appear | [37 empty] | 1 | 4 |  | NO | UnderVolt
B | N | PWR | BPS-CL | 66KVBATC | Charger on Boost Charge | Charger on Boost Charge | [CHBA] : Charger on Boost Charge | Operational event |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Reset | Set |  |  | Reset | 0: None, 1: None | [CHBA] : Charger on Boost Charge : Reset/Set | [37 empty] | 1 | 5 |  | NO | BoostCharge
B | N | PWR | BPS-CL | 66KVBATC | Battery Fuse Failure | Battery Fuse Failure | [B1FF] : Battery Fuse Failure | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [B1FF] : Battery Fuse Failure : Clear/Appear | [37 empty] | 1 | 6 |  | NO | FuseFail
B | N | PWR | BPS-CL | 66KVBATC | Battery Charger Fan Fail | Battery Charger Fan Fail | [CH1F] : Battery Charger Fan Fail | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [CH1F] : Battery Charger Fan Fail : Clear/Appear | [37 empty] | 1 | 7 |  | NO | FanFail
B | N | PWR | BPS-CL | 66KVBATC | Charger Overload | Charger Overload | [C1LF] : Charger Overload | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [C1LF] : Charger Overload : Clear/Appear | [37 empty] | 1 | 8 |  | NO | Overload
B | N | PWR | BPS-CL | 66KVBATC | DC Supply Failure | DC Supply Failure | [C1AS] : DC Supply Failure | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [C1AS] : DC Supply Failure : Clear/Appear | [37 empty] | 1 | 9 |  | NO | SupFailure
B | Y |  |  |  |  | 66kV General Status HV LVDC
B | N | PWR | BPS-CL | 66KVLVDC | Incomer 1 Trip | Incomer 1 Trip | [LVOL] : Incomer 1 Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [LVOL] : Incomer 1 Trip : Clear/Trip | [37 empty] | 1 | 0 |  | NO | Trip1
B | N | PWR | BPS-CL | 66KVLVDC | Incomer 2 Trip | Incomer 2 Trip | [LVOR] : Incomer 2 Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [LVOR] : Incomer 2 Trip : Clear/Trip | [37 empty] | 1 | 1 |  | NO | Trip2
B | N | PWR | BPS-CL | 66KVLVDC | AC Control MCB Off/Trip | AC Control MCB Off/Trip | [TRAS] : AC Control MCB Off/Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [TRAS] : AC Control MCB Off/Trip : Clear/Appear | [37 empty] | 1 | 2 |  | NO | AcOff
B | N | PWR | BPS-CL | 66KVLVDC | DC Feeder Left Bus Trip | DC Feeder Left Bus Trip | [FELF] : DC Feeder Left Bus Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [FELF] : DC Feeder Left Bus Trip : Clear/Trip | [37 empty] | 1 | 3 |  | NO | LeftTrip
B | N | PWR | BPS-CL | 66KVLVDC | DC Feeder Right Bus Trip | DC Feeder Right Bus Trip | [FELR] : DC Feeder Right Bus Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [FELR] : DC Feeder Right Bus Trip : Clear/Trip | [37 empty] | 1 | 4 |  | NO | RightTrip
B | N | PWR | BPS-CL | 66KVLVDC | Under Voltage Left Busbar | Under Voltage Left Busbar | [LVOL] : Under Voltage Left Busbar | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [LVOL] : Under Voltage Left Busbar : Clear/Appear | [37 empty] | 1 | 5 |  | NO | LeftBus
B | N | PWR | BPS-CL | 66KVLVDC | Under Voltage Right Busbar | Under Voltage Right Busbar | [LVOR] : Under Voltage Right Busbar | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [LVOR] : Under Voltage Right Busbar : Clear/Appear | [37 empty] | 1 | 6 |  | NO | RightBus
B | N | PWR | BPS-CL | 66KVLVDC | Incomer-1 Earthfault | Incomer-1 Earthfault | [EXF1] : Incomer-1 Earthfault | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [EXF1] : Incomer-1 Earthfault : Clear/Appear | [37 empty] | 1 | 7 |  | NO | Earthfault1
B | N | PWR | BPS-CL | 66KVLVDC | Incomer-2 Earthfault | Incomer-2 Earthfault | [EXF2] : Incomer-2 Earthfault | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [EXF2] : Incomer-2 Earthfault : Clear/Appear | [37 empty] | 1 | 8 |  | NO | Earthfault2
B | N | PWR | BPS-CL | 66KVLVDC | DC Control MCB Off/Trip | DC Control MCB Off/Trip | [TRDC] : DC Control MCB Off/Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [TRDC] : DC Control MCB Off/Trip : Clear/Appear | [37 empty] | 1 | 9 |  | NO | DcOff
B | Y |  |  |  |  | 33kV General Status LV LVDC
B | N | PWR | BPS-CL | 33KVLVDC | Incomer-1 MCCB Trip | Incomer-1 MCCB Trip | [IN1T] : Incomer-1 MCCB Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [IN1T] : Incomer-1 MCCB Trip : Clear/Trip | [37 empty] | 1 | 0 |  | NO | MccbTrip1
B | N | PWR | BPS-CL | 33KVLVDC | Incomer-2 MCCB Trip | Incomer-2 MCCB Trip | [IN2T] : Incomer-2 MCCB Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [IN2T] : Incomer-2 MCCB Trip : Clear/Trip | [37 empty] | 1 | 1 |  | NO | MccbTrip2
B | N | PWR | BPS-CL | 33KVLVDC | Bus Section MCCB Trip | Bus Section MCCB Trip | [BUST] : Bus Section MCCB Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [BUST] : Bus Section MCCB Trip : Clear/Trip | [37 empty] | 1 | 2 |  | NO | SecMccbTrip
B | N | PWR | BPS-CL | 33KVLVDC | Bus-1 O/G Trip | Bus-1 O/G Trip | [FALB] : Bus-1 O/G Trip | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Crit | [FALB] : Bus-1 O/G Trip : Clear/Trip | [37 empty] | 1 | 3 |  | NO | OgTrip1
B | N | PWR | BPS-CL | 33KVLVDC | Bus-2 O/G Trip | Bus-2 O/G Trip | [FALR] : Bus-2 O/G Trip | Operational Alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Crit | [FALR] : Bus-2 O/G Trip : Clear/Trip | [37 empty] | 1 | 4 |  | NO | OgTrip2
B | N | PWR | BPS-CL | 33KVLVDC | AC Control MCB Off/Trip | AC Control MCB Off/Trip | [TRAS] : AC Control MCB Off/Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [TRAS] : AC Control MCB Off/Trip : Clear/Appear | [37 empty] | 1 | 5 |  | NO | AcOff
B | N | PWR | BPS-CL | 33KVLVDC | DC Control MCB Off/Trip | DC Control MCB Off/Trip | [LVDC] : DC Control MCB Off/Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [LVDC] : DC Control MCB Off/Trip : Clear/Appear | [37 empty] | 1 | 6 |  | NO | DcOff
A9 | Y |  |  |  |  | 66KV Incoming Feeder Bay Measurement Value
A9 | N | PWR | BPS-CL | 66KVIFMV | R Phase Current | R Phase Current | R Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 960,0 |  |  | Line Current Phase R : 0 / 960 | [9 empty] | +-19,2 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 0 |  | YES | Rphase
A9 | N | PWR | BPS-CL | 66KVIFMV | Y Phase Current | Y Phase Current | Y Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 960,0 |  |  | Line Current Phase Y : 0 / 960 | [9 empty] | +-19,2 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 1 |  | YES | Yphase
A9 | N | PWR | BPS-CL | 66KVIFMV | B Phase Current | B Phase Current | B Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 960,0 |  |  | Line Current Phase B : 0 / 960 | [9 empty] | +-19,2 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 2 |  | YES | Bphase
A9 | N | PWR | BPS-CL | 66KVIFMV | Neutral Current In | Neutral Current In | Neutral Current (In) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 960,0 |  |  | Neutral Current In : 0 / 960 | [9 empty] | +-19,2 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 3 |  | YES | NeuCurr
A9 | N | PWR | BPS-CL | 66KVIFMV | RY Phase Voltage | RY Phase Voltage | RY Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 79,20 |  |  | Line Voltage RY : 0 / 79,20 | [9 empty] | +-1,58kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 4 |  | YES | RyPhase
A9 | N | PWR | BPS-CL | 66KVIFMV | YB Phase Voltage | YB Phase Voltage | YB Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 79,20 |  |  | Line Voltage YB : 0 / 79,20 | [9 empty] | +-1,58kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 5 |  | YES | YbPhase
A9 | N | PWR | BPS-CL | 66KVIFMV | BR Phase Voltage | BR Phase Voltage | BR Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 79,20 |  |  | Line Voltage BR : 0 / 79,20 | [9 empty] | +-1,58kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 6 |  | YES | BrPhase
A9 | N | PWR | BPS-CL | 66KVIFMV | Zero Sequence Voltage (V0) | Zero Sequence Voltage (V0) | Zero Sequence Voltage (V0) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 45,73 |  |  | Zero Sequence Voltage : 0 / 45,73 | [9 empty] | +-0,91kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 7 |  | YES | ZeroVolt
A9 | N | PWR | BPS-CL | 66KVIFMV | Active Power | Active Power | [MW] : Active Power | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MW | -109,74 | 109,74 |  |  | Active Power : -109,74 / 109,74 | [9 empty] | +-2,19MW | 0 | Power = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 8 |  | YES | ActivePower
A9 | N | PWR | BPS-CL | 66KVIFMV | Reactive Power | Reactive Power | [MVAR] : Reactive Power | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MVAR | -109,74 | 109,74 |  |  | Reactive Power : -109,74 / 109,74 | [9 empty] | +-2,19MVAR | 0 | Power = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 9 |  | YES | ReacPower
A9 | N | PWR | BPS-CL | 66KVIFMV | Apparent Power | Apparent Power | Apparent Power | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MVA | -109,74 | 109,74 |  |  | Apparent Power : -109,74 / 109,74 | [9 empty] | +-2,19MVA | 0 | Power = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 10 |  | YES | AppPower
A9 | N | PWR | BPS-CL | 66KVIFMV | Power Factor | Power Factor | Power Factor | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [17 empty] | -1 | 1 |  |  | Power Factor : -1 / 1 | [9 empty] | +-0,02 | 0 | PowerFactor = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 11 |  | YES | PowerFactor
A9 | N | PWR | BPS-CL | 66KVIFMV | Frequency | Frequency | Frequency | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | Hz | 0 | 60 |  |  | Frequency : 0 / 60 | [9 empty] | +-0,12Hz | 0 | Frequency = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 12 |  | YES | Frequency
A9 | Y |  |  |  |  | 33KV Incomer Measurement Value
A9 | N | PWR | BPS-CL | 33KVIFMV | R Phase Current | R Phase Current | R Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 1200 |  |  | Line Current Phase R : 0 / 1200 | [9 empty] | +-24 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 0 |  | YES | Rphase
A9 | N | PWR | BPS-CL | 33KVIFMV | Y Phase Current | Y Phase Current | Y Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 1200 |  |  | Line Current Phase Y : 0 / 1200 | [9 empty] | +-24 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 1 |  | YES | Yphase
A9 | N | PWR | BPS-CL | 33KVIFMV | B Phase Current | B Phase Current | B Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 1200 |  |  | Line Current Phase B : 0 / 1200 | [9 empty] | +-24 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 2 |  | YES | Bphase
A9 | N | PWR | BPS-CL | 33KVIFMV | Neutral Current In | Neutral Current In | Neutral Current (In) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 1200 |  |  | Neutral Current In : 0 / 1200 | [9 empty] | +-24 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 3 |  | YES | NeuCurr
A9 | N | PWR | BPS-CL | 33KVIFMV | RY Phase Voltage | RY Phase Voltage | RY Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 39,6 |  |  | Line Voltage RY : 0 / 39,6 | [9 empty] | +-0,79kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 4 |  | YES | RyPhase
A9 | N | PWR | BPS-CL | 33KVIFMV | YB Phase Voltage | YB Phase Voltage | YB Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 39,6 |  |  | Line Voltage YB : 0 / 39,6 | [9 empty] | +-0,79kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 5 |  | YES | YbPhase
A9 | N | PWR | BPS-CL | 33KVIFMV | BR Phase Voltage | BR Phase Voltage | BR Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 39,6 |  |  | Line Voltage BR : 0 / 39,6 | [9 empty] | +-0,79kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 6 |  | YES | BrPhase
A9 | N | PWR | BPS-CL | 33KVIFMV | Zero Sequence Voltage (V0) | Zero Sequence Voltage (V0) | Zero Sequence Voltage (V0) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 7,62 |  |  | Zero Sequence Voltage : 0 / 7,62 | [9 empty] | +-0,15kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 7 |  | YES | ZeroVolt
A9 | N | PWR | BPS-CL | 33KVIFMV | Active Power | Active Power | [MW] : Active Power | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MW | -68.58 | 68.58 |  |  | Active Power : -68,58/68,58 | [9 empty] | +-1,37MW | 0 | Power = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 8 |  | YES | ActivePower
A9 | N | PWR | BPS-CL | 33KVIFMV | Reactive Power | Reactive Power | [MVAR] : Reactive Power | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MVAR | -68.58 | 68.58 |  |  | Reactive Power : -68,58/68,58 | [9 empty] | +-1,37MVAR | 0 | Power = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 9 |  | YES | ReacPower
A9 | N | PWR | BPS-CL | 33KVIFMV | Apparent Power | Apparent Power | Apparent Power (S) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MVA | -68.58 | 68.58 |  |  | Apparent Power : -68,58/68,58 | [9 empty] | +-1,37MVA | 0 | Power = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 10 |  | YES | AppPower
A9 | N | PWR | BPS-CL | 33KVIFMV | Power Factor | Power Factor | Power Factor (P.F) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [17 empty] | -1 | 1 |  |  | Power Factor : -1 / 1 | [9 empty] | +-0,02 | 0 | PowerFactor = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 11 |  | YES | PowerFactor
A9 | N | PWR | BPS-CL | 33KVIFMV | Frequency | Frequency | Frequency (Hz) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | Hz | 0 | 60 |  |  | Frequency : 0 / 60 | [9 empty] | +-0,12Hz | 0 | Frequency = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 12 |  | YES | Frequency
A9 | Y |  |  |  |  | 66/33KV HV IBT Bay Measurement Value
A9 | N | PWR | BPS-CL | 66KVHVMV | R Phase Current | R Phase Current | R Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 480,00 |  |  | Line Current Phase R : 0 / 480 | [9 empty] | +-9,6 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 0 |  | YES | Rphase
A9 | N | PWR | BPS-CL | 66KVHVMV | Y Phase Current | Y Phase Current | Y Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 480,00 |  |  | Line Current Phase Y : 0 / 480 | [9 empty] | +-9,6 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 1 |  | YES | Yphase
A9 | N | PWR | BPS-CL | 66KVHVMV | B Phase Current | B Phase Current | B Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 480,00 |  |  | Line Current Phase B : 0 / 480 | [9 empty] | +-9,6 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 2 |  | YES | Bphase
A9 | N | PWR | BPS-CL | 66KVHVMV | Neutral Current In | Neutral Current In | Neutral Current (In) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 480,00 |  |  | Neutral Current In : 0 / 480 | [9 empty] | +-9,6 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 3 |  | YES | NeuCurr
A9 | N | PWR | BPS-CL | 66KVHVMV | RY Phase Voltage | RY Phase Voltage | RY Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 79,20 |  |  | Line Voltage RY : 0 / 79,20 | [9 empty] | +-1,58kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 4 |  | YES | RyPhase
A9 | N | PWR | BPS-CL | 66KVHVMV | YB Phase Voltage | YB Phase Voltage | YB Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 79,20 |  |  | Line Voltage YB : 0 / 79,20 | [9 empty] | +-1,58kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 5 |  | YES | YbPhase
A9 | N | PWR | BPS-CL | 66KVHVMV | BR Phase Voltage | BR Phase Voltage | BR Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 79,20 |  |  | Line Voltage BR : 0 / 79,20 | [9 empty] | +-1,58kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 6 |  | YES | BrPhase
A9 | N | PWR | BPS-CL | 66KVHVMV | Zero Sequence Voltage (V0) | Zero Sequence Voltage (V0) | Zero Sequence Voltage (V0) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 45,73 |  |  | Zero Sequence Voltage : 0 / 45,73 | [9 empty] | +-0,91kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 7 |  | YES | ZeroVolt
A9 | N | PWR | BPS-CL | 66KVHVMV | Active Power | Active Power | [MW] : Active Power | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MW | -54.87 | 54.87 |  |  | Active Power : -54,87 / 54,87 | [9 empty] | +-1,10MW | 0 | Power = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 8 |  | YES | ActivePower
A9 | N | PWR | BPS-CL | 66KVHVMV | Reactive Power | Reactive Power | [MVAR] : Reactive Power | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MVAR | -54.87 | 54.87 |  |  | Reactive Power : -54,87 / 54,87 | [9 empty] | +-1,10MVAR | 0 | Power = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 9 |  | YES | ReacPower
A9 | N | PWR | BPS-CL | 66KVHVMV | Apparent Power | Apparent Power | Apparent Power (S) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MVA | -54.87 | 54.87 |  |  | Apparent Power : -54,87 / 54,87 | [9 empty] | +-1,10MVA | 0 | Power = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 10 |  | YES | AppPower
A9 | N | PWR | BPS-CL | 66KVHVMV | Power Factor | Power Factor | Power Factor (P.F) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [17 empty] | -1 | 1 |  |  | Power Factor : -1 / 1 | [9 empty] | +-0,02 | 0 | PowerFactor = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 11 |  | YES | PowerFactor
A9 | N | PWR | BPS-CL | 66KVHVMV | Frequency | Frequency | Frequency (Hz) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | Hz | 0 | 60 |  |  | Frequency : 0 / 60 | [9 empty] | +-0,12Hz | 0 | Frequency = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 12 |  | YES | Frequency
A9 | Y |  |  |  |  | 33kV ST.TX Bay Measurement Value
A9 | N | PWR | BPS-CL | 33KVSTMV | R Phase Current | R Phase Current | R Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 240,00 |  |  | Line Current Phase R : 0 / 240 | [9 empty] | +-4,80 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 0 |  | YES | Rphase
A9 | N | PWR | BPS-CL | 33KVSTMV | Y Phase Current | Y Phase Current | Y Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 240,00 |  |  | Line Current Phase Y : 0 / 240 | [9 empty] | +-4,80 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 1 |  | YES | Yphase
A9 | N | PWR | BPS-CL | 33KVSTMV | B Phase Current | B Phase Current | B Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 240,00 |  |  | Line Current Phase B : 0 / 240 | [9 empty] | +-4,80 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 2 |  | YES | Bphase
A9 | N | PWR | BPS-CL | 33KVSTMV | Neutral Current In | Neutral Current In | Neutral Current (In) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 240,00 |  |  | Neutral Current In : 0 / 240 | [9 empty] | +-4,80 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 3 |  | YES | NeuCurr
A9 | N | PWR | BPS-CL | 33KVSTMV | RY Phase Voltage | RY Phase Voltage | RY Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 39.6 |  |  | Line Voltage RY : 0 / 39,60 | [9 empty] | +-0,79kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 4 |  | YES | RyPhase
A9 | N | PWR | BPS-CL | 33KVSTMV | YB Phase Voltage | YB Phase Voltage | YB Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 39.6 |  |  | Line Voltage YB : 0 / 39,60 | [9 empty] | +-0,79kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 5 |  | YES | YbPhase
A9 | N | PWR | BPS-CL | 33KVSTMV | BR Phase Voltage | BR Phase Voltage | BR Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 39.6 |  |  | Line Voltage BR : 0 / 39,60 | [9 empty] | +-0,79kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 6 |  | YES | BrPhase
A9 | N | PWR | BPS-CL | 33KVSTMV | Zero Sequence Voltage (V0) | Zero Sequence Voltage (V0) | Zero Sequence Voltage (V0) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 22,86 |  |  | Zero Sequence Voltage : 0 / 22,86 | [9 empty] | +-0,46kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 7 |  | YES | ZeroVolt
A9 | N | PWR | BPS-CL | 33KVSTMV | Active Power | Active Power | [MW] : Active Power | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MW | -27.44 | 27.44 |  |  | Active Power : -27,44/27,44 | [9 empty] | +-0,55MW | 0 | Power = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 8 |  | YES | ActivePower
A9 | N | PWR | BPS-CL | 33KVSTMV | Reactive Power | Reactive Power | [MVAR] : Reactive Power | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MVAR | -27.44 | 27.44 |  |  | Reactive Power : -27,44/27,44 | [9 empty] | +-0,55MVAR | 0 | Power = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 9 |  | YES | ReacPower
A9 | N | PWR | BPS-CL | 33KVSTMV | Apparent Power | Apparent Power | Apparent Power (S) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MVA | -27.44 | 27.44 |  |  | Apparent Power : -27,44/27,44 | [9 empty] | +-0,55MVA | 0 | Power = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 10 |  | YES | AppPower
A9 | N | PWR | BPS-CL | 33KVSTMV | Power Factor | Power Factor | Power Factor (P.F) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [17 empty] | -1 | 1 |  |  | Power Factor : -1 / 1 | [9 empty] | +-0,02 | 0 | PowerFactor = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 11 |  | YES | PowerFactor
A9 | N | PWR | BPS-CL | 33KVSTMV | Frequency | Frequency | Frequency (Hz) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | Hz | 0 | 60 |  |  | Frequency : 0 / 60 | [9 empty] | +-0,12Hz | 0 | Frequency = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 12 |  | YES | Frequency
A9 | Y |  |  |  |  | 66KV Bus Section Bay Measurement Value
A9 | N | PWR | BPS-CL | 66KVBSMV | R Phase Current | R Phase Current | R Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 2400,00 |  |  | Line Current Phase R : 0 / 2400 | [9 empty] | +-48,0 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 0 |  | YES | Rphase
A9 | N | PWR | BPS-CL | 66KVBSMV | Y Phase Current | Y Phase Current | Y Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 2400,00 |  |  | Line Current Phase Y : 0 / 2400 | [9 empty] | +-48,0 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 1 |  | YES | Yphase
A9 | N | PWR | BPS-CL | 66KVBSMV | B Phase Current | B Phase Current | B Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 2400,00 |  |  | Line Current Phase B : 0 / 2400 | [9 empty] | +-48,0 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 2 |  | YES | Bphase
A9 | N | PWR | BPS-CL | 66KVBSMV | Neutral Current In | Neutral Current In | Neutral Current (In) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 2400,00 |  |  | Neutral Current In : 0 / 2400 | [9 empty] | +-48,0 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 3 |  | YES | NeuCurr
A9 | N | PWR | BPS-CL | 66KVBSMV | RY Phase Voltage | RY Phase Voltage | RY Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 79,20 |  |  | Line Voltage RY : 0 / 79,20 | [9 empty] | +-1,58kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 4 |  | YES | RyPhase
A9 | N | PWR | BPS-CL | 66KVBSMV | YB Phase Voltage | YB Phase Voltage | YB Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 79,20 |  |  | Line Voltage YB : 0 / 79,20 | [9 empty] | +-1,58kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 5 |  | YES | YbPhase
A9 | N | PWR | BPS-CL | 66KVBSMV | BR Phase Voltage | BR Phase Voltage | BR Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 79,20 |  |  | Line Voltage BR : 0 / 79,20 | [9 empty] | +-1,58kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 6 |  | YES | BrPhase
A9 | N | PWR | BPS-CL | 66KVBSMV | Zero Sequence Voltage (V0) | Zero Sequence Voltage (V0) | Zero Sequence Voltage (V0) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 45,73 |  |  | Zero Sequence Voltage : 0 / 45,73 | [9 empty] | +-0,91kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 7 |  | YES | ZeroVolt
A9 | N | PWR | BPS-CL | 66KVBSMV | Active Power | Active Power | [MW] : Active Power | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MW | -274,4 | 274.4 |  |  | Active Power : -274,4 / 274,4 | [9 empty] | +-5,5MW | 0 | Power = RawValue/10; Raw Value is Signed Int16 | [10 empty] | 16 | 8 |  | YES | ActivePower
A9 | N | PWR | BPS-CL | 66KVBSMV | Reactive Power | Reactive Power | [MVAR] : Reactive Power | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MVAR | -274.4 | 274.4 |  |  | Reactive Power : -274,4 / 274,4 | [9 empty] | +-5,5MVAR | 0 | Power = RawValue/10; Raw Value is Signed Int16 | [10 empty] | 16 | 9 |  | YES | ReacPower
A9 | N | PWR | BPS-CL | 66KVBSMV | Apparent Power | Apparent Power | Apparent Power (S) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MVA | -274.4 | 274.4 |  |  | Apparent Power :-274,4 / 274,4 | [9 empty] | +-5,5MVA | 0 | Power = RawValue/10; Raw Value is Signed Int16 | [10 empty] | 16 | 10 |  | YES | AppPower
A9 | N | PWR | BPS-CL | 66KVBSMV | Power Factor | Power Factor | Power Factor (P.F) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [17 empty] | -1 | 1 |  |  | Power Factor : -1 / 1 | [9 empty] | +-0,02 | 0 | PowerFactor = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 11 |  | YES | PowerFactor
A9 | N | PWR | BPS-CL | 66KVBSMV | Frequency | Frequency | Frequency (Hz) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | Hz | 0 | 60 |  |  | Frequency : 0 / 60 | [9 empty] | +-0,12Hz | 0 | Frequency = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 12 |  | YES | Frequency
A9 | Y |  |  |  |  | 33KV Bus Section Bay Measurement Value
A9 | N | PWR | BPS-CL | 33KVBSMV | R Phase Current | R Phase Current | R Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 2400 |  |  | Line Current Phase R : 0 / 2400 | [9 empty] | +-48,0 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 0 |  | YES | Rphase
A9 | N | PWR | BPS-CL | 33KVBSMV | Y Phase Current | Y Phase Current | Y Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 2400 |  |  | Line Current Phase Y : 0 / 2400 | [9 empty] | +-48,0 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 1 |  | YES | Yphase
A9 | N | PWR | BPS-CL | 33KVBSMV | B Phase Current | B Phase Current | B Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 2400 |  |  | Line Current Phase B : 0 / 2400 | [9 empty] | +-48,0 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 2 |  | YES | Bphase
A9 | N | PWR | BPS-CL | 33KVBSMV | Neutral Current In | Neutral Current In | Neutral Current (In) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 2400 |  |  | Neutral Current In : 0 / 2400 | [9 empty] | +-48,0 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 3 |  | YES | NeuCurr
A9 | N | PWR | BPS-CL | 33KVBSMV | RY Phase Voltage | RY Phase Voltage | RY Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 39.6 |  |  | Line Voltage RY : 0 / 39,60 | [9 empty] | +-0,79kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 4 |  | YES | RyPhase
A9 | N | PWR | BPS-CL | 33KVBSMV | YB Phase Voltage | YB Phase Voltage | YB Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 39.6 |  |  | Line Voltage YB : 0 / 39,60 | [9 empty] | +-0,79kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 5 |  | YES | YbPhase
A9 | N | PWR | BPS-CL | 33KVBSMV | BR Phase Voltage | BR Phase Voltage | BR Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 39.6 |  |  | Line Voltage BR : 0 / 39,60 | [9 empty] | +-0,79kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 6 |  | YES | BrPhase
A9 | N | PWR | BPS-CL | 33KVBSMV | Zero Sequence Voltage (V0) | Zero Sequence Voltage (V0) | Zero Sequence Voltage (V0) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 22,86 |  |  | Zero Sequence Voltage : 0 / 22,86 | [9 empty] | +-0,46kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 7 |  | YES | ZeroVolt
A9 | N | PWR | BPS-CL | 33KVBSMV | Active Power | Active Power | [MW] : Active Power | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MW | -137.18 | 137.18 |  |  | Active Power : -137,18/137,18 | [9 empty] | +-2,74MW | 0 | Power = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 8 |  | YES | ActivePower
A9 | N | PWR | BPS-CL | 33KVBSMV | Reactive Power | Reactive Power | [MVAR] : Reactive Power | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MVAR | -137.18 | 137.18 |  |  | Reactive Power : -137,18/137,18 | [9 empty] | +-2,74MVAR | 0 | Power = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 9 |  | YES | ReacPower
A9 | N | PWR | BPS-CL | 33KVBSMV | Apparent Power | Apparent Power | Apparent Power (S) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MVA | -137.18 | 137.18 |  |  | Apparent Power : -137,18/137,18 | [9 empty] | +-2,74MVA | 0 | Power = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 10 |  | YES | AppPower
A9 | N | PWR | BPS-CL | 33KVBSMV | Power Factor | Power Factor | Power Factor (P.F) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [17 empty] | -1 | 1 |  |  | Power Factor : -1 / 1 | [9 empty] | +-0,02 | 0 | PowerFactor = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 11 |  | YES | PowerFactor
A9 | N | PWR | BPS-CL | 33KVBSMV | Frequency | Frequency | Frequency (Hz) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | Hz | 0 | 60 |  |  | Frequency : 0 / 60 | [9 empty] | +-0,12Hz | 0 | Frequency = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 12 |  | YES | Frequency
A9 | Y |  |  |  |  | 33KV Outgoing Feeder Bay Measurement Value
A9 | N | PWR | BPS-CL | 33KVOFMV | R Phase Current | R Phase Current | R Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 480,00 |  |  | Line Current Phase R : 0 / 480 | [9 empty] | +-9,6 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 0 |  | YES | Rphase
A9 | N | PWR | BPS-CL | 33KVOFMV | Y Phase Current | Y Phase Current | Y Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 480,00 |  |  | Line Current Phase Y : 0 / 480 | [9 empty] | +-9,6 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 1 |  | YES | Yphase
A9 | N | PWR | BPS-CL | 33KVOFMV | B Phase Current | B Phase Current | B Phase Current | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 480,00 |  |  | Line Current Phase B : 0 / 480 | [9 empty] | +-9,6 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 2 |  | YES | Bphase
A9 | N | PWR | BPS-CL | 33KVOFMV | Neutral Current In | Neutral Current In | Neutral Current (In) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | A | 0 | 480,00 |  |  | Neutral Current In : 0 / 480 | [9 empty] | +-9,6 A | 0 | Current = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 3 |  | YES | NeuCurr
A9 | N | PWR | BPS-CL | 33KVOFMV | RY Phase Voltage | RY Phase Voltage | RY Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 39.6 |  |  | Line Voltage RY : 0 / 39,60 | [9 empty] | +-0,79kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 4 |  | YES | RyPhase
A9 | N | PWR | BPS-CL | 33KVOFMV | YB Phase Voltage | YB Phase Voltage | YB Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 39.6 |  |  | Line Voltage YB : 0 / 39,60 | [9 empty] | +-0,79kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 5 |  | YES | YbPhase
A9 | N | PWR | BPS-CL | 33KVOFMV | BR Phase Voltage | BR Phase Voltage | BR Phase Voltage | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 39.6 |  |  | Line Voltage BR : 0 / 39,60 | [9 empty] | +-0,79kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 6 |  | YES | BrPhase
A9 | N | PWR | BPS-CL | 33KVOFMV | Zero Sequence Voltage (V0) | Zero Sequence Voltage (V0) | Zero Sequence Voltage (V0) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | kV | 0 | 7,62 |  |  | Zero Sequence Voltage : 0 / 7,62 | [9 empty] | +-0,15kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 7 |  | YES | ZeroVolt
A9 | N | PWR | BPS-CL | 33KVOFMV | Active Power | Active Power | [MW] : Active Power | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MW | -27.44 | 27.44 |  |  | Active Power : -27,44/27,44 | [9 empty] | +-0,55MW | 0 | Power = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 8 |  | YES | ActivePower
A9 | N | PWR | BPS-CL | 33KVOFMV | Reactive Power | Reactive Power | [MVAR] : Reactive Power | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MVAR | -27.44 | 27.44 |  |  | Reactive Power : -27,44/27,44 | [9 empty] | +-0,55MVAR | 0 | Power = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 9 |  | YES | ReacPower
A9 | N | PWR | BPS-CL | 33KVOFMV | Apparent Power | Apparent Power | Apparent Power (S) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | MVA | -27.44 | 27.44 |  |  | Apparent Power : -27,44/27,44 | [9 empty] | +-0,55MVA | 0 | Power = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 10 |  | YES | AppPower
A9 | N | PWR | BPS-CL | 33KVOFMV | Power Factor | Power Factor | Power Factor (P.F) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [17 empty] | -1 | 1 |  |  | Power Factor : -1 / 1 | [9 empty] | +-0,02 | 0 | PowerFactor = RawValue/100; Raw Value is Signed Int16 | [10 empty] | 16 | 11 |  | YES | PowerFactor
A9 | N | PWR | BPS-CL | 33KVOFMV | Frequency | Frequency | Frequency (Hz) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | Hz | 0 | 60 |  |  | Frequency : 0 / 60 | [9 empty] | +-0,12Hz | 0 | Frequency = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 12 |  | YES | Frequency
A9 | Y |  |  |  |  | Voltage Measurement 33KV
A9 | N | PWR | BPS-CL | 33KVVM | Voltage Measurement | Voltage Measurement | Voltage Measurement | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | KV | 0 | 33 |  |  | Voltage Measurement : 0 / 33 | [9 empty] | +-1kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 0 |  | YES | VoltageMesure
A9 | Y |  |  |  |  | Voltage Measurement 66KV
A9 | N | PWR | BPS-CL | 66KVVM | Voltage Measurement | Voltage Measurement | Voltage Measurement | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | KV | 0 | 66 |  |  | Voltage Measurement : 0 / 66 | [9 empty] | +-1kV | 0 | Voltage = RawValue/100; Raw Value is Unsigned Int16 | [10 empty] | 16 | 0 |  | YES | VoltageMesure
A7 | Y |  |  |  |  | Voltage Transformer Isolator
B | N | PWR | BPS-CL | VTIS | Isolator Position | Isolator Position | VT Isolator Position | Technical alarm |  | DI2 | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_DP_NA_1 | IEC104:MEMBLOCK01 | NA | OPEN | CLOSE | NA | CLOSE | 0: Maj, 1: None, 2: None, 3: Maj | VT Isolator Position : NA/OPEN/CLOSE/NA | [37 empty] | 2 | 0 |  | YES | IsoPosition
A6 | Y |  |  |  |  | Watchdog
A9 | N | PWR | BPS-CL | WTDG | Watchdog Counter | Watchdog Counter | Watchdog Counter for SIL2 | Operational alarm |  | AI | SIL2_Monitoring | IEC60870-5-104 | IEC104:M_ME_NB_1 | IEC104:MEMBLOCK01 | [16 empty] | Count | 0 | 65535 |  |  | Critical | Watchdog Counter Failure | [8 empty] | 1 | 0 | UINT | [10 empty] | 16 | 1 |  | YES | WdCounter
B | Y |  |  |  |  | Auxilary Transformer
B | N | PWR | BPS-CL | AUXTF | 1000kVA Auxiliary Transformer Buchholz Alarm | 1000kVA Auxiliary Transformer Buchholz Alarm | [ETBA] : 1000kVA Auxiliary Transformer Buchholz Alarm | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [ETBA] : 1000kVA Auxiliary Transformer Buchholz Alarm : Clear/Appear | [37 empty] | 1 | 0 |  | NO | BuchAlarm
B | N | PWR | BPS-CL | AUXTF | 1000kVA Auxiliary Transformer Buchholz Trip | 1000kVA Auxiliary Transformer Buchholz Trip | [ETBT] : 1000kVA Auxiliary Transformer Buchholz Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Crit | [ETBT] : 1000kVA Auxiliary Transformer Buchholz Trip : Clear/Trip | [37 empty] | 1 | 1 |  | NO | BuchTrip
B | N | PWR | BPS-CL | AUXTF | Oil Level Alarm Min | Oil Level Alarm Min | [OLEA] : Oil Level Alarm Min | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Min | [OLEA] : Oil Level Alarm Min : Clear/Appear | [37 empty] | 1 | 2 |  | NO | OilMin
B | N | PWR | BPS-CL | AUXTF | Oil Level Alarm Max | Oil Level Alarm Max | [OLEA] : Oil Level Alarm Max | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Min | [OLEA] : Oil Level Alarm Max : Clear/Appear | [37 empty] | 1 | 3 |  | NO | OilMax
B | N | PWR | BPS-CL | AUXTF | 1000kVA Auxiliary Transformer Oil Temp Alarm | 1000kVA Auxiliary Transformer Oil Temp Alarm | [OTAL] : 1000kVA Auxiliary Transformer Oil Temperature Alarm | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [OTAL] : 1000kVA Auxiliary Transformer Oil Temperature Alarm : Clear/Appear | [37 empty] | 1 | 4 |  | NO | OilTempAlarm
B | N | PWR | BPS-CL | AUXTF | 1000kVA Auxiliary Transformer PRV Alarm | 1000kVA Auxiliary Transformer PRV Alarm | [ETPA] : 1000kVA Auxiliary Transformer PRV Alarm | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [ETPA] : 1000kVA Auxiliary Transformer PRV Alarm : Clear/Appear | [37 empty] | 1 | 5 |  | NO | PrvAlarm
B | N | PWR | BPS-CL | AUXTF | 1000kVA Auxiliary Transformer Oil Temp Trip | 1000kVA Auxiliary Transformer Oil Temp Trip | [OTTR] : 1000kVA Auxiliary Transformer Oil Temp Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Crit | [OTTR] : 1000kVA Auxiliary Transformer Oil Temp Trip : Clear/Trip | [37 empty] | 1 | 6 |  | NO | OilTempTrip
B | N | PWR | BPS-CL | AUXTF | 1000kVA Auxiliary Transformer PRD Trip | 1000kVA Auxiliary Transformer PRD Trip | [PRVT] : 1000kVA Auxiliary Transformer PRD Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Crit | [PRVT] : 1000kVA Auxiliary Transformer PRD Trip : Clear/Trip | [37 empty] | 1 | 7 |  | NO | PrdTrip
B | N | PWR | BPS-CL | AUXTF | 1000 kVA Auxilary Transformer Winding Temperature Alarm | 1000 kVA Auxilary Transformer Winding Temperature Alarm | [WGTA] : 1000 kVA Auxilary Transformer Winding Temperature Alarm | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WGTA] : 1000 kVA Auxilary Transformer Winding Temperature Alarm : Clear/Appear | [37 empty] | 1 | 8 |  | NO | TempAlarm
B | N | PWR | BPS-CL | AUXTF | 1000 kVA Auxiliary Transformer Winding Temperature Trip | 1000 kVA Auxiliary Transformer Winding Temperature Trip | [WGTT] : 1000 kVA Auxiliary Transformer Winding Temperature Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Crit | [WGTT] : 1000 kVA Auxiliary Transformer Winding Temperature Trip : Clear/Trip | [37 empty] | 1 | 9 |  | NO | TempTrip
B | N | PWR | BPS-CL | AUXTF | CB Spring Charge Fail | CB Spring Charge Fail | [SPCF] : CB Spring Charge Fail | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [SPCF] : CB Spring Charge Fail : Clear/Appear | [37 empty] | 1 | 10 |  | NO | ChargeFail
B | Y |  |  |  |  | Power Transformer
B | N | PWR | BPS-CL | POWTF | Press Relief Device Trip M1/M2 | Press Relief Device Trip M1/M2 | [PRVT] : Press Relief Device Trip M1/M2 | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Min | [PRVT] : Press Relief Device Trip M1/M2 : Clear/Trip | [37 empty] | 1 | 0 |  | NO | Trip
B | N | PWR | BPS-CL | POWTF | Press Relief Device OLTC Trip | Press Relief Device OLTC Trip | [PREL] : Press Relief Device OLTC Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Min | [PREL] : Press Relief Device OLTC Trip : Clear/Trip | [37 empty] | 1 | 1 |  | NO | OltcTrip
B | N | PWR | BPS-CL | POWTF | Press Relief Device Trip HV Cable Box | Press Relief Device Trip HV Cable Box | [PREL] : Press Relief Device Trip HV Cable Box | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Min | [PREL] : Press Relief Device Trip HV Cable Box : Clear/Trip | [37 empty] | 1 | 2 |  | NO | HvCableBox
B | N | PWR | BPS-CL | POWTF | Winding Temp HV Alarm | Winding Temp HV Alarm | [WGTA] : Winding Temp HV Alarm | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [WGTA] : Winding Temp HV Alarm : Clear/Appear | [37 empty] | 1 | 3 |  | NO | TempHvAlarm
B | N | PWR | BPS-CL | POWTF | Winding Temp LV Alarm | Winding Temp LV Alarm | [WGTA] : Winding Temp LV Alarm | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Crit | [WGTA] : Winding Temp LV Alarm : Clear/Appear | [37 empty] | 1 | 4 |  | NO | TempLvAlarm
B | N | PWR | BPS-CL | POWTF | Oil Temperature Trip | Oil Temperature Trip | [OITT] : Oil Temperature Trip | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Min | [OITT] : Oil Temperature Trip : Clear/Trip | [37 empty] | 1 | 5 |  | NO | TempTrip
B | N | PWR | BPS-CL | POWTF | Buchholz Relay Trip - Main Tank | Buchholz Relay Trip - Main Tank | [MTBT] : Buchholz Relay Trip - Main Tank | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Maj | [MTBT] : Buchholz Relay Trip - Main Tank : Clear/Trip | [37 empty] | 1 | 6 |  | NO | MainTank
B | N | PWR | BPS-CL | POWTF | Buchholz Relay Trip - Diverter Sw | Buchholz Relay Trip - Diverter Sw | [MTBT] : Buchholz Relay Trip - Diverter Sw | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Crit | [MTBT] : Buchholz Relay Trip - Diverter Sw : Clear/Trip | [37 empty] | 1 | 7 |  | NO | Diverter
B | N | PWR | BPS-CL | POWTF | Buchholz Relay Trip - CBL Box HV | Buchholz Relay Trip - CBL Box HV | [BUTH] : Buchholz Relay Trip - CBL Box HV | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Trip |  |  | Clear | 0: None, 1: Crit | [BUTH] : Buchholz Relay Trip - CBL Box HV : Clear/Trip | [37 empty] | 1 | 8 |  | NO | CblBox
B | N | PWR | BPS-CL | POWTF | AVR Relay Fail | AVR Relay Fail | [IRFA] : AVR Relay Fail | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [IRFA] : AVR Relay Fail : Clear/Appear | [37 empty] | 1 | 9 |  | NO | Fail
B | N | PWR | BPS-CL | POWTF | AVR DC Supply MCB Fail | AVR DC Supply MCB Fail | [DCAB] : AVR DC Supply MCB Fail | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [DCAB] : AVR DC Supply MCB Fail : Clear/Appear | [37 empty] | 1 | 10 |  | NO | McbFail
B | N | PWR | BPS-CL | POWTF | Tap Changer High Limit | Tap Changer High Limit | [TCER] : Tap Changer High Limit | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [TCER] : Tap Changer High Limit : Clear/Appear | [37 empty] | 1 | 11 |  | NO | TapHigh
B | N | PWR | BPS-CL | POWTF | Tap Changer Low Limit | Tap Changer Low Limit | [TCER] : Tap Changer Low Limit | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [TCER] : Tap Changer Low Limit : Clear/Appear | [37 empty] | 1 | 12 |  | NO | TapLow
B | N | PWR | BPS-CL | POWTF | Tap Changer Out of Step | Tap | [TCOS] : Tap Changer Out of Step | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [TCOS] : Tap Changer Out of Step : Clear/Appear | [37 empty] | 1 | 13 |  | NO | TapOutStep
B | N | PWR | BPS-CL | POWTF | Tap Changer Incomplete | Tap Changer Incomplete | [TCIN] : Tap Changer Incomplete | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | Clear | Appear |  |  | Clear | 0: None, 1: Maj | [TCIN] : Tap Changer Incomplete : Clear/Appear | [37 empty] | 1 | 14 |  | NO | Incomplete
B | N | PWR | BPS-CL | POWTF | AVR Block Release Status | AVR Block Release Status | [B/R] : AVR Block Release Status | Technical alarm |  | DI2 | SIL0 | IEC60870-5-104 | IEC104:M_DP_NA_1 | IEC104:MEMBLOCK01 | NA | Blocked | Released | NA | Blocked | 0: Maj, 1: None, 2: None, 3: Maj | [B/R] : AVR Block Release Status : NA/Blocked/Released/NA | [37 empty] | 2 | 15 |  | NO | ReleaseSts
B | N | PWR | BPS-CL | POWTF | Wdg Temp Indicator (HV) | Wdg Temp Indicator (HV) | [WTEM]: Wdg Temp Indicator (HV) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | °C | 0 | 160 |  |  | Wdg Temp Indication (HV) : 0 / 160 | [9 empty] | +-1°C | 0 | Temperature = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 2 |  | YES | WdgHv
B | N | PWR | BPS-CL | POWTF | Wdg Temp Indicator (LV) | Wdg Temp Indicator (LV) | [WTEM]: Wdg Temp Indicator (LV) | Meter | daily | AI | SIL0 | IEC60870-5-104 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [16 empty] | °C | 0 | 160 |  |  | Wdg Temp Indication (LV) : 0 / 160 | [9 empty] | +-1°C | 0 | Temperature = RawValue/10; Raw Value is Unsigned Int16 | [10 empty] | 16 | 3 |  | YES | WdgLv
B | N | PWR | BPS-CL | POWTF | AVR Block/Release Command | AVR Block/Release Command | [B/R] : AVR BLK/REL Cmd | Command |  | DO2 | SIL0 | IEC60870-5-104 | IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | NA | Block | Release | NA | NA | 5 | NA | NA | NA | [28 empty] | 2 | 1 |  | NO | CmdBlock
B | N | PWR | BPS-CL | POWTF | AVR Auto/Manual Command | AVR Auto/Manual Command | [A/M] : AVR Auto/Man Cmd | Command |  | DO2 | SIL0 | IEC60870-5-104 | IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | NA | Auto | Manual | NA | NA | 5 | NA | NA | NA | [28 empty] | 2 | 2 |  | NO | CmdAuto
B | N | PWR | BPS-CL | POWTF | TAP Raise/Lower Command | TAP Raise/Lower Command | [TCSN] : TAP RA/LO | Command |  | DO2 | SIL0 | IEC60870-5-104 | IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | NA | Raise | Lower | NA | NA | 5 | NA | NA | NA | [28 empty] | 2 | 3 |  | NO | CmdRaise
A9.1 | Y |  |  |  |  | Bay Control Authority
A9.1 | N | PWR | BPS-CL | BCA | Bay Control Status | DGCC Control | [CBLC] : DGCC Control | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | LOCAL | REMOTE |  |  | REMOTE | 0: Maj, 1: None | [CBLC] : DGCC Control : LOCAL/REMOTE | [37 empty] | 1 | 1 |  | NO | ControlSts
A9.1 | N | PWR | BPS-CL | BCA | BCU Card Status | BCU Card Fail | [WDOG] : Card Fail | Technical alarm |  | DI | SIL0 | IEC60870-5-104 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | OK | FAIL |  |  | OK | 0: None, 1: Crit | [WDOG] : Card Fail : OK/FAIL | [37 empty] | 1 | 2 |  | NO | CardSts

## 2-Instance List
|  | LRT/QRC DESIGNATION |  |  |  | EQUIPMENT INSTANCES | [9 empty] | PRTU Configuration
Revision | isAComment | [Lusail] GBS Code | [Lusail] LBS Code LRT Designation Code | [Lusail] LBS Code QRC Designation Code | Description | Location | Sublocation | Class name | Equipment name | RTU Name | PLC Name | InvalidVar1 | InvalidVar2 | InvalidVar3 | Avalanche condition | Instance Id | External System Name | Device Unit Id | FEP Name | FEP instance Id | Short name | Unique ID code | SCADA Transfert function (Internal THALES) | Address | Description (Native language) | ToBeInstantiated
| Y |  |  |  |  | Hierarchy and locations (everything but equipments) | [15 empty] | Hierarchy and locations (everything but equipments)__
| Y |  |  |  | root node |  |  | Hierarchy | PWR | - | [10 empty] | &PWR | __PWR
| Y |  |  |  | Bulk Power Substation | PWR | BPS-CL | FunctionalCat | BPS-CL | - | [10 empty] | &BPS-CL | PWR_BPS-CL_BPS-CL
| Y |  |  |  | IEC interface | PWR |  | Protocol | IEC | - | [10 empty] | &IEC | PWR__IEC
| Y |  |  |  |  | RTU NAME | [15 empty] | RTU NAME__
| Y |  |  |  |  | PWR:BPS:CL | BPS01_RTU | RTU | Daccom | BPS01_RTU | [10 empty] | &Daccom | PWR_BPS_CL_BPS01_RTU_Daccom
| Y |  |  |  |  | CLASS NAME | [15 empty] | CLASS NAME__
| Y |  |  |  |  | PWR:BPS:CL | BPS01 |  |  | BPS01_RTU | [11 empty] | PWR_BPS_CL_BPS01_
| Y |  |  |  |  | PLC NAME | [15 empty] | PLC NAME__
A7 | N |  |  |  | Gateway | PWR:BPS:CL | BPS01 | GTW | GTW1 | BPS01_RTU | [5 empty] | 1 | BPS_CL |  |  |  | &GTW1 | PWR_BPS_CL_BPS01_GTW1 |  |  |  | Y
A7 | N |  |  |  | Gateway | PWR:BPS:CL | BPS01 | GTW | GTW2 | BPS01_RTU | [5 empty] | 2 | BPS_CL |  |  |  | &GTW2 | PWR_BPS_CL_BPS01_GTW2 |  |  |  | Y
| Y |  |  |  |  | BAY TYPE : COMMON | [15 empty] | BAY TYPE _ COMMON__
| Y |  |  |  |  | WTDG | [15 empty] | WTDG__
A7 | N |  |  |  | Watchdog Gateway n°1 | PWR:BPS:CL |  | WTDG | WTDG_GTW1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 3 | BPS_CL |  |  |  | &WTDG-GTW1 | PWR_BPS_CL__WTDG_GTW1 |  |  |  | Y
A7 | N |  |  |  | Watchdog Gateway n°2 | PWR:BPS:CL |  | WTDG | WTDG_GTW2 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 4 | BPS_CL |  |  |  | &WTDG-GTW2 | PWR_BPS_CL__WTDG_GTW2 |  |  |  | Y
| Y |  |  |  |  | BB_66KV BusBar | [15 empty] | BB_66KV BusBar__
| Y |  |  |  |  | BB_66kV BusBar alarm | [15 empty] | BB_66kV BusBar alarm__
B | N |  |  |  | LRT 66KV Switchgear Busbar Bay Alarms: 66KVBB | PWR:BPS:CL | 66KVBB | BBAL | BBAL_66KV | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 5 | BPS_CL |  |  |  | &BBAL-66KV | PWR_BPS_CL_66KVBB_BBAL_66KV |  |  |  | Y
| Y |  |  |  |  | Main Busbar Operationel Status | [15 empty] | Main Busbar Operationel Status__
B | N |  |  |  | LRT 66kV Busbar Protection Zone | PWR:BPS:CL | 66KVBB | BBPZ | BBPZ_66KV | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 6 | BPS_CL |  |  |  | &BBPZ-66KV | PWR_BPS_CL_66KVBB_BBPZ_66KV |  |  |  | Y
| Y |  |  |  |  | Busbar Protection | [15 empty] | Busbar Protection__
B | N |  |  |  | LRT 66kV Busbar Protection Zone: B10 | PWR:BPS:CL | 66KVBB | BBPR | BBPR_B10 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 7 | BPS_CL |  |  |  | &BBPR-B10 | PWR_BPS_CL_66KVBB_BBPR_B10 |  |  |  | Y
B | N |  |  |  | LRT 66kV Busbar Protection Zone: B20 | PWR:BPS:CL | 66KVBB | BBPR | BBPR_B20 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 8 | BPS_CL |  |  |  | &BBPR-B20 | PWR_BPS_CL_66KVBB_BBPR_B20 |  |  |  | Y
B | N |  |  |  | LRT 66kV Busbar Protection Zone: B11 | PWR:BPS:CL | 66KVBB | BBPR | BBPR_B11 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 9 | BPS_CL |  |  |  | &BBPR-B11 | PWR_BPS_CL_66KVBB_BBPR_B11 |  |  |  | Y
B | N |  |  |  | LRT 66kV Busbar Protection Zone: B21 | PWR:BPS:CL | 66KVBB | BBPR | BBPR_B21 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 10 | BPS_CL |  |  |  | &BBPR-B21 | PWR_BPS_CL_66KVBB_BBPR_B21 |  |  |  | Y
| Y |  |  |  |  | Busbar Protection: Bus Section | [15 empty] | Busbar Protection_ Bus Section__
B | N |  |  |  | LRT 66kV Busbar Protection Zone: B12 | PWR:BPS:CL | 66KVBB | BSCP | BSCP_B12 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 11 | BPS_CL |  |  |  | &BSCP-B12 | PWR_BPS_CL_66KVBB_BSCP_B12 |  |  |  | Y
| Y |  |  |  |  | Voltage Measurement | [15 empty] | Voltage Measurement__
A9 | N |  |  |  | LRT 66KV Busbar M1 Voltage Measurement | PWR:BPS:CL | 66KVBB | 66KVVM | VM_B166VT | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 12 | BPS_CL |  |  |  | &VM-B166VT | PWR_BPS_CL_66KVBB_VM_B166VT |  |  |  | Y
A9 | N |  |  |  | LRT 66KV Busbar M2 Voltage Measurement | PWR:BPS:CL | 66KVBB | 66KVVM | VM_B266VT | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 13 | BPS_CL |  |  |  | &VM-B266VT | PWR_BPS_CL_66KVBB_VM_B266VT |  |  |  | Y
| Y |  |  |  |  | Bay Type 66KV Incoming Feeder Bay | [15 empty] | Bay Type 66KV Incoming Feeder Bay__
| Y |  |  |  |  | 66KV Incoming Feeder Bay Alarms | [15 empty] | 66KV Incoming Feeder Bay Alarms__
B | N |  |  |  | LRT 66KV Incomer B10 | PWR:BPS:CL | B10 | 66KVIFBA | 66KVIFBA_B10 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 14 | BPS_CL |  |  |  | &66KVIFBA-B10 | PWR_BPS_CL_B10_66KVIFBA_B10 |  |  |  | Y
B | N |  |  |  | LRT 66KV Incomer B20 | PWR:BPS:CL | B20 | 66KVIFBA | 66KVIFBA_B20 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 15 | BPS_CL |  |  |  | &66KVIFBA-B20 | PWR_BPS_CL_B20_66KVIFBA_B20 |  |  |  | Y
| Y |  |  |  |  | Measurement Value | [15 empty] | Measurement Value__
A9 | N |  |  |  | LRT 66KV Measurement Value B10 | PWR:BPS:CL | B10 | 66KVIFMV | 66KVIFMV_B10 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 16 | BPS_CL |  |  |  | &66KVIFMV-B10 | PWR_BPS_CL_B10_66KVIFMV_B10 |  |  |  | Y
A9 | N |  |  |  | LRT 66KV Measurement Value B20 | PWR:BPS:CL | B20 | 66KVIFMV | 66KVIFMV_B20 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 17 | BPS_CL |  |  |  | &66KVIFMV-B20 | PWR_BPS_CL_B20_66KVIFMV_B20 |  |  |  | Y
| Y |  |  |  |  | Voltage Transformer Isolator | [15 empty] | Voltage Transformer Isolator__
A7.1 | N |  |  |  | LRT 66KV VT Isolator B1064 | PWR:BPS:CL | B10 | VTIS | B1064 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 18 | BPS_CL |  |  |  | &B1064 | PWR_BPS_CL_B10_B1064 |  |  |  | Y
A7.1 | N |  |  |  | LRT 66KV VT Isolator B2064 | PWR:BPS:CL | B20 | VTIS | B2064 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 19 | BPS_CL |  |  |  | &B2064 | PWR_BPS_CL_B20_B2064 |  |  |  | Y
| Y |  |  |  |  | SF6 Circuit Breaker | [15 empty] | SF6 Circuit Breaker__
A9 | N |  |  |  | LRT 66KV SF6 Circuit Breaker B100 | PWR:BPS:CL | B10 | CB_OST | B100 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 20 | BPS_CL |  |  |  | &B100 | PWR_BPS_CL_B10_B100 |  |  |  | Y
A9 | N |  |  |  | LRT 66KV SF6 Circuit Breaker B200 | PWR:BPS:CL | B20 | CB_OST | B200 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 21 | BPS_CL |  |  |  | &B200 | PWR_BPS_CL_B20_B200 |  |  |  | Y
| Y |  |  |  |  | Earth Switch | [15 empty] | Earth Switch__
B | N |  |  |  | LRT 66KV Earth Switch B101 | PWR:BPS:CL | B10 | ESSM | B101 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 22 | BPS_CL |  |  |  | &B101 | PWR_BPS_CL_B10_B101 |  |  |  | Y
B | N |  |  |  | LRT 66KV Earth Switch B201 | PWR:BPS:CL | B20 | ESSM | B201 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 23 | BPS_CL |  |  |  | &B201 | PWR_BPS_CL_B20_B201 |  |  |  | Y
| Y |  |  |  |  | Bus Isolator | [15 empty] | Bus Isolator__
B | N |  |  |  | LRT 66KV Line Isolator B103 | PWR:BPS:CL | B10 | BIST | BIST_B103 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 24 | BPS_CL |  |  |  | &BIST-B103 | PWR_BPS_CL_B10_BIST_B103 |  |  |  | Y
B | N |  |  |  | LRT 66KV Line Isolator B203 | PWR:BPS:CL | B20 | BIST | BIST_B203 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 25 | BPS_CL |  |  |  | &BIST-B203 | PWR_BPS_CL_B20_BIST_B203 |  |  |  | Y
B | N |  |  |  | LRT 66KV Main Busbar Isolator B104 | PWR:BPS:CL | B10 | BIST | BIST_B104 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 26 | BPS_CL |  |  |  | &BIST-B104 | PWR_BPS_CL_B10_BIST_B104 |  |  |  | Y
B | N |  |  |  | LRT 66KV Main Busbar Isolator B204 | PWR:BPS:CL | B20 | BIST | BIST_B204 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 27 | BPS_CL |  |  |  | &BIST-B204 | PWR_BPS_CL_B20_BIST_B204 |  |  |  | Y
| Y |  |  |  |  | Maintenance Earth Switch | [15 empty] | Maintenance Earth Switch__
B | N |  |  |  | LRT 66KV Maintenance Earth Switch B10M2 | PWR:BPS:CL | B10 | ESSM | B10M2 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 28 | BPS_CL |  |  |  | &B10M2 | PWR_BPS_CL_B10_B10M2 |  |  |  | Y
B | N |  |  |  | LRT 66KV Maintenance Earth Switch B20M2 | PWR:BPS:CL | B20 | ESSM | B20M2 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 29 | BPS_CL |  |  |  | &B20M2 | PWR_BPS_CL_B20_B20M2 |  |  |  | Y
B | N |  |  |  | LRT 66KV Maintenance Earth Switch B10M1 | PWR:BPS:CL | B10 | ESSM | B10M1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 30 | BPS_CL |  |  |  | &B10M1 | PWR_BPS_CL_B10_B10M1 |  |  |  | Y
B | N |  |  |  | LRT 66KV Maintenance Earth Switch B20M1 | PWR:BPS:CL | B20 | ESSM | B20M1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 31 | BPS_CL |  |  |  | &B20M1 | PWR_BPS_CL_B20_B20M1 |  |  |  | Y
| Y |  |  |  |  | Circuit Breaker Protection | [15 empty] | Circuit Breaker Protection__
B | N |  |  |  | LRT 66KV Incoming Feeder Circuit Breaker Protection Main-1 | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 32 | BPS_CL |  |  |  | &66KVIFPR-B10-Main1 | PWR_BPS_CL_B10_66KVIFPR_B10_Main1 |  |  |  | Y
B | N |  |  |  | LRT 66KV Incoming Feeder Circuit Breaker Protection Main-2 | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main2 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 33 | BPS_CL |  |  |  | &66KVIFPR-B10-Main2 | PWR_BPS_CL_B10_66KVIFPR_B10_Main2 |  |  |  | Y
B | N |  |  |  | LRT 66KV Incoming Feeder Circuit Breaker Protection Main-1 | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 34 | BPS_CL |  |  |  | &66KVIFPR-B20-Main1 | PWR_BPS_CL_B20_66KVIFPR_B20_Main1 |  |  |  | Y
B | N |  |  |  | LRT 66KV Incoming Feeder Circuit Breaker Protection Main-2 | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main2 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 35 | BPS_CL |  |  |  | &66KVIFPR-B20-Main2 | PWR_BPS_CL_B20_66KVIFPR_B20_Main2 |  |  |  | Y
| Y |  |  |  |  | Bay Type 66KV Busection | [15 empty] | Bay Type 66KV Busection__
| Y |  |  |  |  | 66KV Busection Bay Alarms | [15 empty] | 66KV Busection Bay Alarms__
A9 | N |  |  |  | LRT 66KV Bus Section B12 | PWR:BPS:CL | B12 | 66KVBSBA | 66KVBSBA_B12 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 36 | BPS_CL |  |  |  | &66KVBSBA-B12 | PWR_BPS_CL_B12_66KVBSBA_B12 |  |  |  | Y
| Y |  |  |  |  | SF6 Circuit Breaker | [15 empty] | SF6 Circuit Breaker__
A9 | N |  |  |  | LRT 66KV SF6 Circuit breaker B120 | PWR:BPS:CL | B12 | CB_OST | B120 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 37 | BPS_CL |  |  |  | &B120 | PWR_BPS_CL_B12_B120 |  |  |  | Y
| Y |  |  |  |  | Circuit Breaker Protection | [15 empty] | Circuit Breaker Protection__
B | N |  |  |  | LRT 66KV Bus Section Bay Circuit Breaker Prot B120 | PWR:BPS:CL | B12 | 66KVBSPR | 66KVBSPR_B120 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 38 | BPS_CL |  |  |  | &66KVBSPR-B120 | PWR_BPS_CL_B12_66KVBSPR_B120 |  |  |  | Y
| Y |  |  |  |  | Bus Isolator | [15 empty] | Bus Isolator__
B | N |  |  |  | LRT 66KV Busbar isolator B124 | PWR:BPS:CL | B12 | BIST | BIST_B124 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 39 | BPS_CL |  |  |  | &BIST-B124 | PWR_BPS_CL_B12_BIST_B124 |  |  |  | Y
B | N |  |  |  | LRT 66KV Busbar isolator B126 | PWR:BPS:CL | B12 | BIST | BIST_B126 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 40 | BPS_CL |  |  |  | &BIST-B126 | PWR_BPS_CL_B12_BIST_B126 |  |  |  | Y
B | N |  |  |  | LRT 66KV Busbar Isolator B164 | PWR:BPS:CL | B12 | BIST | BIST_B164 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 41 | BPS_CL |  |  |  | &BIST-B164 | PWR_BPS_CL_B12_BIST_B164 |  |  |  | Y
B | N |  |  |  | LRT 66KV Busbar Isolator B264 | PWR:BPS:CL | B12 | BIST | BIST_B264 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 42 | BPS_CL |  |  |  | &BIST-B264 | PWR_BPS_CL_B12_BIST_B264 |  |  |  | Y
| Y |  |  |  |  | Earth Switch | [15 empty] | Earth Switch__
B | N |  |  |  | LRT 66KV Earth Switch B1241 | PWR:BPS:CL | B12 | ESSM | B1241 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 43 | BPS_CL |  |  |  | &B1241 | PWR_BPS_CL_B12_B1241 |  |  |  | Y
B | N |  |  |  | LRT 66KV Earth Switch B1261 | PWR:BPS:CL | B12 | ESSM | B1261 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 44 | BPS_CL |  |  |  | &B1261 | PWR_BPS_CL_B12_B1261 |  |  |  | Y
| Y |  |  |  |  | Maintenance Earth Switch | [15 empty] | Maintenance Earth Switch__
B | N |  |  |  | LRT 66KV Maintenance earth switch B12M1 | PWR:BPS:CL | B12 | ESSM | B12M1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 45 | BPS_CL |  |  |  | &B12M1 | PWR_BPS_CL_B12_B12M1 |  |  |  | Y
B | N |  |  |  | LRT 66KV Maintenance earth switch B12M2 | PWR:BPS:CL | B12 | ESSM | B12M2 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 46 | BPS_CL |  |  |  | &B12M2 | PWR_BPS_CL_B12_B12M2 |  |  |  | Y
B | N |  |  |  | LRT 66KV Maintenance Earth Switch B16M1 | PWR:BPS:CL | B12 | ESSM | B16M1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 47 | BPS_CL |  |  |  | &B16M1 | PWR_BPS_CL_B12_B16M1 |  |  |  | Y
B | N |  |  |  | LRT 66KV Maintenance Earth Switch B26M1 | PWR:BPS:CL | B12 | ESSM | B26M1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 48 | BPS_CL |  |  |  | &B26M1 | PWR_BPS_CL_B12_B26M1 |  |  |  | Y
| Y |  |  |  |  | Measurement Value | [15 empty] | Measurement Value__
A9 | N |  |  |  | LRT 66KV Bus Section Measurement Value B12 | PWR:BPS:CL | B12 | 66KVBSMV | 66KVBSMV_B12 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 49 | BPS_CL |  |  |  | &66KVBSMV-B12 | PWR_BPS_CL_B12_66KVBSMV_B12 |  |  |  | Y
| Y |  |  |  |  | Bay Type 66/33KV IBT HV Outgoing Feeder Bay | [15 empty] | Bay Type 66/33KV IBT HV Outgoing Feeder Bay__
| Y |  |  |  |  | 66/33KV IBT HV Outgoing Feeder Bay alarms | [15 empty] | 66/33KV IBT HV Outgoing Feeder Bay alarms__
B | N |  |  |  | LRT 66KV IBT HV B11 | PWR:BPS:CL | B11 | 66KVHVBA | 66KVHVBA_B11 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 50 | BPS_CL |  |  |  | &66KVHVBA-B11 | PWR_BPS_CL_B11_66KVHVBA_B11 |  |  |  | Y
B | N |  |  |  | LRT 66KV IBT HV B21 | PWR:BPS:CL | B21 | 66KVHVBA | 66KVHVBA_B21 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 51 | BPS_CL |  |  |  | &66KVHVBA-B21 | PWR_BPS_CL_B21_66KVHVBA_B21 |  |  |  | Y
| Y |  |  |  |  | Circuit Breaker Protection | [15 empty] | Circuit Breaker Protection__
B | N |  |  |  | LRT 66KV IBT HV Circuit Breaker Protection B110 | PWR:BPS:CL | B11 | 66KVHVPR | 66KVHVPR_B110 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 52 | BPS_CL |  |  |  | &66KVHVPR-B110 | PWR_BPS_CL_B11_66KVHVPR_B110 |  |  |  | Y
B | N |  |  |  | LRT 66KV IBT HV Circuit Breaker Protection B210 | PWR:BPS:CL | B21 | 66KVHVPR | 66KVHVPR_B210 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 53 | BPS_CL |  |  |  | &66KVHVPR-B210 | PWR_BPS_CL_B21_66KVHVPR_B210 |  |  |  | Y
| Y |  |  |  |  | Bus Isolator | [15 empty] | Bus Isolator__
B | N |  |  |  | LRT 66KV Busbar Isolator B114 | PWR:BPS:CL | B11 | BIST | BIST_B114 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 54 | BPS_CL |  |  |  | &BIST-B114 | PWR_BPS_CL_B11_BIST_B114 |  |  |  | Y
B | N |  |  |  | LRT 66KV Busbar Isolator B214 | PWR:BPS:CL | B21 | BIST | BIST_B214 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 55 | BPS_CL |  |  |  | &BIST-B214 | PWR_BPS_CL_B21_BIST_B214 |  |  |  | Y
| Y |  |  |  |  | Maintenance Earth Switch | [15 empty] | Maintenance Earth Switch__
B | N |  |  |  | LRT 66KV Maintenance Earth Switch B11M1 | PWR:BPS:CL | B11 | ESSM | B11M1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 56 | BPS_CL |  |  |  | &B11M1 | PWR_BPS_CL_B11_B11M1 |  |  |  | Y
B | N |  |  |  | LRT 66KV Maintenance Earth Switch B21M1 | PWR:BPS:CL | B21 | ESSM | B21M1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 57 | BPS_CL |  |  |  | &B21M1 | PWR_BPS_CL_B21_B21M1 |  |  |  | Y
| Y |  |  |  |  | SF6 Circuit Breaker | [15 empty] | SF6 Circuit Breaker__
A9 | N |  |  |  | LRT 66KV SF6 Circuit Breaker B110 | PWR:BPS:CL | B11 | CB_OST | B110 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 58 | BPS_CL |  |  |  | &B110 | PWR_BPS_CL_B11_B110 |  |  |  | Y
A9 | N |  |  |  | LRT 66KV SF6 Circuit Breaker B210 | PWR:BPS:CL | B21 | CB_OST | B210 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 59 | BPS_CL |  |  |  | &B210 | PWR_BPS_CL_B21_B210 |  |  |  | Y
| Y |  |  |  |  | Measurement Value | [15 empty] | Measurement Value__
A9 | N |  |  |  | LRT 66KV IBT HV B11 Measurement Value | PWR:BPS:CL | B11 | 66KVHVMV | 66KVHVMV_B11 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 60 | BPS_CL |  |  |  | &66KVHVMV-B11 | PWR_BPS_CL_B11_66KVHVMV_B11 |  |  |  | Y
A9 | N |  |  |  | LRT 66KV IBT HV B21 Measurement Value | PWR:BPS:CL | B21 | 66KVHVMV | 66KVHVMV_B21 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 61 | BPS_CL |  |  |  | &66KVHVMV-B21 | PWR_BPS_CL_B21_66KVHVMV_B21 |  |  |  | Y
| Y |  |  |  |  | Earth Switch | [15 empty] | Earth Switch__
B | N |  |  |  | LRT 66KV Earth Switch B111 | PWR:BPS:CL | B11 | ESSM | B111 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 62 | BPS_CL |  |  |  | &B111 | PWR_BPS_CL_B11_B111 |  |  |  | Y
B | N |  |  |  | LRT 66KV Earth Switch B211 | PWR:BPS:CL | B21 | ESSM | B211 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 63 | BPS_CL |  |  |  | &B211 | PWR_BPS_CL_B21_B211 |  |  |  | Y
| Y |  |  |  |  | BB_33KV Busbar | [15 empty] | BB_33KV Busbar__
| Y |  |  |  |  | BB_33kV Busbar Alarm | [15 empty] | BB_33kV Busbar Alarm __
B | N |  |  |  | LRT 33KV Switchgear Busbar Bay Alarms: 33KVBB | PWR:BPS:CL | 33KVBB | BBAL | BBAL_33KV | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 66 | BPS_CL |  |  |  | &BBAL-33KV | PWR_BPS_CL_33KVBB_BBAL_33KV |  |  |  | Y
| Y |  |  |  |  | Main Busbar Operational Status | [15 empty] | Main Busbar Operational Status__
B | N |  |  |  | LRT 33KV Busbar Protection Zone | PWR:BPS:CL | 33KVBB | BBPZ | BBPZ_33KV | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 67 | BPS_CL |  |  |  | &BBPZ-33KV | PWR_BPS_CL_33KVBB_BBPZ_33KV |  |  |  | Y
| Y |  |  |  |  | Busbar Protection | [15 empty] | Busbar Protection__
B | N |  |  |  | LRT 66kV Busbar Protection Zone: E18 | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E18 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 68 | BPS_CL |  |  |  | &BBPR-E18 | PWR_BPS_CL_33KVBB_BBPR_E18 |  |  |  | Y
B | N |  |  |  | LRT 66kV Busbar Protection Zone: E28 | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E28 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 69 | BPS_CL |  |  |  | &BBPR-E28 | PWR_BPS_CL_33KVBB_BBPR_E28 |  |  |  | Y
B | N |  |  |  | LRT 66kV Busbar Protection Zone: E10 | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E10 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 70 | BPS_CL |  |  |  | &BBPR-E10 | PWR_BPS_CL_33KVBB_BBPR_E10 |  |  |  | Y
B | N |  |  |  | LRT 66kV Busbar Protection Zone: E20 | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E20 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 71 | BPS_CL |  |  |  | &BBPR-E20 | PWR_BPS_CL_33KVBB_BBPR_E20 |  |  |  | Y
B | N |  |  |  | LRT 66kV Busbar Protection Zone: E30 | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E30 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 72 | BPS_CL |  |  |  | &BBPR-E30 | PWR_BPS_CL_33KVBB_BBPR_E30 |  |  |  | Y
B | N |  |  |  | LRT 66kV Busbar Protection Zone: E40 | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E40 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 73 | BPS_CL |  |  |  | &BBPR-E40 | PWR_BPS_CL_33KVBB_BBPR_E40 |  |  |  | Y
B | N |  |  |  | LRT 66kV Busbar Protection Zone: E50 | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E50 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 74 | BPS_CL |  |  |  | &BBPR-E50 | PWR_BPS_CL_33KVBB_BBPR_E50 |  |  |  | Y
B | N |  |  |  | LRT 66kV Busbar Protection Zone: E60 | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E60 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 75 | BPS_CL |  |  |  | &BBPR-E60 | PWR_BPS_CL_33KVBB_BBPR_E60 |  |  |  | Y
| Y |  |  |  |  | Busbar Protection: Bus Section | [15 empty] | Busbar Protection_ Bus Section__
B | N |  |  |  | LRT 66kV Busbar Protection Zone: E12 | PWR:BPS:CL | 66KVBB | BSCP | BSCP_E12 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 76 | BPS_CL |  |  |  | &BSCP-E12 | PWR_BPS_CL_66KVBB_BSCP_E12 |  |  |  | Y
| Y |  |  |  |  | Voltage Measurement | [15 empty] | Voltage Measurement__
A9 | N |  |  |  | LRT 33KV Busbar M1 Voltage Measurement | PWR:BPS:CL | 33KVBB | 33KVVM | VM_E166VT | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 77 | BPS_CL |  |  |  | &VM-E166VT | PWR_BPS_CL_33KVBB_VM_E166VT |  |  |  | Y
A9 | N |  |  |  | LRT 33KV Busbar M2 Voltage Measurement | PWR:BPS:CL | 33KVBB | 33KVVM | VM_E266VT | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 78 | BPS_CL |  |  |  | &VM-E266VT | PWR_BPS_CL_33KVBB_VM_E266VT |  |  |  | Y
| Y |  |  |  |  | Bay Type 33KV Incoming Feeder | [15 empty] | Bay Type 33KV Incoming Feeder __
| Y |  |  |  |  | 33KV BB Incoming Feeder Bay Alarms | [15 empty] | 33KV BB Incoming Feeder Bay Alarms__
B | N |  |  |  | LRT 33KV Incomer E18 | PWR:BPS:CL | E18 | 33KVIFBA | 33KVIFBA_E18 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 79 | BPS_CL |  |  |  | &33KVIFBA-E18 | PWR_BPS_CL_E18_33KVIFBA_E18 |  |  |  | Y
B | N |  |  |  | LRT 33KV Incomer E28 | PWR:BPS:CL | E28 | 33KVIFBA | 33KVIFBA_E28 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 80 | BPS_CL |  |  |  | &33KVIFBA-E28 | PWR_BPS_CL_E28_33KVIFBA_E28 |  |  |  | Y
| Y |  |  |  |  | Circuit Breaker Protection | [15 empty] | Circuit Breaker Protection__
B | N |  |  |  | LRT 33KV Incoming Feeder Circuit Breaker Protection E180 | PWR:BPS:CL | E18 | 33KVIFPR | 33KVIFPR_E180 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 81 | BPS_CL |  |  |  | &33KVIFPR-E180 | PWR_BPS_CL_E18_33KVIFPR_E180 |  |  |  | Y
B | N |  |  |  | LRT 33KV Incoming Feeder Circuit Breaker Protection E280 | PWR:BPS:CL | E28 | 33KVIFPR | 33KVIFPR_E280 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 82 | BPS_CL |  |  |  | &33KVIFPR-E280 | PWR_BPS_CL_E28_33KVIFPR_E280 |  |  |  | Y
| Y |  |  |  |  | Measurement Value | [15 empty] | Measurement Value__
A9 | N |  |  |  | LRT 33kV Measurement Value E18 | PWR:BPS:CL | E18 | 33KVIFMV | 33KVIFMV_E18 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 83 | BPS_CL |  |  |  | &33KVIFMV-E18 | PWR_BPS_CL_E18_33KVIFMV_E18 |  |  |  | Y
A9 | N |  |  |  | LRT 33KV Measurement Value E28 | PWR:BPS:CL | E28 | 33KVIFMV | 33KVIFMV_E28 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 84 | BPS_CL |  |  |  | &33KVIFMV-E28 | PWR_BPS_CL_E28_33KVIFMV_E28 |  |  |  | Y
| Y |  |  |  |  | Bus Isolator | [15 empty] | Bus Isolator__
B | N |  |  |  | LRT 33kV Busbar Isolator E184 | PWR:BPS:CL | E18 | ISST | ISST_E184 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 85 | BPS_CL |  |  |  | &ISST-E184 | PWR_BPS_CL_E18_ISST_E184 |  |  |  | Y
B | N |  |  |  | LRT 33KV Busbar Isolator E284 | PWR:BPS:CL | E28 | ISST | ISST_E284 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 86 | BPS_CL |  |  |  | &ISST-E284 | PWR_BPS_CL_E28_ISST_E284 |  |  |  | Y
| Y |  |  |  |  | Maintenance Earth Switch | [15 empty] | Maintenance Earth Switch__
B | N |  |  |  | LRT 33kV Earth Switch E18M1 | PWR:BPS:CL | E18 | ESST | E18M1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 87 | BPS_CL |  |  |  | &E18M1 | PWR_BPS_CL_E18_E18M1 |  |  |  | Y
B | N |  |  |  | LRT 33KV Earth Switch E28M1 | PWR:BPS:CL | E28 | ESST | E28M1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 88 | BPS_CL |  |  |  | &E28M1 | PWR_BPS_CL_E28_E28M1 |  |  |  | Y
| Y |  |  |  |  | Vaccum Circuit Breaker | [15 empty] | Vaccum Circuit Breaker__
A7.1 | N |  |  |  | LRT 33kV Vacuum Circuit Breaker E180 | PWR:BPS:CL | E18 | CB | E180 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 89 | BPS_CL |  |  |  | &E180 | PWR_BPS_CL_E18_E180 |  |  |  | Y
A7.1 | N |  |  |  | LRT 66KV Vacuum Circuit Breaker E280 | PWR:BPS:CL | E28 | CB | E280 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 90 | BPS_CL |  |  |  | &E280 | PWR_BPS_CL_E28_E280 |  |  |  | Y
| Y |  |  |  |  | Bay type 33KV/415KV ST.TX Feeder Bay | [15 empty] | Bay type 33KV/415KV ST.TX Feeder Bay __
| Y |  |  |  |  | 33KV/415KV ST.TX Feeder Bay Alarms | [15 empty] | 33KV/415KV ST.TX Feeder Bay Alarms__
B | N |  |  |  | LRT 33KV ST.TX E10 | PWR:BPS:CL | E10 | 33KVSTBA | 33KVSTBA_E10 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 91 | BPS_CL |  |  |  | &33KVSTBA-E10 | PWR_BPS_CL_E10_33KVSTBA_E10 |  |  |  | Y
B | N |  |  |  | LRT 33KV ST.TX E20 | PWR:BPS:CL | E20 | 33KVSTBA | 33KVSTBA_E20 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 92 | BPS_CL |  |  |  | &33KVSTBA-E20 | PWR_BPS_CL_E20_33KVSTBA_E20 |  |  |  | Y
| Y |  |  |  |  | Bus Isolator | [15 empty] | Bus Isolator__
B | N |  |  |  | LRT 33KV Busbar Isolator E164 | PWR:BPS:CL | E10 | ISST | ISST_E164 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 93 | BPS_CL |  |  |  | &ISST-E164 | PWR_BPS_CL_E10_ISST_E164 |  |  |  | Y
B | N |  |  |  | LRT 33KV Busbar Isolator E264 | PWR:BPS:CL | E20 | ISST | ISST_E264 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 94 | BPS_CL |  |  |  | &ISST-E264 | PWR_BPS_CL_E20_ISST_E264 |  |  |  | Y
B | N |  |  |  | LRT 33KV Busbar Isolator E104 | PWR:BPS:CL | E10 | ISST | ISST_E104 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 95 | BPS_CL |  |  |  | &ISST-E104 | PWR_BPS_CL_E10_ISST_E104 |  |  |  | Y
B | N |  |  |  | LRT 33KV Busbar Isolator E204 | PWR:BPS:CL | E20 | ISST | ISST_E204 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 96 | BPS_CL |  |  |  | &ISST-E204 | PWR_BPS_CL_E20_ISST_E204 |  |  |  | Y
| Y |  |  |  |  | Maintenance Earth Switch | [15 empty] | Maintenance Earth Switch__
B | N |  |  |  | LRT 33KV Earth switch E16M1 | PWR:BPS:CL | E10 | ESST | E16M1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 97 | BPS_CL |  |  |  | &E16M1 | PWR_BPS_CL_E10_E16M1 |  |  |  | Y
B | N |  |  |  | LRT 33KV Earth switch E26M1 | PWR:BPS:CL | E20 | ESST | E26M1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 98 | BPS_CL |  |  |  | &E26M1 | PWR_BPS_CL_E20_E26M1 |  |  |  | Y
B | N |  |  |  | LRT 33KV Earth switch E10M1 | PWR:BPS:CL | E10 | ESST | E10M1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 99 | BPS_CL |  |  |  | &E10M1 | PWR_BPS_CL_E10_E10M1 |  |  |  | Y
B | N |  |  |  | LRT 33KV Earth switch E20M1 | PWR:BPS:CL | E20 | ESST | E20M1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 100 | BPS_CL |  |  |  | &E20M1 | PWR_BPS_CL_E20_E20M1 |  |  |  | Y
| Y |  |  |  |  | Vaccum Circuit Breaker | [15 empty] | Vaccum Circuit Breaker__
A9 | N |  |  |  | LRT 33KV Vacuum Circuit Breaker E100 | PWR:BPS:CL | E10 | CB | E100 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 101 | BPS_CL |  |  |  | &E100 | PWR_BPS_CL_E10_E100 |  |  |  | Y
A9 | N |  |  |  | LRT 33KV Vacuum Circuit Breaker E200 | PWR:BPS:CL | E20 | CB | E200 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 102 | BPS_CL |  |  |  | &E200 | PWR_BPS_CL_E20_E200 |  |  |  | Y
| Y |  |  |  |  | Circuit Breaker Protection | [15 empty] | Circuit Breaker Protection__
B | N |  |  |  | LRT 33KV ST.TX Circuit Breaker Protection E100 | PWR:BPS:CL | E10 | 33KVSTPR | 33KVSTPR_E100 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 103 | BPS_CL |  |  |  | &33KVSTPR-E100 | PWR_BPS_CL_E10_33KVSTPR_E100 |  |  |  | Y
B | N |  |  |  | LRT 33KV ST.TX Circuit Breaker Protection E200 | PWR:BPS:CL | E20 | 33KVSTPR | 33KVSTPR_E200 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 104 | BPS_CL |  |  |  | &33KVSTPR-E200 | PWR_BPS_CL_E20_33KVSTPR_E200 |  |  |  | Y
| Y |  |  |  |  | Measurement Value | [15 empty] | Measurement Value__
A9 | N |  |  |  | LRT 33KV measurement value E10 | PWR:BPS:CL | E10 | 33KVSTMV | 33KVSTMV_E10 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 105 | BPS_CL |  |  |  | &33KVSTMV-E10 | PWR_BPS_CL_E10_33KVSTMV_E10 |  |  |  | Y
A9 | N |  |  |  | LRT 33KV measurement value E20 | PWR:BPS:CL | E20 | 33KVSTMV | 33KVSTMV_E20 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 106 | BPS_CL |  |  |  | &33KVSTMV-E20 | PWR_BPS_CL_E20_33KVSTMV_E20 |  |  |  | Y
A9.1 | Y |  |  |  |  | Bay Control Authority | [16 empty] | Bay Control Authority__
A9.1 | N |  |  |  | LRT 33KV Bay Control Authority E10 | PWR:BPS:CL | E10 | BCA | BCA_E10 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 107 | BPS_CL |  |  |  | &BCA-E10 | PWR_BPS_CL_E10_BCA_E10 |  |  |  | Y
A9.1 | N |  |  |  | LRT 33KV Bay Control Authority E20 | PWR:BPS:CL | E20 | BCA | BCA_E20 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 108 | BPS_CL |  |  |  | &BCA-E20 | PWR_BPS_CL_E20_BCA_E20 |  |  |  | Y
| Y |  |  |  |  | Bay Type 33KV Busection Bay | [15 empty] | Bay Type 33KV Busection Bay__
| Y |  |  |  |  | 33KV BB Busection Bay Alarms | [15 empty] | 33KV BB Busection Bay Alarms__
B | N |  |  |  | LRT 33KV Bus Section E12 | PWR:BPS:CL | E12 | 33KVBSBA | 33KVBSBA_E12 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 109 | BPS_CL |  |  |  | &33KVBSBA-E12 | PWR_BPS_CL_E12_33KVBSBA_E12 |  |  |  | Y
| Y |  |  |  |  | Vaccum Circuit Breaker | [15 empty] | Vaccum Circuit Breaker__
A7.1 | N |  |  |  | LRT 33kV Vacuum circuit breaker E120 | PWR:BPS:CL | E12 | CB | E120 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 110 | BPS_CL |  |  |  | &E120 | PWR_BPS_CL_E12_E120 |  |  |  | Y
| Y |  |  |  |  | Circuit Breaker Protection | [15 empty] | Circuit Breaker Protection__
B | N |  |  |  | LRT 33KV Busection Circuit Breaker Protection E120 | PWR:BPS:CL | E12 | 33KVBSPR | 33KVBSPR_E120 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 111 | BPS_CL |  |  |  | &33KVBSPR-E120 | PWR_BPS_CL_E12_33KVBSPR_E120 |  |  |  | Y
| Y |  |  |  |  | Bus Isolator | [15 empty] | Bus Isolator__
B | N |  |  |  | LRT 33kV Busbar Isolator E124 | PWR:BPS:CL | E12 | ISST | ISST_E124 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 112 | BPS_CL |  |  |  | &ISST-E124 | PWR_BPS_CL_E12_ISST_E124 |  |  |  | Y
B | N |  |  |  | LRT 33kV Busbar Isolator E126 | PWR:BPS:CL | E12 | ISST | ISST_E126 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 113 | BPS_CL |  |  |  | &ISST-E126 | PWR_BPS_CL_E12_ISST_E126 |  |  |  | Y
| Y |  |  |  |  | Maintenance Earth Switch | [15 empty] | Maintenance Earth Switch__
B | N |  |  |  | LRT 33kV Earth Switch E12M1 | PWR:BPS:CL | E12 | ESST | E12M1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 114 | BPS_CL |  |  |  | &E12M1 | PWR_BPS_CL_E12_E12M1 |  |  |  | Y
B | N |  |  |  | LRT 33kV Earth Switch E12M2 | PWR:BPS:CL | E12 | ESST | E12M2 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 115 | BPS_CL |  |  |  | &E12M2 | PWR_BPS_CL_E12_E12M2 |  |  |  | Y
| Y |  |  |  |  | Measurement Value | [15 empty] | Measurement Value__
A9 | N |  |  |  | LRT 33kV Measurement Value E12 | PWR:BPS:CL | E12 | 33KVBSMV | 33KVBSMV_E12 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 116 | BPS_CL |  |  |  | &33KVBSMV-E12 | PWR_BPS_CL_E12_33KVBSMV_E12 |  |  |  | Y
A9.1 | Y |  |  |  |  | Bay Control Authority | [16 empty] | Bay Control Authority__
A9.1 | N |  |  |  | LRT 33KV Bay Control Authority E12 | PWR:BPS:CL | E12 | BCA | BCA_E12 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 117 | BPS_CL |  |  |  | &BCA-E12 | PWR_BPS_CL_E12_BCA_E12 |  |  |  | Y
| Y |  |  |  |  | Bay Type 33KV Outgoing Feeder Bay | [15 empty] | Bay Type 33KV Outgoing Feeder Bay__
| Y |  |  |  |  | 33kV Outgoing Feeder Bay Alarms | [15 empty] | 33kV Outgoing Feeder Bay Alarms__
B | N |  |  |  | LRT 33KV Outgoing Feeder E30 | PWR:BPS:CL | E30 | 33KVOFBA | 33KVOFBA_E30 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 118 | BPS_CL |  |  |  | &33KVOFBA-E30 | PWR_BPS_CL_E30_33KVOFBA_E30 |  |  |  | Y
B | N |  |  |  | LRT 33KV Outgoing Feeder E40 | PWR:BPS:CL | E40 | 33KVOFBA | 33KVOFBA_E40 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 119 | BPS_CL |  |  |  | &33KVOFBA-E40 | PWR_BPS_CL_E40_33KVOFBA_E40 |  |  |  | Y
B | N |  |  |  | LRT 33KV Outgoing Feeder E50 | PWR:BPS:CL | E50 | 33KVOFBA | 33KVOFBA_E50 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 120 | BPS_CL |  |  |  | &33KVOFBA-E50 | PWR_BPS_CL_E50_33KVOFBA_E50 |  |  |  | Y
B | N |  |  |  | LRT 33KV Outgoing Feeder E60 | PWR:BPS:CL | E60 | 33KVOFBA | 33KVOFBA_E60 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 121 | BPS_CL |  |  |  | &33KVOFBA-E60 | PWR_BPS_CL_E60_33KVOFBA_E60 |  |  |  | Y
| Y |  |  |  |  | Bus Isolator | [15 empty] | Bus Isolator__
B | N |  |  |  | LRT 33KV Busbar Isolator E304 | PWR:BPS:CL | E30 | ISST | ISST_E304 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 122 | BPS_CL |  |  |  | &ISST-E304 | PWR_BPS_CL_E30_ISST_E304 |  |  |  | Y
B | N |  |  |  | LRT 33KV Busbar Isolator E404 | PWR:BPS:CL | E40 | ISST | ISST_E404 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 123 | BPS_CL |  |  |  | &ISST-E404 | PWR_BPS_CL_E40_ISST_E404 |  |  |  | Y
B | N |  |  |  | LRT 33KV Busbar Isolator E504 | PWR:BPS:CL | E50 | ISST | ISST_E504 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 124 | BPS_CL |  |  |  | &ISST-E504 | PWR_BPS_CL_E50_ISST_E504 |  |  |  | Y
B | N |  |  |  | LRT 33KV Busbar Isolator E604 | PWR:BPS:CL | E60 | ISST | ISST_E604 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 125 | BPS_CL |  |  |  | &ISST-E604 | PWR_BPS_CL_E60_ISST_E604 |  |  |  | Y
| Y |  |  |  |  | Maintenance Earth Switch | [15 empty] | Maintenance Earth Switch__
B | N |  |  |  | LRT 33KV Earth switch E30M1 | PWR:BPS:CL | E30 | ESST | E30M1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 126 | BPS_CL |  |  |  | &E30M1 | PWR_BPS_CL_E30_E30M1 |  |  |  | Y
B | N |  |  |  | LRT 33KV Earth switch E40M1 | PWR:BPS:CL | E40 | ESST | E40M1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 127 | BPS_CL |  |  |  | &E40M1 | PWR_BPS_CL_E40_E40M1 |  |  |  | Y
B | N |  |  |  | LRT 33KV Earth switch E50M1 | PWR:BPS:CL | E50 | ESST | E50M1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 128 | BPS_CL |  |  |  | &E50M1 | PWR_BPS_CL_E50_E50M1 |  |  |  | Y
B | N |  |  |  | LRT 33KV Earth switch E60M1 | PWR:BPS:CL | E60 | ESST | E60M1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 129 | BPS_CL |  |  |  | &E60M1 | PWR_BPS_CL_E60_E60M1 |  |  |  | Y
| Y |  |  |  |  | Vaccum Circuit Breaker | [15 empty] | Vaccum Circuit Breaker__
A7.1 | N |  |  |  | LRT 33KV Vacuum Circuit Breaker E300 | PWR:BPS:CL | E30 | CB | E300 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 130 | BPS_CL |  |  |  | &E300 | PWR_BPS_CL_E30_E300 |  |  |  | Y
A7.1 | N |  |  |  | LRT 33KV Vacuum Circuit Breaker E400 | PWR:BPS:CL | E40 | CB | E400 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 131 | BPS_CL |  |  |  | &E400 | PWR_BPS_CL_E40_E400 |  |  |  | Y
A7.1 | N |  |  |  | LRT 33KV Vacuum Circuit Breaker E500 | PWR:BPS:CL | E50 | CB | E500 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 132 | BPS_CL |  |  |  | &E500 | PWR_BPS_CL_E50_E500 |  |  |  | Y
A7.1 | N |  |  |  | LRT 33KV Vacuum Circuit Breaker E600 | PWR:BPS:CL | E60 | CB | E600 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 133 | BPS_CL |  |  |  | &E600 | PWR_BPS_CL_E60_E600 |  |  |  | Y
| Y |  |  |  |  | Circuit Breaker Protection | [15 empty] | Circuit Breaker Protection__
B | N |  |  |  | LRT 33KV Outgoing Feeder Circuit Breaker Protection E300 | PWR:BPS:CL | E30 | 33KVOFPR | 33KVOFPR_E300 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 134 | BPS_CL |  |  |  | &33KVOFPR-E300 | PWR_BPS_CL_E30_33KVOFPR_E300 |  |  |  | Y
B | N |  |  |  | LRT 33KV Outgoing Feeder Circuit Breaker Protection E400 | PWR:BPS:CL | E40 | 33KVOFPR | 33KVOFPR_E400 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 135 | BPS_CL |  |  |  | &33KVOFPR-E400 | PWR_BPS_CL_E40_33KVOFPR_E400 |  |  |  | Y
B | N |  |  |  | LRT 33KV Outgoing Feeder Circuit Breaker Protection E500 | PWR:BPS:CL | E50 | 33KVOFPR | 33KVOFPR_E500 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 136 | BPS_CL |  |  |  | &33KVOFPR-E500 | PWR_BPS_CL_E50_33KVOFPR_E500 |  |  |  | Y
B | N |  |  |  | LRT 33KV Outgoing Feeder Circuit Breaker Protection E600 | PWR:BPS:CL | E60 | 33KVOFPR | 33KVOFPR_E600 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 137 | BPS_CL |  |  |  | &33KVOFPR-E600 | PWR_BPS_CL_E60_33KVOFPR_E600 |  |  |  | Y
| Y |  |  |  |  | Measurement Value | [15 empty] | Measurement Value__
A9 | N |  |  |  | LRT 33KV measurement value E30 | PWR:BPS:CL | E30 | 33KVOFMV | 33KVOFMV_E30 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 138 | BPS_CL |  |  |  | &33KVOFMV-E30 | PWR_BPS_CL_E30_33KVOFMV_E30 |  |  |  | Y
A9 | N |  |  |  | LRT 33KV measurement value E40 | PWR:BPS:CL | E40 | 33KVOFMV | 33KVOFMV_E40 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 139 | BPS_CL |  |  |  | &33KVOFMV-E40 | PWR_BPS_CL_E40_33KVOFMV_E40 |  |  |  | Y
A9 | N |  |  |  | LRT 33KV measurement value E50 | PWR:BPS:CL | E50 | 33KVOFMV | 33KVOFMV_E50 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 140 | BPS_CL |  |  |  | &33KVOFMV-E50 | PWR_BPS_CL_E50_33KVOFMV_E50 |  |  |  | Y
A9 | N |  |  |  | LRT 33KV measurement value E60 | PWR:BPS:CL | E60 | 33KVOFMV | 33KVOFMV_E60 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 141 | BPS_CL |  |  |  | &33KVOFMV-E60 | PWR_BPS_CL_E60_33KVOFMV_E60 |  |  |  | Y
A9.1 | Y |  |  |  |  | Bay Control Authority | [16 empty] | Bay Control Authority__
A9.1 | N |  |  |  | LRT 33KV Bay Control Authority E30 | PWR:BPS:CL | E30 | BCA | BCA_E30 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 142 | BPS_CL |  |  |  | &BCA-E30 | PWR_BPS_CL_E30_BCA_E30 |  |  |  | Y
A9.1 | N |  |  |  | LRT 33KV Bay Control Authority E40 | PWR:BPS:CL | E40 | BCA | BCA_E40 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 143 | BPS_CL |  |  |  | &BCA-E40 | PWR_BPS_CL_E40_BCA_E40 |  |  |  | Y
A9.1 | N |  |  |  | LRT 33KV Bay Control Authority E50 | PWR:BPS:CL | E50 | BCA | BCA_E50 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 144 | BPS_CL |  |  |  | &BCA-E50 | PWR_BPS_CL_E50_BCA_E50 |  |  |  | Y
A9.1 | N |  |  |  | LRT 33KV Bay Control Authority E60 | PWR:BPS:CL | E60 | BCA | BCA_E60 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 145 | BPS_CL |  |  |  | &BCA-E60 | PWR_BPS_CL_E60_BCA_E60 |  |  |  | Y
| Y |  |  |  |  | Auxiliary transformer (AT) | [15 empty] | Auxiliary transformer (AT)__
| Y |  |  |  |  | Auxiliary transformer Alarms | [15 empty] | Auxiliary transformer Alarms__
B | N |  |  |  | LRT 33kV/0415kV Auxiliary Transformer Alarms AT1 | PWR:BPS:CL | E10 | AUXTF | AT1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 146 | BPS_CL |  |  |  | &AT1 | PWR_BPS_CL_E10_AT1 |  |  |  | Y
B | N |  |  |  | LRT 33kV/0415kV Auxiliary Transformer Alarms AT2 | PWR:BPS:CL | E20 | AUXTF | AT2 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 147 | BPS_CL |  |  |  | &AT2 | PWR_BPS_CL_E20_AT2 |  |  |  | Y
| Y |  |  |  |  | Power transformer (BET) | [15 empty] | Power transformer (BET)__
| Y |  |  |  |  | Power transformer Alarms | [15 empty] | Power transformer Alarms__
B | N |  |  |  | LRT 66kV/33kV Power Transformer Alarms BE-T1 | PWR:BPS:CL | E18 | POWTF | BE-T1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 148 | BPS_CL |  |  |  | &BE-T1 | PWR_BPS_CL_E18_BE-T1 |  |  |  | Y
B | N |  |  |  | LRT 66kV/33kV Power Transformer Alarms BE-T2 | PWR:BPS:CL | E28 | POWTF | BE-T2 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 149 | BPS_CL |  |  |  | &BE-T2 | PWR_BPS_CL_E28_BE-T2 |  |  |  | Y
| Y |  |  |  |  | BAY TYPE : 66KV COMMON | [15 empty] | BAY TYPE _ 66KV COMMON__
| Y |  |  |  |  | LVAC Alarms | [15 empty] | LVAC Alarms__
B | N |  |  |  | LRT 66Kv LVAC Alarms | PWR:BPS:CL | LVAC_66KV | 66KVLVAC | LVAC_66KV | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 150 | BPS_CL |  |  |  | &LVAC-66KV | PWR_BPS_CL_LVAC_66KV_LVAC_66KV |  |  |  | Y
| Y |  |  |  |  | 110V Battery Charger Signals | [15 empty] | 110V Battery Charger Signals__
B | N |  |  |  | LRT 66Kv Charger-1 Alarms | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-1_66KV | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 151 | BPS_CL |  |  |  | &BATC-1-66KV | PWR_BPS_CL_LVAC_66KV_BATC-1_66KV |  |  |  | Y
B | N |  |  |  | LRT 66Kv Charger-2 Alarms | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-2_66KV | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 152 | BPS_CL |  |  |  | &BATC-2-66KV | PWR_BPS_CL_LVAC_66KV_BATC-2_66KV |  |  |  | Y
| Y |  |  |  |  | LVDC Alarms | [15 empty] | LVDC Alarms__
B | N |  |  |  | LRT 66Kv LVDC Alarms | PWR:BPS:CL | LVAC_66KV | 66KVLVDC | LVDC_66KV | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 153 | BPS_CL |  |  |  | &LVDC-66KV | PWR_BPS_CL_LVAC_66KV_LVDC_66KV |  |  |  | Y
| Y |  |  |  |  | SF6 Circuit Breaker | [15 empty] | SF6 Circuit Breaker__
A7.1 | N |  |  |  | LRT 0 415kV SF6 Circuit Breaker QM1 | PWR:BPS:CL | LVAC_66KV | CB | QM1 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 154 | BPS_CL |  |  |  | &QM1 | PWR_BPS_CL_LVAC_66KV_QM1 |  |  |  | Y
A7.1 | N |  |  |  | LRT 0 415kV SF6 Circuit Breaker QM2 | PWR:BPS:CL | LVAC_66KV | CB | QM2 | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 155 | BPS_CL |  |  |  | &QM2 | PWR_BPS_CL_LVAC_66KV_QM2 |  |  |  | Y
A7.1 | N |  |  |  | LRT 0 415kV SF6 Circuit Breaker QBS | PWR:BPS:CL | LVAC_66KV | CB | QBS | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 156 | BPS_CL |  |  |  | &QBS | PWR_BPS_CL_LVAC_66KV_QBS |  |  |  | Y
| Y |  |  |  |  | BAY TYPE : 33KV COMMON | [15 empty] | BAY TYPE _ 33KV COMMON__
| Y |  |  |  |  | LVDC Alarms | [15 empty] | LVDC Alarms__
B | N |  |  |  | LRT 33Kv LVDC Alarms | PWR:BPS:CL | LVDC_33KV | 33KVLVDC | LVDC_33KV | BPS01_RTU | BPS_CL_GTW |  |  |  |  | 157 | BPS_CL |  |  |  | &LVDC-33KV | PWR_BPS_CL_LVDC_33KV_LVDC_33KV |  |  |  | Y
Note on J88: Katherine Shih: alias will be too long for configuration
Note on J174: Katherine Shih: alias will be too long for configuration

## 3-Class Mapping
Class name | Prototype | Aggregate name | Object type | isAComment | Scstype | Abbreviated Class Name
CB | LusailHK:LusBpsCb |  |  | N | LusBpsCbType | CB
CB_OST | LusailHK:LusBpsCbOst |  |  | N | LusBpsCbOstType | CBOST
WTDG | LusailHK:LusBpsWtdg |  |  | N | LusBpsWtdbType | WTDG
VTIS | LusailHK:LusBpsVtis |  |  | N | LusBpsVtisType | VTIS
GTW | LusailHK:LusBpsGtw |  |  | N | LusBpsGtwType | GTW
BBPZ | LusailHK:LusBpsBbpz |  |  | N | LusBpsBbpzType | BBPZ
BBAL | LusailHK:LusBpsBbal |  |  | N | LusBpsBbalType | BBAL
BBPR | LusailHK:LusBpsBbpr |  |  | N | LusBpsBbprType | BBPR
ISST | LusailHK:LusBpsIsst |  |  | N | LusBpsIsstType | ISST
BIST | LusailHK:LusBpsBist |  |  | N | LusBpsBistType | BIST
BSCP | LusailHK:LusBpsBscp |  |  | N | LusBpsBscpType | BSCP
66KVIFPR | LusailHK:LusBps66kvifpr |  |  | N | LusBps66kvifprType | IFPR6
33KVIFPR | LusailHK:LusBps33kvifpr |  |  | N | LusBps33kvifprType | IFPR3
66KVBSPR | LusailHK:LusBps66kvbspr |  |  | N | LusBps66kvbsprType | BSPR6
33KVBSPR | LusailHK:LusBps33kvbspr |  |  | N | LusBps33kvbsprType | BSPR3
66KVHVPR | LusailHK:LusBps66kvhvpr |  |  | N | LusBps66kvhvprType | HVPR6
33KVSTPR | LusailHK:LusBps33kvstpr |  |  | N | LusBps33kvstprType | STPR3
33KVOFPR | LusailHK:LusBps33kvofpr |  |  | N | LusBps33kvofprType | OFPR3
ESST | LusailHK:LusBpsEsst |  |  | N | LusBpsEsstType | ESST
ESSM | LusailHK:LusBpsEssm |  |  | N | LusBpsEssmType | ESSM
66KVIFBA | LusailHK:LusBps66kvifba |  |  | N | LusBps66kvifbaType | IFBA6
33KVIFBA | LusailHK:LusBps33kvifba |  |  | N | LusBps33kvifbaType | IFBA3
66KVHVBA | LusailHK:LusBps66kvhvba |  |  | N | LusBps66kvhvbaType | HVBA6
33KVSTBA | LusailHK:LusBps33kvstba |  |  | N | LusBps33kvstbaType | STBA3
66KVBSBA | LusailHK:LusBps66kvbsba |  |  | N | LusBps66kvbsbaType | BSBA6
33KVBSBA | LusailHK:LusBps33kvbsba |  |  | N | LusBps33kvbsbaType | BSBA
33KVOFBA | LusailHK:LusBps33kvofba |  |  | N | LusBps33kvofbaType | OFBA
66KVLVAC | LusailHK:LusBps66kvlvac |  |  | N | LusBps66kvlvacType | LVAC
66KVBATC | LusailHK:LusBps66kvbatc |  |  | N | LusBps66kvbatcType | BATC
66KVLVDC | LusailHK:LusBps66kvlvdc |  |  | N | LusBps66kvlvdcType | LVDC6
33KVLVDC | LusailHK:LusBps33kvlvdc |  |  | N | LusBps33kvlvdcType | LVDC3
66KVIFMV | LusailHK:LusBps66kvifmv |  |  | N | LusBps66kvifmvType | IFMV6
33KVIFMV | LusailHK:LusBps33kvifmv |  |  | N | LusBps33kvifmvType | IFMV3
66KVHVMV | LusailHK:LusBps66kvhvmv |  |  | N | LusBps66kvhvmvType | HVMV
33KVSTMV | LusailHK:LusBps33kvstmv |  |  | N | LusBps33kvstmvType | STMV
66KVBSMV | LusailHK:LusBps66kvbsmv |  |  | N | LusBps66kvbsmvType | BSMV6
33KVBSMV | LusailHK:LusBps33kvbsmv |  |  | N | LusBps33kvbsmvType | BSMV3
33KVOFMV | LusailHK:LusBps33kvofmv |  |  | N | LusBps33kvofmvType | OFMV
33KVVM | LusailHK:LusBps33kvvm |  |  | N | LusBps33kvvmType | VVM3
66KVVM | LusailHK:LusBps66kvvm |  |  | N | LusBps66kvvmType | VVM6
AUXTF | LusailHK:LusBpsAuxtf |  |  | N | LusBpsAuxtfType | AUXTF
POWTF | LusailHK:LusBpsPowtf |  |  | N | LusBpsPowtfType | POWTF
BCA | LusailHK:LusBpsBca |  |  | N | LusBpsBcaType | BCA

## 4-External Variables
Class name | iopath | vetype | ve_basename | description | address | EVGroup | Concentrator Suffix | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
BBPZ | dciBBPZ-Trip1:dac | DEIV | Trip1 | Busbar Protection M1 Zone Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
BBPZ | dciBBPZ-Trip2:dac | DEIV | Trip2 | Busbar Protection M2 Zone Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
BBPZ | dciBBPZ-Operated:dac | DEIV | Operated | Busbar Protection Operated | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
BBAL | dciBBAL-OutofServ:dac | DEIV | OutofServ | Busbar Protection Out of Service | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
BBAL | dciBBAL-Disturbed:dac | DEIV | Disturbed | Busbar Protection Disturbed | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
BBAL | dciBBAL-Blocked:dac | DEIV | Blocked | All Protection Blocked | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
BBAL | dciBBAL-Zone1:dac | DEIV | Zone1 | CB Failure Stage 2 M1 Zone | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
BBAL | dciBBAL-Zone2:dac | DEIV | Zone2 | CB Failure Stage 2 M2 Zone | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
BBAL | dciBBAL-Operated:dac | DEIV | Operated | Breaker Failure Operated | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
BBAL | dciBBAL-ZoneTrp1:dac | DEIV | ZoneTrp1 | Busbar Protection M1 Zone Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
BBAL | dciBBAL-ZoneTrp2:dac | DEIV | ZoneTrp2 | Busbar Protection M2 Zone Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
BBAL | dciBBAL-BlockedZone1:dac | DEIV | BlockedZone1 | Busbar Protection Blocked M1 Zone | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
BBAL | dciBBAL-BlcokedZone2:dac | DEIV | BlcokedZone2 | Busbar Protection Blocked M2 Zone | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
BBPR | dciBBPR-Stg1:dac | DEIV | Stg1 | Breaker Failure Stage-1 Operated | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
BBPR | dciBBPR-Stg2:dac | DEIV | Stg2 | Breaker Failure Stage-2 Operated | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
ISST | dciISST-IsoSts:dac | DEIV | IsoSts | Bus Isolator Status | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
ISST | dioISST-CmdSelOpen:dov | DEOV | CmdSelOpen | Bus Isolator Open Order Select | $VOID | VES | _S2C | 0 |  |  |  | 4 |  |  | N
ISST | dciISST-AckSelOpen:dac | DEIV | AckSelOpen | Bus Isolator Open Order Select Ack | $VOID | VEE | _S2C | 0 |  |  |  | 4 |  |  | N
ISST | dioISST-CmdExeOpen:dov | DEOV | CmdExeOpen | Bus Isolator Open Order Execute | $VOID | VES | _S2C | 0 |  |  |  | 4 |  |  | N
ISST | dciISST-AckExeOpen:dac | DEIV | AckExeOpen | Bus Isolator Open Order Execute Ack | $VOID | VEE | _S2C | 0 |  |  |  | 4 |  |  | N
ISST | dioISST-CmdSelClose:dov | DEOV | CmdSelClose | Bus Isolator Close Order Select | $VOID | VES | _S2C | 0 |  |  |  | 4 |  |  | N
ISST | dciISST-AckSelClose:dac | DEIV | AckSelClose | Bus Isolator Close Order Select Ack | $VOID | VEE | _S2C | 0 |  |  |  | 4 |  |  | N
ISST | dioISST-CmdExeClose:dov | DEOV | CmdExeClose | Bus Isolator Close Order Execute | $VOID | VES | _S2C | 0 |  |  |  | 4 |  |  | N
ISST | dciISST-AckExeClose:dac | DEIV | AckExeClose | Bus Isolator Close Order Execute Ack | $VOID | VEE | _S2C | 0 |  |  |  | 4 |  |  | N
BIST | dciBIST-IsoSts:dac | DEIV | IsoSts | Bus Isolator Status | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
CB | dciCB-CirBrkStatus:dac | DEIV | CirBrkStatus | Circuit Breaker Status | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
CB | dioCB-CmdSelOpen:dov | DEOV | CmdSelOpen | Circuit Breaker Open Order Select | $VOID | VES | _S2C | 0 |  |  |  | 4 |  |  | N
CB | dciCB-AckSelOpen:dac | DEIV | AckSelOpen | Circuit Breaker Open Order Select Ack | $VOID | VEE | _S2C | 0 |  |  |  | 4 |  |  | N
CB | dioCB-CmdExeOpen:dov | DEOV | CmdExeOpen | Circuit Breaker Open Order Execute | $VOID | VES | _S2C | 0 |  |  |  | 4 |  |  | N
CB | dciCB-AckExeOpen:dac | DEIV | AckExeOpen | Circuit Breaker Open Order Execute Ack | $VOID | VEE | _S2C | 0 |  |  |  | 4 |  |  | N
CB | dioCB-CmdSelClose:dov | DEOV | CmdSelClose | Circuit Breaker Close Order Select | $VOID | VES | _S2C | 0 |  |  |  | 4 |  |  | N
CB | dciCB-AckSelClose:dac | DEIV | AckSelClose | Circuit Breaker Close Order Select Ack | $VOID | VEE | _S2C | 0 |  |  |  | 4 |  |  | N
CB | dioCB-CmdExeClose:dov | DEOV | CmdExeClose | Circuit Breaker Close Order Execute | $VOID | VES | _S2C | 0 |  |  |  | 4 |  |  | N
CB | dciCB-AckExeClose:dac | DEIV | AckExeClose | Circuit Breaker Close Order Execute Ack | $VOID | VEE | _S2C | 0 |  |  |  | 4 |  |  | N
CB_OST | dciCBOST-Status:dac | DEIV | Status | Circuit Breaker Status | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
BSCP | dciBSCP-Stg1Oper1:dac | DEIV | Stg1Oper1 | Breaker Failure Stage-1 Operated - M1 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
BSCP | dciBSCP-Stg2Oper1:dac | DEIV | Stg2Oper1 | Breaker Failure Stage-2 Operated - M1 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
BSCP | dciBSCP-Stg1Oper2:dac | DEIV | Stg1Oper2 | Breaker Failure Stage-1 Operated - M2 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
BSCP | dciBSCP-Stg2Oper2:dac | DEIV | Stg2Oper2 | Breaker Failure Stage-2 Operated - M2 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFPR | dciIFPR6-SupFail11:dac | DEIV | SupFail11 | T11 DC Supply Fail | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFPR | dciIFPR6-SupFaill21:dac | DEIV | SupFaill21 | T21 DC Supply Fail | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFPR | dciIFPR6-FailCh1:dac | DEIV | FailCh1 | Diff Communication Fail Ch-1 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFPR | dciIFPR6-FailCh2:dac | DEIV | FailCh2 | Diff Communication Fail Ch-2 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFPR | dciIFPR6-ProtTrip:dac | DEIV | ProtTrip | Main-1 Dist Protection Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFPR | dciIFPR6-LoadCurr:dac | DEIV | LoadCurr | Main-1 110% of Full Load Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFPR | dciIFPR6-SoftTrip:dac | DEIV | SoftTrip | Main-1 SOTF Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFPR | dciIFPR6-Swing:dac | DEIV | Swing | Main-1 Power Swing Block | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFPR | dciIFPR6-McbTrip:dac | DEIV | McbTrip | Main-1 VT Fuse Failure / MCB Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFPR | dciIFPR6-OverCurrTrip:dac | DEIV | OverCurrTrip | Backup Overcurrent I>Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFPR | dciIFPR6-ReceCh1:dac | DEIV | ReceCh1 | Intertrip Received Channel-1 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFPR | dciIFPR6-ReceCh2:dac | DEIV | ReceCh2 | Intertrip Received Channel-2 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFPR | dciIFPR6-SentCh1:dac | DEIV | SentCh1 | Intertrip Sent Channel-1 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFPR | dciIFPR6-SentCh2:dac | DEIV | SentCh2 | Intertrip Sent Channel-2 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFPR | dciIFPR3-DirTrip:dac | DEIV | DirTrip | Dir Overcurrent I>Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFPR | dciIFPR3-RefTrip:dac | DEIV | RefTrip | 40MVA-T1 LV REF Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFPR | dciIFPR3-EfTrip1:dac | DEIV | EfTrip1 | Standby EF In>St-1 Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFPR | dciIFPR3-EfTrip2:dac | DEIV | EfTrip2 | Standby EF In>St-2 Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFPR | dciIFPR3-Start:dac | DEIV | Start | Standby EF In>Start | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFPR | dciIFPR3-Faulty:dac | DEIV | Faulty | NER Faulty | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFPR | dciIFPR3-GroundFault:dac | DEIV | GroundFault | NER Ground Fault | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFPR | dciIFPR3-Unhealthy:dac | DEIV | Unhealthy | NER Monitor Unhealthy | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSPR | dciBSPR6-GenTrip:dac | DEIV | GenTrip | General Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSPR | dciBSPR3-OverCurTrip:dac | DEIV | OverCurTrip | Over Current Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVPR | dciHVPR6-DiffTrip:dac | DEIV | DiffTrip | 40MVA-T1 Main-1 Diff Prot Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVPR | dciHVPR6-ProtHigh:dac | DEIV | ProtHigh | 40MVA-T1 Diff Prot High Set St2 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVPR | dciHVPR6-GenTrip:dac | DEIV | GenTrip | General Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTPR | dciSTPR3-GenTrip:dac | DEIV | GenTrip | General Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTPR | dciSTPR3-RefTrip:dac | DEIV | RefTrip | 1000kVA AT-1 LV REF Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFPR | dciOFPR3-GenTrip:dac | DEIV | GenTrip | General Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFPR | dciOFPR3-DiffProtTrip:dac | DEIV | DiffProtTrip | Differential Protection Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFPR | dciOFPR3-OverloadAlarm:dac | DEIV | OverloadAlarm | Thermal Overload Alarm St-1 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFPR | dciOFPR3-CommFail:dac | DEIV | CommFail | Diff Communication Fail | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFPR | dciOFPR3-FuseFail:dac | DEIV | FuseFail | VT Fuse Failure / MCB Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFPR | dciOFPR3-OvercurrTrip:dac | DEIV | OvercurrTrip | Backup Overcurrent I>Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFPR | dciOFPR3-Received:dac | DEIV | Received | Intertrip Received | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFPR | dciOFPR3-Sent:dac | DEIV | Sent | Intertrip Sent | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
ESST | dciESST-SwitchSts:dac | DEIV | SwitchSts | Earth Switch Status | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
ESST | dioESST-CmdOpen:dov | DEOV | CmdOpen | Earth Switch Control 1 | $VOID | VES | _S0 | 0 |  |  |  | 4 |  |  | N
ESST | dioESST-CmdClose:dov | DEOV | CmdClose | Earth Switch Control 2 | $VOID | VES | _S0 | 0 |  |  |  | 4 |  |  | N
ESSM | dciESSM-SwitchSts:dac | DEIV | SwitchSts | Earth Switch Status | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFBA | dciIFBA6-AcPanel:dac | DEIV | AcPanel | AC Fail Relay Panel / LCC | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFBA | dciIFBA6-DcPanel:dac | DEIV | DcPanel | DC Fail Relay Panel | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFBA | dciIFBA6-LccPanel:dac | DEIV | LccPanel | DC Fail LCC | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFBA | dciIFBA6-Stage1:dac | DEIV | Stage1 | Gas Pressure Stage 1 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFBA | dciIFBA6-Stage2:dac | DEIV | Stage2 | Gas Pressure Stage 2 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFBA | dciIFBA6-Operated:dac | DEIV | Operated | MasterTrip relay operated | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
66KVIFBA | dciIFBA6-IedWtdg:dac | DEIV | IedWtdg | IED WatchDog | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFBA | dciIFBA6-BcuWtdg:dac | DEIV | BcuWtdg | BCU WatchDog | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
66KVIFBA | dciIFBA6-FuseFail:dac | DEIV | FuseFail | Voltage Transformer Fuse Fail | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFBA | dciIFBA6-OverloadAlarm:dac | DEIV | OverloadAlarm | Thermal over load Alarm | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFBA | dciIFBA6-CardFail:dac | DEIV | CardFail | BCU Card Fail | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFBA | dciIFBA3-AcPanel:dac | DEIV | AcPanel | AC Fail Relay Panel / LCC | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFBA | dciIFBA3-DcPanel:dac | DEIV | DcPanel | DC Fail Relay Panel | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFBA | dciIFBA3-FailCell:dac | DEIV | FailCell | DC Fail Cell | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFBA | dciIFBA3-IedWtdg:dac | DEIV | IedWtdg | IED WatchDog | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFBA | dciIFBA3-BcuWtdg:dac | DEIV | BcuWtdg | BCU WatchDog | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
33KVIFBA | dciIFBA3-FaultAlarm:dac | DEIV | FaultAlarm | Voltage Transformer Fault alarm | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFBA | dciIFBA3-TempTrip:dac | DEIV | TempTrip | 40MVA T-1 Winding Temp Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFBA | dciIFBA3-TempAlarm:dac | DEIV | TempAlarm | 40MVA T-1 Winding Temp Alarm | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFBA | dciIFBA3-Limit:dac | DEIV | Limit | Tap Changer Limit | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFBA | dciIFBA3-OilLvAlarm:dac | DEIV | OilLvAlarm | Main Transformer Oil Level Alarm | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFBA | dciIFBA3-CoolerAlarm:dac | DEIV | CoolerAlarm | Tap Changer Oil Level Alarm | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFBA | dciIFBA3-FanAlarm:dac | DEIV | FanAlarm | Transformer Fan Cooler Alarm | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFBA | dciIFBA3-DehyAlarm:dac | DEIV | DehyAlarm | 40MVA T-1 Main Dehydrating Alarm | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFBA | dciIFBA3-CardFail:dac | DEIV | CardFail | BCU Card Fail | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVBA | dciHVBA6-AcPanel:dac | DEIV | AcPanel | AC Fail Relay Panel / LCC | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVBA | dciHVBA6-DcPanel:dac | DEIV | DcPanel | DC Fail Relay Panel | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVBA | dciHVBA6-LccPanel:dac | DEIV | LccPanel | DC Fail LCC Panel | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVBA | dciHVBA6-Stage1:dac | DEIV | Stage1 | SF6 Gas Pressure Stage 1 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVBA | dciHVBA6-Stage2:dac | DEIV | Stage2 | SF6 Gas Pressure Stage 2 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVBA | dciHVBA6-Operated:dac | DEIV | Operated | MasterTrip relay operated | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
66KVHVBA | dciHVBA6-IedWtdg:dac | DEIV | IedWtdg | IED WatchDog | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVBA | dciHVBA6-BcuWtdg:dac | DEIV | BcuWtdg | BCU WatchDog | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
66KVHVBA | dciHVBA6-ProtOperated:dac | DEIV | ProtOperated | OC/EF Protection Operated | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
66KVHVBA | dciHVBA6-CardFail:dac | DEIV | CardFail | BCU Card Fail | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTBA | dciSTBA3-AcPanel:dac | DEIV | AcPanel | AC Fail Relay Panel / SWGR | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTBA | dciSTBA3-DcPanel:dac | DEIV | DcPanel | DC Fail Relay Panel | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTBA | dciSTBA3-FailSwgr:dac | DEIV | FailSwgr | DC Fail SWGR | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTBA | dciSTBA3-IedWtdg:dac | DEIV | IedWtdg | IED WatchDog | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTBA | dciSTBA3-BcuWtdg:dac | DEIV | BcuWtdg | BCU WatchDog | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
33KVSTBA | dciSTBA3-FaultAlarm:dac | DEIV | FaultAlarm | Voltage Transformer Fault alarm | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTBA | dciSTBA3-CardFail:dac | DEIV | CardFail | BCU Card Fail | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSBA | dciBSBA6-AcPanel:dac | DEIV | AcPanel | AC Fail Relay Panel / LCC | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSBA | dciBSBA6-DcPanel:dac | DEIV | DcPanel | DC Fail Relay Panel | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSBA | dciBSBA6-LccPanel:dac | DEIV | LccPanel | DC Fail LCC Panel | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSBA | dciBSBA6-Stage1:dac | DEIV | Stage1 | SF6 Gas Pressure 1st Stage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSBA | dciBSBA6-Stage2:dac | DEIV | Stage2 | SF6 Gas Pressure 2nd Stage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSBA | dciBSBA6-Operated:dac | DEIV | Operated | MasterTrip relay operated | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
66KVBSBA | dciBSBA6-IedWtdg:dac | DEIV | IedWtdg | IED WatchDog | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSBA | dciBSBA6-BcuWtdg:dac | DEIV | BcuWtdg | BCU WatchDog | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
66KVBSBA | dciBSBA6-FaultAlarm:dac | DEIV | FaultAlarm | Voltage Transformer Fault alarm | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSBA | dciBSBA6-BrkStage1:dac | DEIV | BrkStage1 | Breaker failure stage 1 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSBA | dciBSBA6-BrkStage2:dac | DEIV | BrkStage2 | Breaker failure stage 2 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSBA | dciBSBA6-CardFail:dac | DEIV | CardFail | BCU Card Fail | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSBA | dciBSBA-AcPanel:dac | DEIV | AcPanel | AC Fail Relay Panel / Cell | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSBA | dciBSBA-DcPanel:dac | DEIV | DcPanel | DC Fail Relay Panel | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSBA | dciBSBA-FailCell:dac | DEIV | FailCell | DC Fail Cell | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSBA | dciBSBA-Operated:dac | DEIV | Operated | MasterTrip relay operated | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
33KVBSBA | dciBSBA-IedWtdg:dac | DEIV | IedWtdg | IED WatchDog | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSBA | dciBSBA-BcuWtdg:dac | DEIV | BcuWtdg | BCU WatchDog | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
33KVBSBA | dciBSBA-FaultAlarm:dac | DEIV | FaultAlarm | Voltage Transformer Fault alarm | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSBA | dciBSBA-SyncFail:dac | DEIV | SyncFail | Synchronisation Fail | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSBA | dciBSBA-CardFail:dac | DEIV | CardFail | BCU Card Fail | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFBA | dciOFBA-AcPanel:dac | DEIV | AcPanel | AC Fail Relay Panel / SWGR | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFBA | dciOFBA-DcPanel:dac | DEIV | DcPanel | DC Fail Relay Panel | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFBA | dciOFBA-FailSwgr:dac | DEIV | FailSwgr | DC Fail SWGR | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFBA | dciOFBA-IedWtdg:dac | DEIV | IedWtdg | IED WatchDog | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFBA | dciOFBA-BcuWtdg:dac | DEIV | BcuWtdg | BCU WatchDog | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
33KVOFBA | dciOFBA-FaultAlarm:dac | DEIV | FaultAlarm | Voltage Transformer Fault alarm | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFBA | dciOFBA-CardFail:dac | DEIV | CardFail | BCU Card Fail | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
GTW | dciGTW-ConnSts:dac | DEIV | ConnSts | [GTW]: Connection Status | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVLVAC | dciLVAC-BrkTrip1:dac | DEIV | BrkTrip1 | Incomer 1 Breaker Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVLVAC | dciLVAC-BrkTrip2:dac | DEIV | BrkTrip2 | Incomer 2 Breaker Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVLVAC | dciLVAC-SecBrkTrip:dac | DEIV | SecBrkTrip | Bus Section Breaker Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVLVAC | dciLVAC-Fault1:dac | DEIV | Fault1 | Bus-1 Feeder Fault | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVLVAC | dciLVAC-Fault2:dac | DEIV | Fault2 | Bus-2 Feeder Fault | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVLVAC | dciLVAC-AcOff:dac | DEIV | AcOff | AC Control MCB Off/Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVLVAC | dciLVAC-DcOff:dac | DEIV | DcOff | DC Control MCB Off/Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBATC | dciBATC-ChargerFault:dac | DEIV | ChargerFault | Charger Fault | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBATC | dciBATC-AcFail1:dac | DEIV | AcFail1 | AC Supply Failure 1 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBATC | dciBATC-AcFail2:dac | DEIV | AcFail2 | AC Supply Failure 2 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBATC | dciBATC-EqualizerCharge:dac | DEIV | EqualizerCharge | Charger on Equalizer Charge | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBATC | dciBATC-UnderVolt:dac | DEIV | UnderVolt | Charger Under Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBATC | dciBATC-BoostCharge:dac | DEIV | BoostCharge | Charger on Boost Charge | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBATC | dciBATC-FuseFail:dac | DEIV | FuseFail | Battery Fuse Failure | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBATC | dciBATC-FanFail:dac | DEIV | FanFail | Battery Charger Fan Fail | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBATC | dciBATC-Overload:dac | DEIV | Overload | Charger Overload | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBATC | dciBATC-SupFailure:dac | DEIV | SupFailure | DC Supply Failure | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVLVDC | dciLVDC6-Trip1:dac | DEIV | Trip1 | Incomer 1 Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVLVDC | dciLVDC6-Trip2:dac | DEIV | Trip2 | Incomer 2 Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVLVDC | dciLVDC6-AcOff:dac | DEIV | AcOff | AC Control MCB Off/Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVLVDC | dciLVDC6-LeftTrip:dac | DEIV | LeftTrip | DC Feeder Left Bus Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVLVDC | dciLVDC6-RightTrip:dac | DEIV | RightTrip | DC Feeder Right Bus Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVLVDC | dciLVDC6-LeftBus:dac | DEIV | LeftBus | Under Voltage Left Busbar | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVLVDC | dciLVDC6-RightBus:dac | DEIV | RightBus | Under Voltage Right Busbar | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVLVDC | dciLVDC6-Earthfault1:dac | DEIV | Earthfault1 | Incomer-1 Earthfault | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVLVDC | dciLVDC6-Earthfault2:dac | DEIV | Earthfault2 | Incomer-2 Earthfault | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVLVDC | dciLVDC6-DcOff:dac | DEIV | DcOff | DC Control MCB Off/Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVLVDC | dciLVDC3-MccbTrip1:dac | DEIV | MccbTrip1 | Incomer-1 MCCB Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVLVDC | dciLVDC3-MccbTrip2:dac | DEIV | MccbTrip2 | Incomer-2 MCCB Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVLVDC | dciLVDC3-SecMccbTrip:dac | DEIV | SecMccbTrip | Bus Section MCCB Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVLVDC | dciLVDC3-OgTrip1:dac | DEIV | OgTrip1 | Bus-1 O/G Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVLVDC | dciLVDC3-OgTrip2:dac | DEIV | OgTrip2 | Bus-2 O/G Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVLVDC | dciLVDC3-AcOff:dac | DEIV | AcOff | AC Control MCB Off/Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVLVDC | dciLVDC3-DcOff:dac | DEIV | DcOff | DC Control MCB Off/Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFMV | aciIFMV6-Rphase | AEIV | Rphase | R Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFMV | aciIFMV6-Yphase | AEIV | Yphase | Y Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFMV | aciIFMV6-Bphase | AEIV | Bphase | B Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFMV | aciIFMV6-NeuCurr | AEIV | NeuCurr | Neutral Current In | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFMV | aciIFMV6-RyPhase | AEIV | RyPhase | RY Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFMV | aciIFMV6-YbPhase | AEIV | YbPhase | YB Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFMV | aciIFMV6-BrPhase | AEIV | BrPhase | BR Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFMV | aciIFMV6-ZeroVolt | AEIV | ZeroVolt | Zero Sequence Voltage (V0) | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFMV | aciIFMV6-ActivePower | AEIV | ActivePower | Active Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFMV | aciIFMV6-ReacPower | AEIV | ReacPower | Reactive Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFMV | aciIFMV6-AppPower | AEIV | AppPower | Apparent Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFMV | aciIFMV6-PowerFactor | AEIV | PowerFactor | Power Factor | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVIFMV | aciIFMV6-Frequency | AEIV | Frequency | Frequency | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFMV | aciIFMV3-Rphase | AEIV | Rphase | R Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFMV | aciIFMV3-Yphase | AEIV | Yphase | Y Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFMV | aciIFMV3-Bphase | AEIV | Bphase | B Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFMV | aciIFMV3-NeuCurr | AEIV | NeuCurr | Neutral Current In | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFMV | aciIFMV3-RyPhase | AEIV | RyPhase | RY Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFMV | aciIFMV3-YbPhase | AEIV | YbPhase | YB Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFMV | aciIFMV3-BrPhase | AEIV | BrPhase | BR Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFMV | aciIFMV3-ZeroVolt | AEIV | ZeroVolt | Zero Sequence Voltage (V0) | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFMV | aciIFMV3-ActivePower | AEIV | ActivePower | Active Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFMV | aciIFMV3-ReacPower | AEIV | ReacPower | Reactive Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFMV | aciIFMV3-AppPower | AEIV | AppPower | Apparent Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFMV | aciIFMV3-PowerFactor | AEIV | PowerFactor | Power Factor | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVIFMV | aciIFMV3-Frequency | AEIV | Frequency | Frequency | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVMV | aciHVMV-Rphase | AEIV | Rphase | R Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVMV | aciHVMV-Yphase | AEIV | Yphase | Y Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVMV | aciHVMV-Bphase | AEIV | Bphase | B Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVMV | aciHVMV-NeuCurr | AEIV | NeuCurr | Neutral Current In | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVMV | aciHVMV-RyPhase | AEIV | RyPhase | RY Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVMV | aciHVMV-YbPhase | AEIV | YbPhase | YB Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVMV | aciHVMV-BrPhase | AEIV | BrPhase | BR Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVMV | aciHVMV-ZeroVolt | AEIV | ZeroVolt | Zero Sequence Voltage (V0) | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVMV | aciHVMV-ActivePower | AEIV | ActivePower | Active Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVMV | aciHVMV-ReacPower | AEIV | ReacPower | Reactive Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVMV | aciHVMV-AppPower | AEIV | AppPower | Apparent Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVMV | aciHVMV-PowerFactor | AEIV | PowerFactor | Power Factor | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVHVMV | aciHVMV-Frequency | AEIV | Frequency | Frequency | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTMV | aciSTMV-Rphase | AEIV | Rphase | R Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTMV | aciSTMV-Yphase | AEIV | Yphase | Y Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTMV | aciSTMV-Bphase | AEIV | Bphase | B Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTMV | aciSTMV-NeuCurr | AEIV | NeuCurr | Neutral Current In | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTMV | aciSTMV-RyPhase | AEIV | RyPhase | RY Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTMV | aciSTMV-YbPhase | AEIV | YbPhase | YB Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTMV | aciSTMV-BrPhase | AEIV | BrPhase | BR Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTMV | aciSTMV-ZeroVolt | AEIV | ZeroVolt | Zero Sequence Voltage (V0) | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTMV | aciSTMV-ActivePower | AEIV | ActivePower | Active Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTMV | aciSTMV-ReacPower | AEIV | ReacPower | Reactive Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTMV | aciSTMV-AppPower | AEIV | AppPower | Apparent Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTMV | aciSTMV-PowerFactor | AEIV | PowerFactor | Power Factor | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVSTMV | aciSTMV-Frequency | AEIV | Frequency | Frequency | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSMV | aciBSMV6-Rphase | AEIV | Rphase | R Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSMV | aciBSMV6-Yphase | AEIV | Yphase | Y Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSMV | aciBSMV6-Bphase | AEIV | Bphase | B Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSMV | aciBSMV6-NeuCurr | AEIV | NeuCurr | Neutral Current In | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSMV | aciBSMV6-RyPhase | AEIV | RyPhase | RY Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSMV | aciBSMV6-YbPhase | AEIV | YbPhase | YB Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSMV | aciBSMV6-BrPhase | AEIV | BrPhase | BR Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSMV | aciBSMV6-ZeroVolt | AEIV | ZeroVolt | Zero Sequence Voltage (V0) | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSMV | aciBSMV6-ActivePower | AEIV | ActivePower | Active Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSMV | aciBSMV6-ReacPower | AEIV | ReacPower | Reactive Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSMV | aciBSMV6-AppPower | AEIV | AppPower | Apparent Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSMV | aciBSMV6-PowerFactor | AEIV | PowerFactor | Power Factor | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVBSMV | aciBSMV6-Frequency | AEIV | Frequency | Frequency | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSMV | aciBSMV3-Rphase | AEIV | Rphase | R Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSMV | aciBSMV3-Yphase | AEIV | Yphase | Y Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSMV | aciBSMV3-Bphase | AEIV | Bphase | B Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSMV | aciBSMV3-NeuCurr | AEIV | NeuCurr | Neutral Current In | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSMV | aciBSMV3-RyPhase | AEIV | RyPhase | RY Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSMV | aciBSMV3-YbPhase | AEIV | YbPhase | YB Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSMV | aciBSMV3-BrPhase | AEIV | BrPhase | BR Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSMV | aciBSMV3-ZeroVolt | AEIV | ZeroVolt | Zero Sequence Voltage (V0) | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSMV | aciBSMV3-ActivePower | AEIV | ActivePower | Active Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSMV | aciBSMV3-ReacPower | AEIV | ReacPower | Reactive Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSMV | aciBSMV3-AppPower | AEIV | AppPower | Apparent Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSMV | aciBSMV3-PowerFactor | AEIV | PowerFactor | Power Factor | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVBSMV | aciBSMV3-Frequency | AEIV | Frequency | Frequency | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFMV | aciOFMV-Rphase | AEIV | Rphase | R Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFMV | aciOFMV-Yphase | AEIV | Yphase | Y Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFMV | aciOFMV-Bphase | AEIV | Bphase | B Phase Current | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFMV | aciOFMV-NeuCurr | AEIV | NeuCurr | Neutral Current In | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFMV | aciOFMV-RyPhase | AEIV | RyPhase | RY Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFMV | aciOFMV-YbPhase | AEIV | YbPhase | YB Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFMV | aciOFMV-BrPhase | AEIV | BrPhase | BR Phase Voltage | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFMV | aciOFMV-ZeroVolt | AEIV | ZeroVolt | Zero Sequence Voltage (V0) | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFMV | aciOFMV-ActivePower | AEIV | ActivePower | Active Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFMV | aciOFMV-ReacPower | AEIV | ReacPower | Reactive Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFMV | aciOFMV-AppPower | AEIV | AppPower | Apparent Power | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFMV | aciOFMV-PowerFactor | AEIV | PowerFactor | Power Factor | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVOFMV | aciOFMV-Frequency | AEIV | Frequency | Frequency | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
33KVVM | aciVVM3-VoltageMesure | AEIV | VoltageMesure | Voltage Measurement | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
66KVVM | aciVVM6-VoltageMesure | AEIV | VoltageMesure | Voltage Measurement | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
VTIS | dciVTIS-IsoPosition:dac | DEIV | IsoPosition | Isolator Position | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
WTDG | aciWTDG-WdCounter | AEIV | WdCounter | Watchdog Counter | $VOID | VEE | _S2M | 0 |  |  |  | 4 |  |  | N
AUXTF | dciAUXTF-BuchAlarm:dac | DEIV | BuchAlarm | 1000kVA Auxiliary Transformer Buchholz Alarm | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
AUXTF | dciAUXTF-BuchTrip:dac | DEIV | BuchTrip | 1000kVA Auxiliary Transformer Buchholz Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
AUXTF | dciAUXTF-OilMin:dac | DEIV | OilMin | Oil Level Alarm Min | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
AUXTF | dciAUXTF-OilMax:dac | DEIV | OilMax | Oil Level Alarm Max | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
AUXTF | dciAUXTF-OilTempAlarm:dac | DEIV | OilTempAlarm | 1000kVA Auxiliary Transformer Oil Temp Alarm | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
AUXTF | dciAUXTF-PrvAlarm:dac | DEIV | PrvAlarm | 1000kVA Auxiliary Transformer PRV Alarm | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
AUXTF | dciAUXTF-OilTempTrip:dac | DEIV | OilTempTrip | 1000kVA Auxiliary Transformer Oil Temp Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
AUXTF | dciAUXTF-PrdTrip:dac | DEIV | PrdTrip | 1000kVA Auxiliary Transformer PRD Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
AUXTF | dciAUXTF-TempAlarm:dac | DEIV | TempAlarm | 1000 kVA Auxilary Transformer Winding Temperature Alarm | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
AUXTF | dciAUXTF-TempTrip:dac | DEIV | TempTrip | 1000 kVA Auxiliary Transformer Winding Temperature Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
AUXTF | dciAUXTF-ChargeFail:dac | DEIV | ChargeFail | CB Spring Charge Fail | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dciPOWTF-Trip:dac | DEIV | Trip | Press Relief Device Trip M1/M2 | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dciPOWTF-OltcTrip:dac | DEIV | OltcTrip | Press Relief Device OLTC Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dciPOWTF-HvCableBox:dac | DEIV | HvCableBox | Press Relief Device Trip HV Cable Box | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dciPOWTF-TempHvAlarm:dac | DEIV | TempHvAlarm | Winding Temp HV Alarm | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dciPOWTF-TempLvAlarm:dac | DEIV | TempLvAlarm | Winding Temp LV Alarm | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dciPOWTF-TempTrip:dac | DEIV | TempTrip | Oil Temperature Trip | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dciPOWTF-MainTank:dac | DEIV | MainTank | Buchholz Relay Trip - Main Tank | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dciPOWTF-Diverter:dac | DEIV | Diverter | Buchholz Relay Trip - Diverter Sw | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dciPOWTF-CblBox:dac | DEIV | CblBox | Buchholz Relay Trip - CBL Box HV | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dciPOWTF-Fail:dac | DEIV | Fail | AVR Relay Fail | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dciPOWTF-McbFail:dac | DEIV | McbFail | AVR DC Supply MCB Fail | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dciPOWTF-TapHigh:dac | DEIV | TapHigh | Tap Changer High Limit | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dciPOWTF-TapLow:dac | DEIV | TapLow | Tap Changer Low Limit | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dciPOWTF-TapOutStep:dac | DEIV | TapOutStep | Tap Changer Out of Step | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dciPOWTF-Incomplete:dac | DEIV | Incomplete | Tap Changer Incomplete | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dciPOWTF-ReleaseSts:dac | DEIV | ReleaseSts | AVR Block Release Status | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | aciPOWTF-WdgHv | AEIV | WdgHv | Wdg Temp Indicator (HV) | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | aciPOWTF-WdgLv | AEIV | WdgLv | Wdg Temp Indicator (LV) | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dioPOWTF-CmdBlock:dov1 | DEOV | CmdBlock | AVR Block/Release Command | $VOID | VES | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dioPOWTF-CmdBlock:dov2 | DEOV | CmdBlock | AVR Block/Release Command | $VOID | VES | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dioPOWTF-CmdAuto:dov1 | DEOV | CmdAuto | AVR Auto/Manual Command | $VOID | VES | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dioPOWTF-CmdAuto:dov2 | DEOV | CmdAuto | AVR Auto/Manual Command | $VOID | VES | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dioPOWTF-CmdRaise:dov1 | DEOV | CmdRaise | TAP Raise/Lower Command | $VOID | VES | _S0 | 0 |  |  |  | 4 |  |  | N
POWTF | dioPOWTF-CmdRaise:dov2 | DEOV | CmdRaise | TAP Raise/Lower Command | $VOID | VES | _S0 | 0 |  |  |  | 4 |  |  | N
BCA | dciBCA-ControlSts:dac | DEIV | ControlSts | Bay Control Status | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
BCA | dciBCA-CardSts:dac | DEIV | CardSts | BCU Card Status | $VOID | VEE | _S0 | 0 |  |  |  | 4 |  |  | N
Note on F1: HILDEBERT Rene: To be calculated from the instance List

## 4-External Variables - SIL0 (hidden)
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
CD_Prot | dciCDPROT-CbDfComSta:dac | DEIV | CbDfComSta | Cable Differential Protection Communication Status (channel 1&2) | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CD_Prot | dciCDPROT-CbDfPtSta:dac | DEIV | CbDfPtSta | Cable Differential Protection Trip Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CD_Prot | dciCDPROT-ItpRevSta:dac | DEIV | ItpRevSta | Intertrip Received Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CD_Prot | dciCDPROT-ItpStSta:dac | DEIV | ItpStSta | Intertrip Sent Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
LVAC_MDB | dciLVMDB-LvacDcStatus:dac | DEIV | LvacDcStatus | LVAC DC Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
LVAC_MDB | dciLVMDB-AcMcbSwgStatus:dac | DEIV | AcMcbSwgStatus | AC MCB Trip AC SWG Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
LVAC_MDB | dciLVMDB-LvacPlcStatus:dac | DEIV | LvacPlcStatus | LVAC PLC Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
LVAC_FEED | dciLVFD-FdLftBusStatus:dac | DEIV | FdLftBusStatus | LVAC Feeder Left Bus Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
LVAC_FEED | dciLVFD-FdRgtBusStatus:dac | DEIV | FdRgtBusStatus | LVAC Feeder Right Bus Satus | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
LVAC_FEED | dciLVFD-FdBus1Status:dac | DEIV | FdBus1Status | LVAC Feeder Bus1 Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
LVAC_FEED | dciLVFD-FdBus2Status:dac | DEIV | FdBus2Status | LVAC Feeder Bus2 Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
LVAC_FEED | dciLVFD-FdBus3Status:dac | DEIV | FdBus3Status | LVAC Feeder Bus3 Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
LVAC_INC | dciLVINC-IncTrpStatus:dac | DEIV | IncTrpStatus | LVAC Incomer Trip Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
LVAC_INC | dciLVINC-LvacStatus:dac | DEIV | LvacStatus | LVAC Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
SF6CB | dciSF6CB-CirBkPos:dac | DEIV | CirBkPos | Circuit Breaker Position | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
SF6CB | dciSF6CB-CbMtPort:dac | DEIV | CbMtPort | CB Motor Protection | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
SF6CB | dciSF6CB-CbMtRunTm:dac | DEIV | CbMtRunTm | CB Motor Run Time Supervision | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
SF6CB | dciSF6CB-CbMtVol:dac | DEIV | CbMtVol | CB Motor Voltage MCB Off/Trip | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
SF6CB | dioSF6CB-CmdOpen:dov1 | DEOV | CmdOpen | Circuit Breaker command OPEN | $VOID | VES | 0 |  |  |  | 4 |  |  | N
Feeder_Bay_CL | dciFDCL-AcrpLccStatus:dac | DEIV | AcrpLccStatus | AC RP/LCC Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
Feeder_Bay_CL | dciFDCL-DcAbRpStatus:dac | DEIV | DcAbRpStatus | DC AB/RP Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
Feeder_Bay_CL | dciFDCL-DcAfLccStatus:dac | DEIV | DcAfLccStatus | DC AF/LCC Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
Feeder_Bay_CL | dciFDCL-EndProtTripStatus:dac | DEIV | EndProtTripStatus | End Protection Trip Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
Feeder_Bay_CL | dciFDCL-PressureLvl1:dac | DEIV | PressureLvl1 | SF6 1st Stage Pressure Level | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
Feeder_Bay_CL | dciFDCL-PressureLvl2:dac | DEIV | PressureLvl2 | SF6 2nd Stage Pressure Level | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
Feeder_Bay_CL | dciFDCL-GisAnnunOpStatus:dac | DEIV | GisAnnunOpStatus | GIS Annunciator Operation Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
Feeder_Bay_CL | dciFDCL-ProtectMode:dac | DEIV | ProtectMode | OC/EF Protection Mode | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
Feeder_Bay_CL | dciFDCL-TherOvLdStatus:dac | DEIV | TherOvLdStatus | Thermal Overload Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
Feeder_Bay_CL | dciFDCL-ByPassStatus:dac | DEIV | ByPassStatus | Interlock By-Pass Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
Feeder_Bay_CL | dciFDCL-VoltTransStatus:dac | DEIV | VoltTransStatus | Voltage Transformer Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
Feeder_Bay_CL | dciFDCL-WdgIedStatus:dac | DEIV | WdgIedStatus | WatchDog IED's Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CMN_Bay | dciCMN-Bb1DcSupStatus:dac | DEIV | Bb1DcSupStatus | BB1 DC Supply Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CMN_Bay | dciCMN-AuxTransBlzTripSta:dac | DEIV | AuxTransBlzTripSta | Busbar CBF Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CMN_Bay | dciCMN-BusCbfProStab:dac | DEIV | BusCbfProStab | Busbar CBF-CTS Protection Stability | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CMN_Bay | dciCMN-BusBFOProMode:dac | DEIV | BusBFOProMode | Busbar BF-OUTPUT Protection Mode | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CMN_Bay | dciCMN-CbZoneProMode:dac | DEIV | CbZoneProMode | CB Zone Protection Mode | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BB_OST | dciBBOST-BusProZOpMode:dac | DEIV | BusProZOpMode | Busbar Protection Zone Operational Mode | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
VT | aciVT-VoltageMesure:aac | AEIV | VoltageMesure | Voltage Measurement | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BS_Bay | dciBS-AcrpLccStatus:dac | DEIV | AcrpLccStatus | AC RP/LCC Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BS_Bay | dciBS-DcAbRpStatus:dac | DEIV | DcAbRpStatus | DC AB/RP Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BS_Bay | dciBS-DcAfLccStatus:dac | DEIV | DcAfLccStatus | DC AF/LCC Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BS_Bay | dciBS-DcSec1LccStatus:dac | DEIV | DcSec1LccStatus | DC Section 1 AF/RP/LCC Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BS_Bay | dciBS-DcSec2LccStatus:dac | DEIV | DcSec2LccStatus | DC Section 2 AF/RP/LCC Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BS_Bay | dciBS-PressureLvl1:dac | DEIV | PressureLvl1 | SF6 1st Stage Pressure Level | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BS_Bay | dciBS-PressureLvl2:dac | DEIV | PressureLvl2 | SF6 2nd Stage Pressure Level | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BS_Bay | dciBS-GisAnnunOpStatus:dac | DEIV | GisAnnunOpStatus | GIS Annunciator Operation Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BS_Bay | dciBS-ProtectMode:dac | DEIV | ProtectMode | OC/EF Protection Mode | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BS_Bay | dciBS-ByPassStatus:dac | DEIV | ByPassStatus | Interlock By-Pass Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BS_Bay | dciBS-SyncChkStatus:dac | DEIV | SyncChkStatus | Synchronity Check Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BS_Bay | dciBS-VoltTransStatus:dac | DEIV | VoltTransStatus | Voltage Transformer Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BS_Bay | dciBS-WdgIedStatus:dac | DEIV | WdgIedStatus | WatchDog IED's Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
XF_AUX | dciXFAUX-ATBuchholz:dac | DEIV | ATBuchholz | Auxiliary Transformer Buchholz Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
XF_AUX | dciXFAUX-ATBlzTrip:dac | DEIV | ATBlzTrip | Auxiliary Transformer Buchholz Trip Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
XF_AUX | dciXFAUX-ATOCEF:dac | DEIV | ATOCEF | Auxiliary Transformer O/C & E/F Mode | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
XF_AUX | dciXFAUX-ATOilLv:dac | DEIV | ATOilLv | Auxiliary Transformer Oil Level | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
XF_AUX | dciXFAUX-ATOilTempLv:dac | DEIV | ATOilTempLv | Auxiliary Transformer Oil Temperature Level | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
XF_AUX | dciXFAUX-ATOilTempTrip:dac | DEIV | ATOilTempTrip | Auxiliary Transformer Oil Temp Trip Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
XF_AUX | dciXFAUX-ATPrsRelief:dac | DEIV | ATPrsRelief | Auxiliary Transformer Pressure Relief Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
XF_AUX | dciXFAUX-ATWindTemp:dac | DEIV | ATWindTemp | Auxilary Transformer Winding Temperature Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
XF_AUX | dciXFAUX-ATWindTempTrip:dac | DEIV | ATWindTempTrip | Auxilary Transformer Winding Temperature Trip Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
XF_AUX | dciXFAUX-REFProtMode:dac | DEIV | REFProtMode | REF Protection Mode | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
XF_AUX | dciXFAUX-SpringCharge:dac | DEIV | SpringCharge | Spring Charge Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
XF_AUX | dciXFAUX-VoltTrans:dac | DEIV | VoltTrans | Voltage Transformer Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
XF_AUX | dciXFAUX-WtdgBCUFO:dac | DEIV | WtdgBCUFO | WatchDog BCU/FO Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
XF_AUX | dciXFAUX-WtdgIED:dac | DEIV | WtdgIED | WatchDog IED's Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
XF_AUX | dciXFAUX-FullLoadLv:dac | DEIV | FullLoadLv | Transformer Full Load Level | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CB | dioCB-CmdOpen:dov1 | DEOV | CmdOpen | Circuit Breaker Control | $VOID | VES | 0 |  |  |  | 4 |  |  | N
CB_Prot | dciCBPROT-CbProtecMode1:dac | DEIV | CbProtecMode1 | Circuit Breaker 1st Stage Protection Mode | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CB_Prot | dciCBPROT-CbProtecMode2:dac | DEIV | CbProtecMode2 | Circuit Breaker 2nd Stage Protection Mode | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CB_Prot | dciCBPROT-CbPressureLvl1:dac | DEIV | CbPressureLvl1 | CB Compartment 1st Stage Pressure Level | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CB_Prot | dciCBPROT-CbPressureLvl2:dac | DEIV | CbPressureLvl2 | CB Compartment 2nd Stage Pressure Level | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CB_Prot | dciCBPROT-CbLockStatus:dac | DEIV | CbLockStatus | Circuit Breaker Lock Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
PM | aciPM-ActivePwr:aac | AEIV | ActivePwr | Active Power | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
PM | aciPM-ReactivePwr:aac | AEIV | ReactivePwr | Reactive Power | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CT | aciCT-CtCurMet:aac | AEIV | CtCurMet | Current Measurement | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BIS | dioBIS-CmdOpen:dov1 | DEOV | CmdOpen | Bus Isolator Control OPEN | $VOID | VES | 0 |  |  |  | 4 |  |  | N
VTIS | dciVTIS-CirbreakerStatus:dac | DEIV | CirbreakerStatus | Circuit Breaker Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
GTW | dciGTW-GTWConStatus:dac | DEIV | GTWConStatus | Connection Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
Note on F1: HILDEBERT Rene: To be calculated from the instance List

## 4-External Variables - SIL2MON (hidden)
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
CB_OST | dciCBOST-CirbreakerStatus:dac | DEIV | CirbreakerStatus | Circuit Breaker Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
WTDG | aciWTDG-WdCounter:aac | AEIV | WdCounter | Watchdog Counter | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
Feeder_Bay_CL | dciFDCL-MstrTrpRyMode:dac | DEIV | MstrTrpRyMode | Master Trip Relay Mode | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
Feeder_Bay_CL | dciFDCL-TripCtStatus:dac | DEIV | TripCtStatus | Trip Circuit Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
Feeder_Bay_CL | dciFDCL-WdgBcuStatus:dac | DEIV | WdgBcuStatus | WatchDog BCU/FO Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CMN_Bay | dciCMN-WdogRelBcuFoSt:dac | DEIV | WdogRelBcuFoSt | WatchDog RELAY/BCU/FO Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BS_Bay | dciBS-MstrTrpRyMode:dac | DEIV | MstrTrpRyMode | Master Trip Relay Mode | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BS_Bay | dciBS-TripCtStatus:dac | DEIV | TripCtStatus | Trip Circuit Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BS_Bay | dciBS-WdgBcuStatus:dac | DEIV | WdgBcuStatus | WatchDog BCU/FO Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CB | dciCB-CirbreakerStatus:dac | DEIV | CirbreakerStatus | Circuit Breaker Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CB_Prot | dciCBPROT-CbDriveStatus:dac | DEIV | CbDriveStatus | Circuit Breaker Drive Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CB_Prot | dciCBPROT-CbControlMode:dac | DEIV | CbControlMode | Circuit Breaker Control Mode | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CB_Prot | dciCBPROT-CbStatus:dac | DEIV | CbStatus | Circuit breaker Not Ready | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BIS | dciBIS-BusIsolatorStatus:dac | DEIV | BusIsolatorStatus | Bus Isolator Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
ES | dciES-EsStatus:dac | DEIV | EsStatus | Bus Isolator Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
Note on F1: HILDEBERT Rene: To be calculated from the instance List

## 4-External Variables - SIL2CON (hidden)
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
SF6CB | dioSF6CB-CmdExeClose:dov1 | DEOV | CmdExeClose | Circuit Breaker command CLOSE | $VOID | VES | 0 |  |  |  | 4 |  |  | N
SF6CB | dioSF6CB-CmdSelClose:dov1 | DEOV | CmdSelClose | Circuit Breaker command Select CLOSE | $VOID | VES | 0 |  |  |  | 4 |  |  | N
SF6CB | dciSF6CB-AckSelClose:dac | DEIV | AckSelClose | Circuit Breaker command Select CLOSE Ack | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
SF6CB | dciSF6CB-AckExeClose:dac | DEIV | AckExeClose | Circuit Breaker command Execute CLOSE Ack | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BIS | dioBIS-CmdExeClose:dov1 | DEOV | CmdExeClose | Bus Isolator Control CLOSE | $VOID | VES | 0 |  |  |  | 4 |  |  | N
BIS | dioBIS-CmdSelClose:dov1 | DEOV | CmdSelClose | Bus Isolator Control Select CLOSE | $VOID | VES | 0 |  |  |  | 4 |  |  | N
BIS | dciBIS-AckSelClose:dac | DEIV | AckSelClose | Bus Isolator Control Select CLOSE Ack | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
BIS | dciBIS-AckExeClose:dac | DEIV | AckExeClose | Bus Isolator Control Execute CLOSE Ack | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CB | dioCB-CmdExeClose:dov1 | DEOV | CmdExeClose | Circuit Breaker Control CLOSE | $VOID | VES | 0 |  |  |  | 4 |  |  | N
CB | dioCB-CmdSelClose:dov1 | DEOV | CmdSelClose | Circuit Breaker Control Select CLOSE | $VOID | VES | 0 |  |  |  | 4 |  |  | N
CB | dciCB-AckSelClose:dac | DEIV | AckSelClose | Circuit Breaker Control Select CLOSE Ack | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
CB | dciCB-AckExeClose:dac | DEIV | AckExeClose | Circuit Breaker Control Execute CLOSE Ack | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
Note on F1: HILDEBERT Rene: To be calculated from the instance List

## 10-PLC Points
row_id | concentrator | location | sub_location | class_name | eqp_name | instance_id | attribute_code | sil_channel | operation_type | point_address | start_bit | nb_bits | Warning | Error | PRTU Name | SWC Name | Daccom Source File | Daccom Variable Type | FC Code / ASDU Type | Daccom Type Num | Protocol Address | Start Bit | Nb Bits | Daccom External Variable Name | field1 | field2 | field3 | field4 | field5 | External Var Comment
1 | BPS01_RTU | PWR:BPS:CL | BPS01 | GTW | GTW1 | 1 | GTWConStatus | SIL0 | IEC104:M_SP_NA_1 | 1041 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1041 | 0 | 1 | deiPWRBPSCLBPS01GTW1GTWConStatus | 4 |  |  | 0 | $ComStatus , , | #[GTW]: Connection Status
2 | BPS01_RTU | PWR:BPS:CL | BPS01 | GTW | GTW2 | 2 | GTWConStatus | SIL0 | IEC104:M_SP_NA_1 | 1081 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1081 | 0 | 1 | deiPWRBPSCLBPS01GTW2GTWConStatus | 4 |  |  | 0 | $ComStatus , , | #[GTW]: Connection Status
3 | BPS01_RTU | PWR:BPS:CL |  | WTDG | WTDG_GTW1 | 3 | WdCounter | SIL2_Monitoring | IEC104:M_ME_NB_1 | 10121 | 0 | 16 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | AEIV | M_ME_NB | 1 | 10121 | 0 | 16 | aeiPWRBPSCLWTDG_GTW1WdCounter | 4 |  |  | 0 | $ComStatus , , | #Watchdog Counter for SIL2
4 | BPS01_RTU | PWR:BPS:CL |  | WTDG | WTDG_GTW2 | 4 | WdCounter | SIL2_Monitoring | IEC104:M_ME_NB_1 | 10161 | 0 | 16 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | AEIV | M_ME_NB | 1 | 10161 | 0 | 16 | aeiPWRBPSCLWTDG_GTW2WdCounter | 4 |  |  | 0 | $ComStatus , , | #Watchdog Counter for SIL2
5 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBAL | BBAL_66KV | 5 | BBPOutofServ | SIL0 | IEC104:M_SP_NA_1 | 1200 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1200 | 0 | 1 | deiPWRBPSCL66KVBBBBAL_66KVBBPOutofServ | 4 |  |  | 0 | $ComStatus , , | #[BPOS] : Busbar Protection Out of Service
6 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBAL | BBAL_66KV | 5 | BBPDisturbed | SIL0 | IEC104:M_SP_NA_1 | 1201 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1201 | 0 | 1 | deiPWRBPSCL66KVBBBBAL_66KVBBPDisturbed | 4 |  |  | 0 | $ComStatus , , | #[BPU1] : Busbar Protection Disturbed
7 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBAL | BBAL_66KV | 5 | BBPAllProtBlocked | SIL0 | IEC104:M_SP_NA_1 | 1202 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1202 | 0 | 1 | deiPWRBPSCL66KVBBBBAL_66KVBBPAllProtBlocked | 4 |  |  | 0 | $ComStatus , , | #[BBPB] : All Protection Blocked
8 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBAL | BBAL_66KV | 5 | CBFailS2M1Mode | SIL0 | IEC104:M_SP_NA_1 | 1203 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1203 | 0 | 1 | deiPWRBPSCL66KVBBBBAL_66KVCBFailS2M1Mode | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : CB Failure Stage 2 M1 Zone
9 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBAL | BBAL_66KV | 5 | CBFailS2M2Mode | SIL0 | IEC104:M_SP_NA_1 | 1204 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1204 | 0 | 1 | deiPWRBPSCL66KVBBBBAL_66KVCBFailS2M2Mode | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : CB Failure Stage 2 M2 Zone
10 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBAL | BBAL_66KV | 5 | BrkFailOperated | SIL2_Monitoring | IEC104:M_SP_NA_1 | 1205 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 1205 | 0 | 1 | deiPWRBPSCL66KVBBBBAL_66KVBrkFailOperated | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Operated
11 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBAL | BBAL_66KV | 5 | BBPM1Out | SIL0 | IEC104:M_SP_NA_1 | 1206 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1206 | 0 | 1 | deiPWRBPSCL66KVBBBBAL_66KVBBPM1Out | 4 |  |  | 0 | $ComStatus , , | #[BPU1] Busbar Protection M1 Zone
12 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBAL | BBAL_66KV | 5 | BBPM2Out | SIL0 | IEC104:M_SP_NA_1 | 1207 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1207 | 0 | 1 | deiPWRBPSCL66KVBBBBAL_66KVBBPM2Out | 4 |  |  | 0 | $ComStatus , , | #[BPU1] Busbar Protection M2 Zone
13 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBAL | BBAL_66KV | 5 | BusProZOpMode1 | SIL0 | IEC104:M_SP_NA_1 | 1208 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1208 | 0 | 1 | deiPWRBPSCL66KVBBBBAL_66KVBusProZOpMode1 | 4 |  |  | 0 | $ComStatus , , | #[BPU1] Busbar Protection Blocked M1 Zone
14 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBAL | BBAL_66KV | 5 | BusProZOpMode2 | SIL0 | IEC104:M_SP_NA_1 | 1209 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1209 | 0 | 1 | deiPWRBPSCL66KVBBBBAL_66KVBusProZOpMode2 | 4 |  |  | 0 | $ComStatus , , | #[BPU1] Busbar Protection Blocked M2 Zone
15 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBPZ | BBPZ_66KV | 6 | BBPM1Trip | SIL0 | IEC104:M_SP_NA_1 | 1240 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1240 | 0 | 1 | deiPWRBPSCL66KVBBBBPZ_66KVBBPM1Trip | 4 |  |  | 0 | $ComStatus , , | #[BM1O] Busbar Protection M1 Trip
16 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBPZ | BBPZ_66KV | 6 | BBPM2Trip | SIL0 | IEC104:M_SP_NA_1 | 1241 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1241 | 0 | 1 | deiPWRBPSCL66KVBBBBPZ_66KVBBPM2Trip | 4 |  |  | 0 | $ComStatus , , | #[BM2O] Busbar Protection M2 Trip
17 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBPZ | BBPZ_66KV | 6 | BBProtOperated | SIL0 | IEC104:M_SP_NA_1 | 1242 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1242 | 0 | 1 | deiPWRBPSCL66KVBBBBPZ_66KVBBProtOperated | 4 |  |  | 0 | $ComStatus , , | #[CBFO] Busbar Protection Operated
18 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBPR | BBPR_B10 | 7 | BrkFailStage1 | SIL0 | IEC104:M_SP_NA_1 | 1280 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1280 | 0 | 1 | deiPWRBPSCL66KVBBBBPR_B10BrkFailStage1 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-1 Operated
19 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBPR | BBPR_B10 | 7 | BrkFailStage2 | SIL0 | IEC104:M_SP_NA_1 | 1281 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1281 | 0 | 1 | deiPWRBPSCL66KVBBBBPR_B10BrkFailStage2 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-2 Operated
20 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBPR | BBPR_B20 | 8 | BrkFailStage1 | SIL0 | IEC104:M_SP_NA_1 | 1320 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1320 | 0 | 1 | deiPWRBPSCL66KVBBBBPR_B20BrkFailStage1 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-1 Operated
21 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBPR | BBPR_B20 | 8 | BrkFailStage2 | SIL0 | IEC104:M_SP_NA_1 | 1321 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1321 | 0 | 1 | deiPWRBPSCL66KVBBBBPR_B20BrkFailStage2 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-2 Operated
22 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBPR | BBPR_B11 | 9 | BrkFailStage1 | SIL0 | IEC104:M_SP_NA_1 | 1360 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1360 | 0 | 1 | deiPWRBPSCL66KVBBBBPR_B11BrkFailStage1 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-1 Operated
23 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBPR | BBPR_B11 | 9 | BrkFailStage2 | SIL0 | IEC104:M_SP_NA_1 | 1361 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1361 | 0 | 1 | deiPWRBPSCL66KVBBBBPR_B11BrkFailStage2 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-2 Operated
24 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBPR | BBPR_B21 | 10 | BrkFailStage1 | SIL0 | IEC104:M_SP_NA_1 | 1400 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1400 | 0 | 1 | deiPWRBPSCL66KVBBBBPR_B21BrkFailStage1 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-1 Operated
25 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BBPR | BBPR_B21 | 10 | BrkFailStage2 | SIL0 | IEC104:M_SP_NA_1 | 1401 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1401 | 0 | 1 | deiPWRBPSCL66KVBBBBPR_B21BrkFailStage2 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-2 Operated
26 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BSCP | BSCP_B12 | 11 | BrkFailS1M1Op | SIL0 | IEC104:M_SP_NA_1 | 1440 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1440 | 0 | 1 | deiPWRBPSCL66KVBBBSCP_B12BrkFailS1M1Op | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-1 Operated - M1
27 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BSCP | BSCP_B12 | 11 | BrkFailS2M1Op | SIL0 | IEC104:M_SP_NA_1 | 1441 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1441 | 0 | 1 | deiPWRBPSCL66KVBBBSCP_B12BrkFailS2M1Op | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-2 Operated - M1
28 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BSCP | BSCP_B12 | 11 | BrkFailS1M2Op | SIL0 | IEC104:M_SP_NA_1 | 1442 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1442 | 0 | 1 | deiPWRBPSCL66KVBBBSCP_B12BrkFailS1M2Op | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-1 Operated - M2
29 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BSCP | BSCP_B12 | 11 | BrkFailS2M2Op | SIL0 | IEC104:M_SP_NA_1 | 1443 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1443 | 0 | 1 | deiPWRBPSCL66KVBBBSCP_B12BrkFailS2M2Op | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-2 Operated - M2
30 | BPS01_RTU | PWR:BPS:CL | 66KVBB | 66KVVM | VM_B166VT | 12 | VoltageMesure | SIL0 | IEC104:M_ME_NA_1 | 7480 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7480 | 0 | 16 | aeiPWRBPSCL66KVBBVM_B166VTVoltageMesure | 4 |  |  | 0 | $ComStatus , , | #Voltage Measurement
31 | BPS01_RTU | PWR:BPS:CL | 66KVBB | 66KVVM | VM_B266VT | 13 | VoltageMesure | SIL0 | IEC104:M_ME_NA_1 | 7520 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7520 | 0 | 16 | aeiPWRBPSCL66KVBBVM_B266VTVoltageMesure | 4 |  |  | 0 | $ComStatus , , | #Voltage Measurement
32 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFBA | 66KVIFBA_B10 | 14 | ACFailRPLcc | SIL0 | IEC104:M_SP_NA_1 | 1560 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1560 | 0 | 1 | deiPWRBPSCLB1066KVIFBA_B10ACFailRPLcc | 4 |  |  | 0 | $ComStatus , , | #[ACFL] : AC Fail Relay Panel / LCC
33 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFBA | 66KVIFBA_B10 | 14 | DCFailRP | SIL0 | IEC104:M_SP_NA_1 | 1561 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1561 | 0 | 1 | deiPWRBPSCLB1066KVIFBA_B10DCFailRP | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : DC Fail Relay Panel
34 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFBA | 66KVIFBA_B10 | 14 | DCFailLcc | SIL0 | IEC104:M_SP_NA_1 | 1562 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1562 | 0 | 1 | deiPWRBPSCLB1066KVIFBA_B10DCFailLcc | 4 |  |  | 0 | $ComStatus , , | #[DCFA] : DC Fail LCC
35 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFBA | 66KVIFBA_B10 | 14 | GasPressureSt1 | SIL0 | IEC104:M_SP_NA_1 | 1563 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1563 | 0 | 1 | deiPWRBPSCLB1066KVIFBA_B10GasPressureSt1 | 4 |  |  | 0 | $ComStatus , , | #[GAS1] : Gas Pressure Stage 1
36 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFBA | 66KVIFBA_B10 | 14 | GasPressureSt2 | SIL0 | IEC104:M_SP_NA_1 | 1564 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1564 | 0 | 1 | deiPWRBPSCLB1066KVIFBA_B10GasPressureSt2 | 4 |  |  | 0 | $ComStatus , , | #[GAS2] : Gas Pressure Stage 2
37 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFBA | 66KVIFBA_B10 | 14 | MstrTrpRyOp | SIL2_Monitoring | IEC104:M_SP_NA_1 | 1565 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 1565 | 0 | 1 | deiPWRBPSCLB1066KVIFBA_B10MstrTrpRyOp | 4 |  |  | 0 | $ComStatus , , | #[MTRO] : Master Trip relay operated
38 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFBA | 66KVIFBA_B10 | 14 | WdgIedStatus | SIL0 | IEC104:M_SP_NA_1 | 1566 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1566 | 0 | 1 | deiPWRBPSCLB1066KVIFBA_B10WdgIedStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : IED WatchDog
39 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFBA | 66KVIFBA_B10 | 14 | WdgBcuStatus | SIL2_Monitoring | IEC104:M_SP_NA_1 | 1567 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 1567 | 0 | 1 | deiPWRBPSCLB1066KVIFBA_B10WdgBcuStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Watchdog
40 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFBA | 66KVIFBA_B10 | 14 | VTFuseFail | SIL0 | IEC104:M_SP_NA_1 | 1568 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1568 | 0 | 1 | deiPWRBPSCLB1066KVIFBA_B10VTFuseFail | 4 |  |  | 0 | $ComStatus , , | #[VTFA] : Voltage Transformer Fuse Fail
41 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFBA | 66KVIFBA_B10 | 14 | TherOvLdAlarm | SIL0 | IEC104:M_SP_NA_1 | 1569 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1569 | 0 | 1 | deiPWRBPSCLB1066KVIFBA_B10TherOvLdAlarm | 4 |  |  | 0 | $ComStatus , , | #[QAFA] : Thermal over load Alarm
42 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFBA | 66KVIFBA_B10 | 14 | BCUCardFail | SIL0 | IEC104:M_SP_NA_1 | 1570 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1570 | 0 | 1 | deiPWRBPSCLB1066KVIFBA_B10BCUCardFail | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Card Fail
43 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFBA | 66KVIFBA_B20 | 15 | ACFailRPLcc | SIL0 | IEC104:M_SP_NA_1 | 1600 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1600 | 0 | 1 | deiPWRBPSCLB2066KVIFBA_B20ACFailRPLcc | 4 |  |  | 0 | $ComStatus , , | #[ACFL] : AC Fail Relay Panel / LCC
44 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFBA | 66KVIFBA_B20 | 15 | DCFailRP | SIL0 | IEC104:M_SP_NA_1 | 1601 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1601 | 0 | 1 | deiPWRBPSCLB2066KVIFBA_B20DCFailRP | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : DC Fail Relay Panel
45 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFBA | 66KVIFBA_B20 | 15 | DCFailLcc | SIL0 | IEC104:M_SP_NA_1 | 1602 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1602 | 0 | 1 | deiPWRBPSCLB2066KVIFBA_B20DCFailLcc | 4 |  |  | 0 | $ComStatus , , | #[DCFA] : DC Fail LCC
46 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFBA | 66KVIFBA_B20 | 15 | GasPressureSt1 | SIL0 | IEC104:M_SP_NA_1 | 1603 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1603 | 0 | 1 | deiPWRBPSCLB2066KVIFBA_B20GasPressureSt1 | 4 |  |  | 0 | $ComStatus , , | #[GAS1] : Gas Pressure Stage 1
47 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFBA | 66KVIFBA_B20 | 15 | GasPressureSt2 | SIL0 | IEC104:M_SP_NA_1 | 1604 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1604 | 0 | 1 | deiPWRBPSCLB2066KVIFBA_B20GasPressureSt2 | 4 |  |  | 0 | $ComStatus , , | #[GAS2] : Gas Pressure Stage 2
48 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFBA | 66KVIFBA_B20 | 15 | MstrTrpRyOp | SIL2_Monitoring | IEC104:M_SP_NA_1 | 1605 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 1605 | 0 | 1 | deiPWRBPSCLB2066KVIFBA_B20MstrTrpRyOp | 4 |  |  | 0 | $ComStatus , , | #[MTRO] : Master Trip relay operated
49 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFBA | 66KVIFBA_B20 | 15 | WdgIedStatus | SIL0 | IEC104:M_SP_NA_1 | 1606 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1606 | 0 | 1 | deiPWRBPSCLB2066KVIFBA_B20WdgIedStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : IED WatchDog
50 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFBA | 66KVIFBA_B20 | 15 | WdgBcuStatus | SIL2_Monitoring | IEC104:M_SP_NA_1 | 1607 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 1607 | 0 | 1 | deiPWRBPSCLB2066KVIFBA_B20WdgBcuStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Watchdog
51 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFBA | 66KVIFBA_B20 | 15 | VTFuseFail | SIL0 | IEC104:M_SP_NA_1 | 1608 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1608 | 0 | 1 | deiPWRBPSCLB2066KVIFBA_B20VTFuseFail | 4 |  |  | 0 | $ComStatus , , | #[VTFA] : Voltage Transformer Fuse Fail
52 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFBA | 66KVIFBA_B20 | 15 | TherOvLdAlarm | SIL0 | IEC104:M_SP_NA_1 | 1609 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1609 | 0 | 1 | deiPWRBPSCLB2066KVIFBA_B20TherOvLdAlarm | 4 |  |  | 0 | $ComStatus , , | #[QAFA] : Thermal over load Alarm
53 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFBA | 66KVIFBA_B20 | 15 | BCUCardFail | SIL0 | IEC104:M_SP_NA_1 | 1610 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 1610 | 0 | 1 | deiPWRBPSCLB2066KVIFBA_B20BCUCardFail | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Card Fail
54 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFMV | 66KVIFMV_B10 | 16 | RPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 7640 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7640 | 0 | 16 | aeiPWRBPSCLB1066KVIFMV_B10RPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #R Phase Current
55 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFMV | 66KVIFMV_B10 | 16 | YPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 7641 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7641 | 0 | 16 | aeiPWRBPSCLB1066KVIFMV_B10YPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #Y Phase Current
56 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFMV | 66KVIFMV_B10 | 16 | BPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 7642 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7642 | 0 | 16 | aeiPWRBPSCLB1066KVIFMV_B10BPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #B Phase Current
57 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFMV | 66KVIFMV_B10 | 16 | NeutralCur | SIL0 | IEC104:M_ME_NA_1 | 7643 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7643 | 0 | 16 | aeiPWRBPSCLB1066KVIFMV_B10NeutralCur | 4 |  |  | 0 | $ComStatus , , | #Neutral Current (In)
58 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFMV | 66KVIFMV_B10 | 16 | RYPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 7644 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7644 | 0 | 16 | aeiPWRBPSCLB1066KVIFMV_B10RYPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #RY Phase Voltage
59 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFMV | 66KVIFMV_B10 | 16 | YBPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 7645 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7645 | 0 | 16 | aeiPWRBPSCLB1066KVIFMV_B10YBPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #YB Phase Voltage
60 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFMV | 66KVIFMV_B10 | 16 | BRPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 7646 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7646 | 0 | 16 | aeiPWRBPSCLB1066KVIFMV_B10BRPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #BR Phase Voltage
61 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFMV | 66KVIFMV_B10 | 16 | ZeroSeqVolt | SIL0 | IEC104:M_ME_NA_1 | 7647 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7647 | 0 | 16 | aeiPWRBPSCLB1066KVIFMV_B10ZeroSeqVolt | 4 |  |  | 0 | $ComStatus , , | #Zero Sequence Voltage (V0)
62 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFMV | 66KVIFMV_B10 | 16 | ActivePower | SIL0 | IEC104:M_ME_NA_1 | 7648 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7648 | 0 | 16 | aeiPWRBPSCLB1066KVIFMV_B10ActivePower | 4 |  |  | 0 | $ComStatus , , | #[MW] : Active Power
63 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFMV | 66KVIFMV_B10 | 16 | ReacPower | SIL0 | IEC104:M_ME_NA_1 | 7649 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7649 | 0 | 16 | aeiPWRBPSCLB1066KVIFMV_B10ReacPower | 4 |  |  | 0 | $ComStatus , , | #[MVAR] : Reactive Power
64 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFMV | 66KVIFMV_B10 | 16 | AppPower | SIL0 | IEC104:M_ME_NA_1 | 7650 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7650 | 0 | 16 | aeiPWRBPSCLB1066KVIFMV_B10AppPower | 4 |  |  | 0 | $ComStatus , , | #Apparent Power
65 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFMV | 66KVIFMV_B10 | 16 | PowerFactor | SIL0 | IEC104:M_ME_NA_1 | 7651 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7651 | 0 | 16 | aeiPWRBPSCLB1066KVIFMV_B10PowerFactor | 4 |  |  | 0 | $ComStatus , , | #Power Factor
66 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFMV | 66KVIFMV_B10 | 16 | Frequency | SIL0 | IEC104:M_ME_NA_1 | 7652 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7652 | 0 | 16 | aeiPWRBPSCLB1066KVIFMV_B10Frequency | 4 |  |  | 0 | $ComStatus , , | #Frequency
67 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFMV | 66KVIFMV_B20 | 17 | RPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 7680 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7680 | 0 | 16 | aeiPWRBPSCLB2066KVIFMV_B20RPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #R Phase Current
68 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFMV | 66KVIFMV_B20 | 17 | YPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 7681 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7681 | 0 | 16 | aeiPWRBPSCLB2066KVIFMV_B20YPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #Y Phase Current
69 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFMV | 66KVIFMV_B20 | 17 | BPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 7682 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7682 | 0 | 16 | aeiPWRBPSCLB2066KVIFMV_B20BPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #B Phase Current
70 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFMV | 66KVIFMV_B20 | 17 | NeutralCur | SIL0 | IEC104:M_ME_NA_1 | 7683 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7683 | 0 | 16 | aeiPWRBPSCLB2066KVIFMV_B20NeutralCur | 4 |  |  | 0 | $ComStatus , , | #Neutral Current (In)
71 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFMV | 66KVIFMV_B20 | 17 | RYPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 7684 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7684 | 0 | 16 | aeiPWRBPSCLB2066KVIFMV_B20RYPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #RY Phase Voltage
72 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFMV | 66KVIFMV_B20 | 17 | YBPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 7685 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7685 | 0 | 16 | aeiPWRBPSCLB2066KVIFMV_B20YBPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #YB Phase Voltage
73 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFMV | 66KVIFMV_B20 | 17 | BRPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 7686 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7686 | 0 | 16 | aeiPWRBPSCLB2066KVIFMV_B20BRPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #BR Phase Voltage
74 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFMV | 66KVIFMV_B20 | 17 | ZeroSeqVolt | SIL0 | IEC104:M_ME_NA_1 | 7687 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7687 | 0 | 16 | aeiPWRBPSCLB2066KVIFMV_B20ZeroSeqVolt | 4 |  |  | 0 | $ComStatus , , | #Zero Sequence Voltage (V0)
75 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFMV | 66KVIFMV_B20 | 17 | ActivePower | SIL0 | IEC104:M_ME_NA_1 | 7688 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7688 | 0 | 16 | aeiPWRBPSCLB2066KVIFMV_B20ActivePower | 4 |  |  | 0 | $ComStatus , , | #[MW] : Active Power
76 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFMV | 66KVIFMV_B20 | 17 | ReacPower | SIL0 | IEC104:M_ME_NA_1 | 7689 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7689 | 0 | 16 | aeiPWRBPSCLB2066KVIFMV_B20ReacPower | 4 |  |  | 0 | $ComStatus , , | #[MVAR] : Reactive Power
77 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFMV | 66KVIFMV_B20 | 17 | AppPower | SIL0 | IEC104:M_ME_NA_1 | 7690 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7690 | 0 | 16 | aeiPWRBPSCLB2066KVIFMV_B20AppPower | 4 |  |  | 0 | $ComStatus , , | #Apparent Power
78 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFMV | 66KVIFMV_B20 | 17 | PowerFactor | SIL0 | IEC104:M_ME_NA_1 | 7691 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7691 | 0 | 16 | aeiPWRBPSCLB2066KVIFMV_B20PowerFactor | 4 |  |  | 0 | $ComStatus , , | #Power Factor
79 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFMV | 66KVIFMV_B20 | 17 | Frequency | SIL0 | IEC104:M_ME_NA_1 | 7692 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 7692 | 0 | 16 | aeiPWRBPSCLB2066KVIFMV_B20Frequency | 4 |  |  | 0 | $ComStatus , , | #Frequency
80 | BPS01_RTU | PWR:BPS:CL | B10 | VTIS | B1064 | 18 | IsolPosition | SIL2_Monitoring | IEC104:M_DP_NA_1 | 4360 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 4360 | 0 | 2 | deiPWRBPSCLB10B1064IsolPosition | 4 |  |  | 0 | $ComStatus , , | #VT Isolator Position
81 | BPS01_RTU | PWR:BPS:CL | B20 | VTIS | B2064 | 19 | IsolPosition | SIL2_Monitoring | IEC104:M_DP_NA_1 | 4380 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 4380 | 0 | 2 | deiPWRBPSCLB20B2064IsolPosition | 4 |  |  | 0 | $ComStatus , , | #VT Isolator Position
82 | BPS01_RTU | PWR:BPS:CL | B10 | CB_OST | B100 | 20 | CbPositionM | SIL2_Monitoring | IEC104:M_DP_NA_1 | 4400 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 4400 | 0 | 2 | deiPWRBPSCLB10B100CbPositionM | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Status
83 | BPS01_RTU | PWR:BPS:CL | B20 | CB_OST | B200 | 21 | CbPositionM | SIL2_Monitoring | IEC104:M_DP_NA_1 | 4420 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 4420 | 0 | 2 | deiPWRBPSCLB20B200CbPositionM | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Status
84 | BPS01_RTU | PWR:BPS:CL | B10 | ESSM | B101 | 22 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 4440 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 4440 | 0 | 2 | deiPWRBPSCLB10B101EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
85 | BPS01_RTU | PWR:BPS:CL | B20 | ESSM | B201 | 23 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 4460 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 4460 | 0 | 2 | deiPWRBPSCLB20B201EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
86 | BPS01_RTU | PWR:BPS:CL | B10 | BIST | BIST_B103 | 24 | BusIsolPosM | SIL2_Monitoring | IEC104:M_DP_NA_1 | 4480 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 4480 | 0 | 2 | deiPWRBPSCLB10BIST_B103BusIsolPosM | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
87 | BPS01_RTU | PWR:BPS:CL | B20 | BIST | BIST_B203 | 25 | BusIsolPosM | SIL2_Monitoring | IEC104:M_DP_NA_1 | 4500 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 4500 | 0 | 2 | deiPWRBPSCLB20BIST_B203BusIsolPosM | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
88 | BPS01_RTU | PWR:BPS:CL | B10 | BIST | BIST_B104 | 26 | BusIsolPosM | SIL2_Monitoring | IEC104:M_DP_NA_1 | 4520 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 4520 | 0 | 2 | deiPWRBPSCLB10BIST_B104BusIsolPosM | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
89 | BPS01_RTU | PWR:BPS:CL | B20 | BIST | BIST_B204 | 27 | BusIsolPosM | SIL2_Monitoring | IEC104:M_DP_NA_1 | 4540 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 4540 | 0 | 2 | deiPWRBPSCLB20BIST_B204BusIsolPosM | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
90 | BPS01_RTU | PWR:BPS:CL | B10 | ESSM | B10M2 | 28 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 4560 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 4560 | 0 | 2 | deiPWRBPSCLB10B10M2EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
91 | BPS01_RTU | PWR:BPS:CL | B20 | ESSM | B20M2 | 29 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 4580 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 4580 | 0 | 2 | deiPWRBPSCLB20B20M2EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
92 | BPS01_RTU | PWR:BPS:CL | B10 | ESSM | B10M1 | 30 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 4600 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 4600 | 0 | 2 | deiPWRBPSCLB10B10M1EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
93 | BPS01_RTU | PWR:BPS:CL | B20 | ESSM | B20M1 | 31 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 4620 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 4620 | 0 | 2 | deiPWRBPSCLB20B20M1EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
94 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main1 | 32 | T11DCSupplyFail | SIL0 | IEC104:M_SP_NA_1 | 2280 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2280 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main1T11DCSupplyFail | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : T11 DC Supply Fail
95 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main1 | 32 | T21DCSupplyFail | SIL0 | IEC104:M_SP_NA_1 | 2281 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2281 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main1T21DCSupplyFail | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : T12 DC Supply Fail
96 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main1 | 32 | FOC1Fail | SIL0 | IEC104:M_SP_NA_1 | 2282 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2282 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main1FOC1Fail | 4 |  |  | 0 | $ComStatus , , | #[CDFA] : Diff Communication Fail Ch-1
97 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main1 | 32 | FOC2Fail | SIL0 | IEC104:M_SP_NA_1 | 2283 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2283 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main1FOC2Fail | 4 |  |  | 0 | $ComStatus , , | #[CDFA] : Diff Communication Fail Ch-2
98 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main1 | 32 | DisProtTrip | SIL0 | IEC104:M_SP_NA_1 | 2284 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2284 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main1DisProtTrip | 4 |  |  | 0 | $ComStatus , , | #[nDIO] : Main-1 Dist Protection Trip
99 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main1 | 32 | LoadCurOp | SIL0 | IEC104:M_SP_NA_1 | 2285 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2285 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main1LoadCurOp | 4 |  |  | 0 | $ComStatus , , | #[BEFL] : 110% of Full Load Current
100 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main1 | 32 | SoftTrip | SIL0 | IEC104:M_SP_NA_1 | 2286 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2286 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main1SoftTrip | 4 |  |  | 0 | $ComStatus , , | #[SOTF] : SOTF Trip
101 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main1 | 32 | PowSwBlk | SIL0 | IEC104:M_SP_NA_1 | 2287 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2287 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main1PowSwBlk | 4 |  |  | 0 | $ComStatus , , | #[nDIP] : Power Swing Block
102 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main1 | 32 | VTFuseFail | SIL0 | IEC104:M_SP_NA_1 | 2288 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2288 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main1VTFuseFail | 4 |  |  | 0 | $ComStatus , , | #[nVTF] : VT Fuse Failure / MCB Trip
103 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main1 | 32 | BckpCurTrip | SIL0 | IEC104:M_SP_NA_1 | 2289 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2289 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main1BckpCurTrip | 4 |  |  | 0 | $ComStatus , , | #[OCPO] : Backup Overcurrent I>Trip
104 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main1 | 32 | InterTripRCh1 | SIL0 | IEC104:M_SP_NA_1 | 2290 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2290 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main1InterTripRCh1 | 4 |  |  | 0 | $ComStatus , , | #[INTR] : Intertrip Received Channel-1
105 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main1 | 32 | InterTripRCh2 | SIL0 | IEC104:M_SP_NA_1 | 2291 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2291 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main1InterTripRCh2 | 4 |  |  | 0 | $ComStatus , , | #[INTR] : Intertrip Received Channel-2
106 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main1 | 32 | InterTripSCh1 | SIL0 | IEC104:M_SP_NA_1 | 2292 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2292 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main1InterTripSCh1 | 4 |  |  | 0 | $ComStatus , , | #[INTS] : Intertrip Sent Channel-1
107 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main1 | 32 | InterTripSCh2 | SIL0 | IEC104:M_SP_NA_1 | 2293 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2293 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main1InterTripSCh2 | 4 |  |  | 0 | $ComStatus , , | #[INTS] : Intertrip Sent Channel-2
108 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main2 | 33 | T11DCSupplyFail | SIL0 | IEC104:M_SP_NA_1 | 2320 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2320 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main2T11DCSupplyFail | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : T11 DC Supply Fail
109 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main2 | 33 | T21DCSupplyFail | SIL0 | IEC104:M_SP_NA_1 | 2321 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2321 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main2T21DCSupplyFail | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : T12 DC Supply Fail
110 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main2 | 33 | FOC1Fail | SIL0 | IEC104:M_SP_NA_1 | 2322 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2322 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main2FOC1Fail | 4 |  |  | 0 | $ComStatus , , | #[CDFA] : Diff Communication Fail Ch-1
111 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main2 | 33 | FOC2Fail | SIL0 | IEC104:M_SP_NA_1 | 2323 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2323 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main2FOC2Fail | 4 |  |  | 0 | $ComStatus , , | #[CDFA] : Diff Communication Fail Ch-2
112 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main2 | 33 | DisProtTrip | SIL0 | IEC104:M_SP_NA_1 | 2324 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2324 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main2DisProtTrip | 4 |  |  | 0 | $ComStatus , , | #[nDIO] : Main-1 Dist Protection Trip
113 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main2 | 33 | LoadCurOp | SIL0 | IEC104:M_SP_NA_1 | 2325 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2325 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main2LoadCurOp | 4 |  |  | 0 | $ComStatus , , | #[BEFL] : 110% of Full Load Current
114 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main2 | 33 | SoftTrip | SIL0 | IEC104:M_SP_NA_1 | 2326 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2326 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main2SoftTrip | 4 |  |  | 0 | $ComStatus , , | #[SOTF] : SOTF Trip
115 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main2 | 33 | PowSwBlk | SIL0 | IEC104:M_SP_NA_1 | 2327 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2327 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main2PowSwBlk | 4 |  |  | 0 | $ComStatus , , | #[nDIP] : Power Swing Block
116 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main2 | 33 | VTFuseFail | SIL0 | IEC104:M_SP_NA_1 | 2328 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2328 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main2VTFuseFail | 4 |  |  | 0 | $ComStatus , , | #[nVTF] : VT Fuse Failure / MCB Trip
117 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main2 | 33 | BckpCurTrip | SIL0 | IEC104:M_SP_NA_1 | 2329 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2329 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main2BckpCurTrip | 4 |  |  | 0 | $ComStatus , , | #[OCPO] : Backup Overcurrent I>Trip
118 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main2 | 33 | InterTripRCh1 | SIL0 | IEC104:M_SP_NA_1 | 2330 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2330 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main2InterTripRCh1 | 4 |  |  | 0 | $ComStatus , , | #[INTR] : Intertrip Received Channel-1
119 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main2 | 33 | InterTripRCh2 | SIL0 | IEC104:M_SP_NA_1 | 2331 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2331 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main2InterTripRCh2 | 4 |  |  | 0 | $ComStatus , , | #[INTR] : Intertrip Received Channel-2
120 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main2 | 33 | InterTripSCh1 | SIL0 | IEC104:M_SP_NA_1 | 2332 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2332 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main2InterTripSCh1 | 4 |  |  | 0 | $ComStatus , , | #[INTS] : Intertrip Sent Channel-1
121 | BPS01_RTU | PWR:BPS:CL | B10 | 66KVIFPR | 66KVIFPR_B10_Main2 | 33 | InterTripSCh2 | SIL0 | IEC104:M_SP_NA_1 | 2333 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2333 | 0 | 1 | deiPWRBPSCLB1066KVIFPR_B10_Main2InterTripSCh2 | 4 |  |  | 0 | $ComStatus , , | #[INTS] : Intertrip Sent Channel-2
122 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main1 | 34 | T11DCSupplyFail | SIL0 | IEC104:M_SP_NA_1 | 2360 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2360 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main1T11DCSupplyFail | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : T11 DC Supply Fail
123 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main1 | 34 | T21DCSupplyFail | SIL0 | IEC104:M_SP_NA_1 | 2361 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2361 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main1T21DCSupplyFail | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : T12 DC Supply Fail
124 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main1 | 34 | FOC1Fail | SIL0 | IEC104:M_SP_NA_1 | 2362 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2362 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main1FOC1Fail | 4 |  |  | 0 | $ComStatus , , | #[CDFA] : Diff Communication Fail Ch-1
125 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main1 | 34 | FOC2Fail | SIL0 | IEC104:M_SP_NA_1 | 2363 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2363 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main1FOC2Fail | 4 |  |  | 0 | $ComStatus , , | #[CDFA] : Diff Communication Fail Ch-2
126 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main1 | 34 | DisProtTrip | SIL0 | IEC104:M_SP_NA_1 | 2364 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2364 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main1DisProtTrip | 4 |  |  | 0 | $ComStatus , , | #[nDIO] : Main-1 Dist Protection Trip
127 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main1 | 34 | LoadCurOp | SIL0 | IEC104:M_SP_NA_1 | 2365 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2365 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main1LoadCurOp | 4 |  |  | 0 | $ComStatus , , | #[BEFL] : 110% of Full Load Current
128 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main1 | 34 | SoftTrip | SIL0 | IEC104:M_SP_NA_1 | 2366 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2366 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main1SoftTrip | 4 |  |  | 0 | $ComStatus , , | #[SOTF] : SOTF Trip
129 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main1 | 34 | PowSwBlk | SIL0 | IEC104:M_SP_NA_1 | 2367 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2367 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main1PowSwBlk | 4 |  |  | 0 | $ComStatus , , | #[nDIP] : Power Swing Block
130 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main1 | 34 | VTFuseFail | SIL0 | IEC104:M_SP_NA_1 | 2368 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2368 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main1VTFuseFail | 4 |  |  | 0 | $ComStatus , , | #[nVTF] : VT Fuse Failure / MCB Trip
131 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main1 | 34 | BckpCurTrip | SIL0 | IEC104:M_SP_NA_1 | 2369 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2369 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main1BckpCurTrip | 4 |  |  | 0 | $ComStatus , , | #[OCPO] : Backup Overcurrent I>Trip
132 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main1 | 34 | InterTripRCh1 | SIL0 | IEC104:M_SP_NA_1 | 2370 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2370 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main1InterTripRCh1 | 4 |  |  | 0 | $ComStatus , , | #[INTR] : Intertrip Received Channel-1
133 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main1 | 34 | InterTripRCh2 | SIL0 | IEC104:M_SP_NA_1 | 2371 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2371 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main1InterTripRCh2 | 4 |  |  | 0 | $ComStatus , , | #[INTR] : Intertrip Received Channel-2
134 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main1 | 34 | InterTripSCh1 | SIL0 | IEC104:M_SP_NA_1 | 2372 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2372 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main1InterTripSCh1 | 4 |  |  | 0 | $ComStatus , , | #[INTS] : Intertrip Sent Channel-1
135 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main1 | 34 | InterTripSCh2 | SIL0 | IEC104:M_SP_NA_1 | 2373 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2373 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main1InterTripSCh2 | 4 |  |  | 0 | $ComStatus , , | #[INTS] : Intertrip Sent Channel-2
136 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main2 | 35 | T11DCSupplyFail | SIL0 | IEC104:M_SP_NA_1 | 2400 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2400 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main2T11DCSupplyFail | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : T11 DC Supply Fail
137 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main2 | 35 | T21DCSupplyFail | SIL0 | IEC104:M_SP_NA_1 | 2401 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2401 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main2T21DCSupplyFail | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : T12 DC Supply Fail
138 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main2 | 35 | FOC1Fail | SIL0 | IEC104:M_SP_NA_1 | 2402 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2402 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main2FOC1Fail | 4 |  |  | 0 | $ComStatus , , | #[CDFA] : Diff Communication Fail Ch-1
139 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main2 | 35 | FOC2Fail | SIL0 | IEC104:M_SP_NA_1 | 2403 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2403 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main2FOC2Fail | 4 |  |  | 0 | $ComStatus , , | #[CDFA] : Diff Communication Fail Ch-2
140 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main2 | 35 | DisProtTrip | SIL0 | IEC104:M_SP_NA_1 | 2404 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2404 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main2DisProtTrip | 4 |  |  | 0 | $ComStatus , , | #[nDIO] : Main-1 Dist Protection Trip
141 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main2 | 35 | LoadCurOp | SIL0 | IEC104:M_SP_NA_1 | 2405 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2405 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main2LoadCurOp | 4 |  |  | 0 | $ComStatus , , | #[BEFL] : 110% of Full Load Current
142 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main2 | 35 | SoftTrip | SIL0 | IEC104:M_SP_NA_1 | 2406 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2406 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main2SoftTrip | 4 |  |  | 0 | $ComStatus , , | #[SOTF] : SOTF Trip
143 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main2 | 35 | PowSwBlk | SIL0 | IEC104:M_SP_NA_1 | 2407 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2407 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main2PowSwBlk | 4 |  |  | 0 | $ComStatus , , | #[nDIP] : Power Swing Block
144 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main2 | 35 | VTFuseFail | SIL0 | IEC104:M_SP_NA_1 | 2408 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2408 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main2VTFuseFail | 4 |  |  | 0 | $ComStatus , , | #[nVTF] : VT Fuse Failure / MCB Trip
145 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main2 | 35 | BckpCurTrip | SIL0 | IEC104:M_SP_NA_1 | 2409 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2409 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main2BckpCurTrip | 4 |  |  | 0 | $ComStatus , , | #[OCPO] : Backup Overcurrent I>Trip
146 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main2 | 35 | InterTripRCh1 | SIL0 | IEC104:M_SP_NA_1 | 2410 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2410 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main2InterTripRCh1 | 4 |  |  | 0 | $ComStatus , , | #[INTR] : Intertrip Received Channel-1
147 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main2 | 35 | InterTripRCh2 | SIL0 | IEC104:M_SP_NA_1 | 2411 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2411 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main2InterTripRCh2 | 4 |  |  | 0 | $ComStatus , , | #[INTR] : Intertrip Received Channel-2
148 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main2 | 35 | InterTripSCh1 | SIL0 | IEC104:M_SP_NA_1 | 2412 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2412 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main2InterTripSCh1 | 4 |  |  | 0 | $ComStatus , , | #[INTS] : Intertrip Sent Channel-1
149 | BPS01_RTU | PWR:BPS:CL | B20 | 66KVIFPR | 66KVIFPR_B20_Main2 | 35 | InterTripSCh2 | SIL0 | IEC104:M_SP_NA_1 | 2413 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2413 | 0 | 1 | deiPWRBPSCLB2066KVIFPR_B20_Main2InterTripSCh2 | 4 |  |  | 0 | $ComStatus , , | #[INTS] : Intertrip Sent Channel-2
150 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSBA | 66KVBSBA_B12 | 36 | ACFailRPLcc | SIL0 | IEC104:M_SP_NA_1 | 2440 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2440 | 0 | 1 | deiPWRBPSCLB1266KVBSBA_B12ACFailRPLcc | 4 |  |  | 0 | $ComStatus , , | #[ACFL] : AC Fail Relay Panel / LCC
151 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSBA | 66KVBSBA_B12 | 36 | DCFailRP | SIL0 | IEC104:M_SP_NA_1 | 2441 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2441 | 0 | 1 | deiPWRBPSCLB1266KVBSBA_B12DCFailRP | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : DC Fail Relay Panel
152 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSBA | 66KVBSBA_B12 | 36 | DCFailLcc | SIL0 | IEC104:M_SP_NA_1 | 2442 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2442 | 0 | 1 | deiPWRBPSCLB1266KVBSBA_B12DCFailLcc | 4 |  |  | 0 | $ComStatus , , | #[DCFA] : DC Fail LCC Panel
153 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSBA | 66KVBSBA_B12 | 36 | SF6GasPressSt1 | SIL0 | IEC104:M_SP_NA_1 | 2443 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2443 | 0 | 1 | deiPWRBPSCLB1266KVBSBA_B12SF6GasPressSt1 | 4 |  |  | 0 | $ComStatus , , | #[GAS1] : SF6 Gas Pressure 1st Stage
154 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSBA | 66KVBSBA_B12 | 36 | SF6GasPressSt2 | SIL0 | IEC104:M_SP_NA_1 | 2444 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2444 | 0 | 1 | deiPWRBPSCLB1266KVBSBA_B12SF6GasPressSt2 | 4 |  |  | 0 | $ComStatus , , | #[GAS2] : SF6 Gas Pressure 2nd Stage
155 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSBA | 66KVBSBA_B12 | 36 | MstrTrpRyOp | SIL2_Monitoring | IEC104:M_SP_NA_1 | 2445 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 2445 | 0 | 1 | deiPWRBPSCLB1266KVBSBA_B12MstrTrpRyOp | 4 |  |  | 0 | $ComStatus , , | #[MTRO] : Master Trip relay operated
156 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSBA | 66KVBSBA_B12 | 36 | WdgIedStatus | SIL0 | IEC104:M_SP_NA_1 | 2446 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2446 | 0 | 1 | deiPWRBPSCLB1266KVBSBA_B12WdgIedStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG**] : IED WatchDog
157 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSBA | 66KVBSBA_B12 | 36 | WdgBcuStatus | SIL2_Monitoring | IEC104:M_SP_NA_1 | 2447 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 2447 | 0 | 1 | deiPWRBPSCLB1266KVBSBA_B12WdgBcuStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG**] : BCU Watchdog
158 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSBA | 66KVBSBA_B12 | 36 | VoltTransStatus | SIL0 | IEC104:M_SP_NA_1 | 2448 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2448 | 0 | 1 | deiPWRBPSCLB1266KVBSBA_B12VoltTransStatus | 4 |  |  | 0 | $ComStatus , , | #[VTFA] : Voltage Transformer Fault alarm
159 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSBA | 66KVBSBA_B12 | 36 | BrkFailStage1 | SIL0 | IEC104:M_SP_NA_1 | 2449 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2449 | 0 | 1 | deiPWRBPSCLB1266KVBSBA_B12BrkFailStage1 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker failure stage 1
160 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSBA | 66KVBSBA_B12 | 36 | BrkFailStage2 | SIL0 | IEC104:M_SP_NA_1 | 2450 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2450 | 0 | 1 | deiPWRBPSCLB1266KVBSBA_B12BrkFailStage2 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker failure stage 2
161 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSBA | 66KVBSBA_B12 | 36 | BCUCardFail | SIL0 | IEC104:M_SP_NA_1 | 2451 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2451 | 0 | 1 | deiPWRBPSCLB1266KVBSBA_B12BCUCardFail | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Card Fail
162 | BPS01_RTU | PWR:BPS:CL | B12 | CB_OST | B120 | 37 | CbPositionM | SIL2_Monitoring | IEC104:M_DP_NA_1 | 4740 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 4740 | 0 | 2 | deiPWRBPSCLB12B120CbPositionM | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Status
163 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSPR | 66KVBSPR_B120 | 38 | GenTrip | SIL0 | IEC104:M_SP_NA_1 | 2520 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 2520 | 0 | 1 | deiPWRBPSCLB1266KVBSPR_B120GenTrip | 4 |  |  | 0 | $ComStatus , , | #[OEPO] : General Trip
164 | BPS01_RTU | PWR:BPS:CL | B12 | BIST | BIST_B124 | 39 | BusIsolPosM | SIL2_Monitoring | IEC104:M_DP_NA_1 | 4780 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 4780 | 0 | 2 | deiPWRBPSCLB12BIST_B124BusIsolPosM | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
165 | BPS01_RTU | PWR:BPS:CL | B12 | BIST | BIST_B126 | 40 | BusIsolPosM | SIL2_Monitoring | IEC104:M_DP_NA_1 | 4800 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 4800 | 0 | 2 | deiPWRBPSCLB12BIST_B126BusIsolPosM | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
166 | BPS01_RTU | PWR:BPS:CL | B12 | BIST | BIST_B164 | 41 | BusIsolPosM | SIL2_Monitoring | IEC104:M_DP_NA_1 | 4820 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 4820 | 0 | 2 | deiPWRBPSCLB12BIST_B164BusIsolPosM | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
167 | BPS01_RTU | PWR:BPS:CL | B12 | BIST | BIST_B264 | 42 | BusIsolPosM | SIL2_Monitoring | IEC104:M_DP_NA_1 | 4840 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 4840 | 0 | 2 | deiPWRBPSCLB12BIST_B264BusIsolPosM | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
168 | BPS01_RTU | PWR:BPS:CL | B12 | ESSM | B1241 | 43 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 4860 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 4860 | 0 | 2 | deiPWRBPSCLB12B1241EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
169 | BPS01_RTU | PWR:BPS:CL | B12 | ESSM | B1261 | 44 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 4880 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 4880 | 0 | 2 | deiPWRBPSCLB12B1261EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
170 | BPS01_RTU | PWR:BPS:CL | B12 | ESSM | B12M1 | 45 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 4900 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 4900 | 0 | 2 | deiPWRBPSCLB12B12M1EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
171 | BPS01_RTU | PWR:BPS:CL | B12 | ESSM | B12M2 | 46 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 4920 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 4920 | 0 | 2 | deiPWRBPSCLB12B12M2EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
172 | BPS01_RTU | PWR:BPS:CL | B12 | ESSM | B16M1 | 47 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 4940 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 4940 | 0 | 2 | deiPWRBPSCLB12B16M1EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
173 | BPS01_RTU | PWR:BPS:CL | B12 | ESSM | B26M1 | 48 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 4960 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 4960 | 0 | 2 | deiPWRBPSCLB12B26M1EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
174 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSMV | 66KVBSMV_B12 | 49 | RPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 8960 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 8960 | 0 | 16 | aeiPWRBPSCLB1266KVBSMV_B12RPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #R Phase Current
175 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSMV | 66KVBSMV_B12 | 49 | YPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 8961 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 8961 | 0 | 16 | aeiPWRBPSCLB1266KVBSMV_B12YPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #Y Phase Current
176 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSMV | 66KVBSMV_B12 | 49 | BPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 8962 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 8962 | 0 | 16 | aeiPWRBPSCLB1266KVBSMV_B12BPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #B Phase Current
177 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSMV | 66KVBSMV_B12 | 49 | NeutralCur | SIL0 | IEC104:M_ME_NA_1 | 8963 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 8963 | 0 | 16 | aeiPWRBPSCLB1266KVBSMV_B12NeutralCur | 4 |  |  | 0 | $ComStatus , , | #Neutral Current (In)
178 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSMV | 66KVBSMV_B12 | 49 | RYPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 8964 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 8964 | 0 | 16 | aeiPWRBPSCLB1266KVBSMV_B12RYPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #RY Phase Voltage
179 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSMV | 66KVBSMV_B12 | 49 | YBPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 8965 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 8965 | 0 | 16 | aeiPWRBPSCLB1266KVBSMV_B12YBPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #YB Phase Voltage
180 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSMV | 66KVBSMV_B12 | 49 | BRPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 8966 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 8966 | 0 | 16 | aeiPWRBPSCLB1266KVBSMV_B12BRPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #BR Phase Voltage
181 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSMV | 66KVBSMV_B12 | 49 | ZeroSeqVolt | SIL0 | IEC104:M_ME_NA_1 | 8967 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 8967 | 0 | 16 | aeiPWRBPSCLB1266KVBSMV_B12ZeroSeqVolt | 4 |  |  | 0 | $ComStatus , , | #Zero Sequence Voltage (V0)
182 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSMV | 66KVBSMV_B12 | 49 | ActivePower | SIL0 | IEC104:M_ME_NA_1 | 8968 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 8968 | 0 | 16 | aeiPWRBPSCLB1266KVBSMV_B12ActivePower | 4 |  |  | 0 | $ComStatus , , | #[MW] : Active Power
183 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSMV | 66KVBSMV_B12 | 49 | ReacPower | SIL0 | IEC104:M_ME_NA_1 | 8969 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 8969 | 0 | 16 | aeiPWRBPSCLB1266KVBSMV_B12ReacPower | 4 |  |  | 0 | $ComStatus , , | #[MVAR] : Reactive Power
184 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSMV | 66KVBSMV_B12 | 49 | AppPower | SIL0 | IEC104:M_ME_NA_1 | 8970 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 8970 | 0 | 16 | aeiPWRBPSCLB1266KVBSMV_B12AppPower | 4 |  |  | 0 | $ComStatus , , | #Apparent Power (S)
185 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSMV | 66KVBSMV_B12 | 49 | PowerFactor | SIL0 | IEC104:M_ME_NA_1 | 8971 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 8971 | 0 | 16 | aeiPWRBPSCLB1266KVBSMV_B12PowerFactor | 4 |  |  | 0 | $ComStatus , , | #Power Factor (P.F)
186 | BPS01_RTU | PWR:BPS:CL | B12 | 66KVBSMV | 66KVBSMV_B12 | 49 | Frequency | SIL0 | IEC104:M_ME_NA_1 | 8972 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 8972 | 0 | 16 | aeiPWRBPSCLB1266KVBSMV_B12Frequency | 4 |  |  | 0 | $ComStatus , , | #Frequency (Hz)
187 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVBA | 66KVHVBA_B11 | 50 | ACFailRPLcc | SIL0 | IEC104:M_SP_NA_1 | 3000 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3000 | 0 | 1 | deiPWRBPSCLB1166KVHVBA_B11ACFailRPLcc | 4 |  |  | 0 | $ComStatus , , | #[ACFL] : AC Fail Relay Panel / LCC
188 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVBA | 66KVHVBA_B11 | 50 | DCFailRP | SIL0 | IEC104:M_SP_NA_1 | 3001 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3001 | 0 | 1 | deiPWRBPSCLB1166KVHVBA_B11DCFailRP | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : DC Fail Relay Panel
189 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVBA | 66KVHVBA_B11 | 50 | DCFailLcc | SIL0 | IEC104:M_SP_NA_1 | 3002 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3002 | 0 | 1 | deiPWRBPSCLB1166KVHVBA_B11DCFailLcc | 4 |  |  | 0 | $ComStatus , , | #[DCFA] : DC Fail LCC Panel
190 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVBA | 66KVHVBA_B11 | 50 | SF6GasPressSt1 | SIL0 | IEC104:M_SP_NA_1 | 3003 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3003 | 0 | 1 | deiPWRBPSCLB1166KVHVBA_B11SF6GasPressSt1 | 4 |  |  | 0 | $ComStatus , , | #[GAS1] : SF6 Gas Pressure Stage 1
191 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVBA | 66KVHVBA_B11 | 50 | SF6GasPressSt2 | SIL0 | IEC104:M_SP_NA_1 | 3004 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3004 | 0 | 1 | deiPWRBPSCLB1166KVHVBA_B11SF6GasPressSt2 | 4 |  |  | 0 | $ComStatus , , | #[GAS2] : SF6 Gas Pressure Stage 2
192 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVBA | 66KVHVBA_B11 | 50 | MstrTrpRyOp | SIL2_Monitoring | IEC104:M_SP_NA_1 | 3005 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 3005 | 0 | 1 | deiPWRBPSCLB1166KVHVBA_B11MstrTrpRyOp | 4 |  |  | 0 | $ComStatus , , | #[MTRO] : Master Trip relay operated
193 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVBA | 66KVHVBA_B11 | 50 | WdgIedStatus | SIL0 | IEC104:M_SP_NA_1 | 3006 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3006 | 0 | 1 | deiPWRBPSCLB1166KVHVBA_B11WdgIedStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : IED WatchDog
194 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVBA | 66KVHVBA_B11 | 50 | WdgBcuStatus | SIL2_Monitoring | IEC104:M_SP_NA_1 | 3007 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 3007 | 0 | 1 | deiPWRBPSCLB1166KVHVBA_B11WdgBcuStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Watchdog
195 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVBA | 66KVHVBA_B11 | 50 | OCEFProtOp | SIL2_Monitoring | IEC104:M_SP_NA_1 | 3008 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 3008 | 0 | 1 | deiPWRBPSCLB1166KVHVBA_B11OCEFProtOp | 4 |  |  | 0 | $ComStatus , , | #[OEPE] : OC/EF Protection Operated
196 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVBA | 66KVHVBA_B11 | 50 | BCUCardFail | SIL0 | IEC104:M_SP_NA_1 | 3009 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3009 | 0 | 1 | deiPWRBPSCLB1166KVHVBA_B11BCUCardFail | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Card Fail
197 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVBA | 66KVHVBA_B21 | 51 | ACFailRPLcc | SIL0 | IEC104:M_SP_NA_1 | 3040 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3040 | 0 | 1 | deiPWRBPSCLB2166KVHVBA_B21ACFailRPLcc | 4 |  |  | 0 | $ComStatus , , | #[ACFL] : AC Fail Relay Panel / LCC
198 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVBA | 66KVHVBA_B21 | 51 | DCFailRP | SIL0 | IEC104:M_SP_NA_1 | 3041 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3041 | 0 | 1 | deiPWRBPSCLB2166KVHVBA_B21DCFailRP | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : DC Fail Relay Panel
199 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVBA | 66KVHVBA_B21 | 51 | DCFailLcc | SIL0 | IEC104:M_SP_NA_1 | 3042 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3042 | 0 | 1 | deiPWRBPSCLB2166KVHVBA_B21DCFailLcc | 4 |  |  | 0 | $ComStatus , , | #[DCFA] : DC Fail LCC Panel
200 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVBA | 66KVHVBA_B21 | 51 | SF6GasPressSt1 | SIL0 | IEC104:M_SP_NA_1 | 3043 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3043 | 0 | 1 | deiPWRBPSCLB2166KVHVBA_B21SF6GasPressSt1 | 4 |  |  | 0 | $ComStatus , , | #[GAS1] : SF6 Gas Pressure Stage 1
201 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVBA | 66KVHVBA_B21 | 51 | SF6GasPressSt2 | SIL0 | IEC104:M_SP_NA_1 | 3044 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3044 | 0 | 1 | deiPWRBPSCLB2166KVHVBA_B21SF6GasPressSt2 | 4 |  |  | 0 | $ComStatus , , | #[GAS2] : SF6 Gas Pressure Stage 2
202 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVBA | 66KVHVBA_B21 | 51 | MstrTrpRyOp | SIL2_Monitoring | IEC104:M_SP_NA_1 | 3045 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 3045 | 0 | 1 | deiPWRBPSCLB2166KVHVBA_B21MstrTrpRyOp | 4 |  |  | 0 | $ComStatus , , | #[MTRO] : Master Trip relay operated
203 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVBA | 66KVHVBA_B21 | 51 | WdgIedStatus | SIL0 | IEC104:M_SP_NA_1 | 3046 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3046 | 0 | 1 | deiPWRBPSCLB2166KVHVBA_B21WdgIedStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : IED WatchDog
204 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVBA | 66KVHVBA_B21 | 51 | WdgBcuStatus | SIL2_Monitoring | IEC104:M_SP_NA_1 | 3047 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 3047 | 0 | 1 | deiPWRBPSCLB2166KVHVBA_B21WdgBcuStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Watchdog
205 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVBA | 66KVHVBA_B21 | 51 | OCEFProtOp | SIL2_Monitoring | IEC104:M_SP_NA_1 | 3048 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 3048 | 0 | 1 | deiPWRBPSCLB2166KVHVBA_B21OCEFProtOp | 4 |  |  | 0 | $ComStatus , , | #[OEPE] : OC/EF Protection Operated
206 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVBA | 66KVHVBA_B21 | 51 | BCUCardFail | SIL0 | IEC104:M_SP_NA_1 | 3049 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3049 | 0 | 1 | deiPWRBPSCLB2166KVHVBA_B21BCUCardFail | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Card Fail
207 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVPR | 66KVHVPR_B110 | 52 | DiffTrip | SIL0 | IEC104:M_SP_NA_1 | 3080 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3080 | 0 | 1 | deiPWRBPSCLB1166KVHVPR_B110DiffTrip | 4 |  |  | 0 | $ComStatus , , | #[TDPO] : 40MVA-T1 Main-1 Diff Prot Trip
208 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVPR | 66KVHVPR_B110 | 52 | DiffHighSetSt2 | SIL0 | IEC104:M_SP_NA_1 | 3081 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3081 | 0 | 1 | deiPWRBPSCLB1166KVHVPR_B110DiffHighSetSt2 | 4 |  |  | 0 | $ComStatus , , | #[TDP1] : 40MVA-T1 Diff Prot High Set St2
209 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVPR | 66KVHVPR_B110 | 52 | GenTrip | SIL0 | IEC104:M_SP_NA_1 | 3082 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3082 | 0 | 1 | deiPWRBPSCLB1166KVHVPR_B110GenTrip | 4 |  |  | 0 | $ComStatus , , | #[OEPO] : General Trip
210 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVPR | 66KVHVPR_B210 | 53 | DiffTrip | SIL0 | IEC104:M_SP_NA_1 | 3120 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3120 | 0 | 1 | deiPWRBPSCLB2166KVHVPR_B210DiffTrip | 4 |  |  | 0 | $ComStatus , , | #[TDPO] : 40MVA-T1 Main-1 Diff Prot Trip
211 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVPR | 66KVHVPR_B210 | 53 | DiffHighSetSt2 | SIL0 | IEC104:M_SP_NA_1 | 3121 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3121 | 0 | 1 | deiPWRBPSCLB2166KVHVPR_B210DiffHighSetSt2 | 4 |  |  | 0 | $ComStatus , , | #[TDP1] : 40MVA-T1 Diff Prot High Set St2
212 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVPR | 66KVHVPR_B210 | 53 | GenTrip | SIL0 | IEC104:M_SP_NA_1 | 3122 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3122 | 0 | 1 | deiPWRBPSCLB2166KVHVPR_B210GenTrip | 4 |  |  | 0 | $ComStatus , , | #[OEPO] : General Trip
213 | BPS01_RTU | PWR:BPS:CL | B11 | BIST | BIST_B114 | 54 | BusIsolPosM | SIL2_Monitoring | IEC104:M_DP_NA_1 | 5080 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 5080 | 0 | 2 | deiPWRBPSCLB11BIST_B114BusIsolPosM | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
214 | BPS01_RTU | PWR:BPS:CL | B21 | BIST | BIST_B214 | 55 | BusIsolPosM | SIL2_Monitoring | IEC104:M_DP_NA_1 | 5100 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 5100 | 0 | 2 | deiPWRBPSCLB21BIST_B214BusIsolPosM | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
215 | BPS01_RTU | PWR:BPS:CL | B11 | ESSM | B11M1 | 56 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 5120 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 5120 | 0 | 2 | deiPWRBPSCLB11B11M1EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
216 | BPS01_RTU | PWR:BPS:CL | B21 | ESSM | B21M1 | 57 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 5140 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 5140 | 0 | 2 | deiPWRBPSCLB21B21M1EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
217 | BPS01_RTU | PWR:BPS:CL | B11 | CB_OST | B110 | 58 | CbPositionM | SIL2_Monitoring | IEC104:M_DP_NA_1 | 5160 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 5160 | 0 | 2 | deiPWRBPSCLB11B110CbPositionM | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Status
218 | BPS01_RTU | PWR:BPS:CL | B21 | CB_OST | B210 | 59 | CbPositionM | SIL2_Monitoring | IEC104:M_DP_NA_1 | 5180 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 5180 | 0 | 2 | deiPWRBPSCLB21B210CbPositionM | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Status
219 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVMV | 66KVHVMV_B11 | 60 | RPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 9400 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9400 | 0 | 16 | aeiPWRBPSCLB1166KVHVMV_B11RPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #R Phase Current
220 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVMV | 66KVHVMV_B11 | 60 | YPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 9401 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9401 | 0 | 16 | aeiPWRBPSCLB1166KVHVMV_B11YPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #Y Phase Current
221 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVMV | 66KVHVMV_B11 | 60 | BPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 9402 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9402 | 0 | 16 | aeiPWRBPSCLB1166KVHVMV_B11BPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #B Phase Current
222 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVMV | 66KVHVMV_B11 | 60 | NeutralCur | SIL0 | IEC104:M_ME_NA_1 | 9403 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9403 | 0 | 16 | aeiPWRBPSCLB1166KVHVMV_B11NeutralCur | 4 |  |  | 0 | $ComStatus , , | #Neutral Current (In)
223 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVMV | 66KVHVMV_B11 | 60 | RYPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 9404 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9404 | 0 | 16 | aeiPWRBPSCLB1166KVHVMV_B11RYPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #RY Phase Voltage
224 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVMV | 66KVHVMV_B11 | 60 | YBPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 9405 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9405 | 0 | 16 | aeiPWRBPSCLB1166KVHVMV_B11YBPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #YB Phase Voltage
225 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVMV | 66KVHVMV_B11 | 60 | BRPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 9406 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9406 | 0 | 16 | aeiPWRBPSCLB1166KVHVMV_B11BRPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #BR Phase Voltage
226 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVMV | 66KVHVMV_B11 | 60 | ZeroSeqVolt | SIL0 | IEC104:M_ME_NA_1 | 9407 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9407 | 0 | 16 | aeiPWRBPSCLB1166KVHVMV_B11ZeroSeqVolt | 4 |  |  | 0 | $ComStatus , , | #Zero Sequence Voltage (V0)
227 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVMV | 66KVHVMV_B11 | 60 | ActivePower | SIL0 | IEC104:M_ME_NA_1 | 9408 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9408 | 0 | 16 | aeiPWRBPSCLB1166KVHVMV_B11ActivePower | 4 |  |  | 0 | $ComStatus , , | #[MW] : Active Power
228 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVMV | 66KVHVMV_B11 | 60 | ReacPower | SIL0 | IEC104:M_ME_NA_1 | 9409 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9409 | 0 | 16 | aeiPWRBPSCLB1166KVHVMV_B11ReacPower | 4 |  |  | 0 | $ComStatus , , | #[MVAR] : Reactive Power
229 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVMV | 66KVHVMV_B11 | 60 | AppPower | SIL0 | IEC104:M_ME_NA_1 | 9410 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9410 | 0 | 16 | aeiPWRBPSCLB1166KVHVMV_B11AppPower | 4 |  |  | 0 | $ComStatus , , | #Apparent Power (S)
230 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVMV | 66KVHVMV_B11 | 60 | PowerFactor | SIL0 | IEC104:M_ME_NA_1 | 9411 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9411 | 0 | 16 | aeiPWRBPSCLB1166KVHVMV_B11PowerFactor | 4 |  |  | 0 | $ComStatus , , | #Power Factor (P.F)
231 | BPS01_RTU | PWR:BPS:CL | B11 | 66KVHVMV | 66KVHVMV_B11 | 60 | Frequency | SIL0 | IEC104:M_ME_NA_1 | 9412 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9412 | 0 | 16 | aeiPWRBPSCLB1166KVHVMV_B11Frequency | 4 |  |  | 0 | $ComStatus , , | #Frequency (Hz)
232 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVMV | 66KVHVMV_B21 | 61 | RPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 9440 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9440 | 0 | 16 | aeiPWRBPSCLB2166KVHVMV_B21RPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #R Phase Current
233 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVMV | 66KVHVMV_B21 | 61 | YPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 9441 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9441 | 0 | 16 | aeiPWRBPSCLB2166KVHVMV_B21YPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #Y Phase Current
234 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVMV | 66KVHVMV_B21 | 61 | BPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 9442 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9442 | 0 | 16 | aeiPWRBPSCLB2166KVHVMV_B21BPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #B Phase Current
235 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVMV | 66KVHVMV_B21 | 61 | NeutralCur | SIL0 | IEC104:M_ME_NA_1 | 9443 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9443 | 0 | 16 | aeiPWRBPSCLB2166KVHVMV_B21NeutralCur | 4 |  |  | 0 | $ComStatus , , | #Neutral Current (In)
236 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVMV | 66KVHVMV_B21 | 61 | RYPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 9444 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9444 | 0 | 16 | aeiPWRBPSCLB2166KVHVMV_B21RYPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #RY Phase Voltage
237 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVMV | 66KVHVMV_B21 | 61 | YBPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 9445 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9445 | 0 | 16 | aeiPWRBPSCLB2166KVHVMV_B21YBPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #YB Phase Voltage
238 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVMV | 66KVHVMV_B21 | 61 | BRPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 9446 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9446 | 0 | 16 | aeiPWRBPSCLB2166KVHVMV_B21BRPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #BR Phase Voltage
239 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVMV | 66KVHVMV_B21 | 61 | ZeroSeqVolt | SIL0 | IEC104:M_ME_NA_1 | 9447 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9447 | 0 | 16 | aeiPWRBPSCLB2166KVHVMV_B21ZeroSeqVolt | 4 |  |  | 0 | $ComStatus , , | #Zero Sequence Voltage (V0)
240 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVMV | 66KVHVMV_B21 | 61 | ActivePower | SIL0 | IEC104:M_ME_NA_1 | 9448 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9448 | 0 | 16 | aeiPWRBPSCLB2166KVHVMV_B21ActivePower | 4 |  |  | 0 | $ComStatus , , | #[MW] : Active Power
241 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVMV | 66KVHVMV_B21 | 61 | ReacPower | SIL0 | IEC104:M_ME_NA_1 | 9449 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9449 | 0 | 16 | aeiPWRBPSCLB2166KVHVMV_B21ReacPower | 4 |  |  | 0 | $ComStatus , , | #[MVAR] : Reactive Power
242 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVMV | 66KVHVMV_B21 | 61 | AppPower | SIL0 | IEC104:M_ME_NA_1 | 9450 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9450 | 0 | 16 | aeiPWRBPSCLB2166KVHVMV_B21AppPower | 4 |  |  | 0 | $ComStatus , , | #Apparent Power (S)
243 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVMV | 66KVHVMV_B21 | 61 | PowerFactor | SIL0 | IEC104:M_ME_NA_1 | 9451 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9451 | 0 | 16 | aeiPWRBPSCLB2166KVHVMV_B21PowerFactor | 4 |  |  | 0 | $ComStatus , , | #Power Factor (P.F)
244 | BPS01_RTU | PWR:BPS:CL | B21 | 66KVHVMV | 66KVHVMV_B21 | 61 | Frequency | SIL0 | IEC104:M_ME_NA_1 | 9452 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 9452 | 0 | 16 | aeiPWRBPSCLB2166KVHVMV_B21Frequency | 4 |  |  | 0 | $ComStatus , , | #Frequency (Hz)
245 | BPS01_RTU | PWR:BPS:CL | B11 | ESSM | B111 | 62 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 5240 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 5240 | 0 | 2 | deiPWRBPSCLB11B111EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
246 | BPS01_RTU | PWR:BPS:CL | B21 | ESSM | B211 | 63 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 5260 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 5260 | 0 | 2 | deiPWRBPSCLB21B211EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
247 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBAL | BBAL_33KV | 66 | BBPOutofServ | SIL0 | IEC104:M_SP_NA_1 | 3640 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3640 | 0 | 1 | deiPWRBPSCL33KVBBBBAL_33KVBBPOutofServ | 4 |  |  | 0 | $ComStatus , , | #[BPOS] : Busbar Protection Out of Service
248 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBAL | BBAL_33KV | 66 | BBPDisturbed | SIL0 | IEC104:M_SP_NA_1 | 3641 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3641 | 0 | 1 | deiPWRBPSCL33KVBBBBAL_33KVBBPDisturbed | 4 |  |  | 0 | $ComStatus , , | #[BPU1] : Busbar Protection Disturbed
249 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBAL | BBAL_33KV | 66 | BBPAllProtBlocked | SIL0 | IEC104:M_SP_NA_1 | 3642 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3642 | 0 | 1 | deiPWRBPSCL33KVBBBBAL_33KVBBPAllProtBlocked | 4 |  |  | 0 | $ComStatus , , | #[BBPB] : All Protection Blocked
250 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBAL | BBAL_33KV | 66 | CBFailS2M1Mode | SIL0 | IEC104:M_SP_NA_1 | 3643 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3643 | 0 | 1 | deiPWRBPSCL33KVBBBBAL_33KVCBFailS2M1Mode | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : CB Failure Stage 2 M1 Zone
251 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBAL | BBAL_33KV | 66 | CBFailS2M2Mode | SIL0 | IEC104:M_SP_NA_1 | 3644 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3644 | 0 | 1 | deiPWRBPSCL33KVBBBBAL_33KVCBFailS2M2Mode | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : CB Failure Stage 2 M2 Zone
252 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBAL | BBAL_33KV | 66 | BrkFailOperated | SIL2_Monitoring | IEC104:M_SP_NA_1 | 3645 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 3645 | 0 | 1 | deiPWRBPSCL33KVBBBBAL_33KVBrkFailOperated | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Operated
253 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBAL | BBAL_33KV | 66 | BBPM1Out | SIL0 | IEC104:M_SP_NA_1 | 3646 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3646 | 0 | 1 | deiPWRBPSCL33KVBBBBAL_33KVBBPM1Out | 4 |  |  | 0 | $ComStatus , , | #[BPU1] Busbar Protection M1 Zone
254 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBAL | BBAL_33KV | 66 | BBPM2Out | SIL0 | IEC104:M_SP_NA_1 | 3647 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3647 | 0 | 1 | deiPWRBPSCL33KVBBBBAL_33KVBBPM2Out | 4 |  |  | 0 | $ComStatus , , | #[BPU1] Busbar Protection M2 Zone
255 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBAL | BBAL_33KV | 66 | BusProZOpMode1 | SIL0 | IEC104:M_SP_NA_1 | 3648 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3648 | 0 | 1 | deiPWRBPSCL33KVBBBBAL_33KVBusProZOpMode1 | 4 |  |  | 0 | $ComStatus , , | #[BPU1] Busbar Protection Blocked M1 Zone
256 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBAL | BBAL_33KV | 66 | BusProZOpMode2 | SIL0 | IEC104:M_SP_NA_1 | 3649 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3649 | 0 | 1 | deiPWRBPSCL33KVBBBBAL_33KVBusProZOpMode2 | 4 |  |  | 0 | $ComStatus , , | #[BPU1] Busbar Protection Blocked M2 Zone
257 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPZ | BBPZ_33KV | 67 | BBPM1Trip | SIL0 | IEC104:M_SP_NA_1 | 3680 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3680 | 0 | 1 | deiPWRBPSCL33KVBBBBPZ_33KVBBPM1Trip | 4 |  |  | 0 | $ComStatus , , | #[BM1O] Busbar Protection M1 Trip
258 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPZ | BBPZ_33KV | 67 | BBPM2Trip | SIL0 | IEC104:M_SP_NA_1 | 3681 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3681 | 0 | 1 | deiPWRBPSCL33KVBBBBPZ_33KVBBPM2Trip | 4 |  |  | 0 | $ComStatus , , | #[BM2O] Busbar Protection M2 Trip
259 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPZ | BBPZ_33KV | 67 | BBProtOperated | SIL0 | IEC104:M_SP_NA_1 | 3682 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3682 | 0 | 1 | deiPWRBPSCL33KVBBBBPZ_33KVBBProtOperated | 4 |  |  | 0 | $ComStatus , , | #[CBFO] Busbar Protection Operated
260 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E18 | 68 | BrkFailStage1 | SIL0 | IEC104:M_SP_NA_1 | 3720 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3720 | 0 | 1 | deiPWRBPSCL33KVBBBBPR_E18BrkFailStage1 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-1 Operated
261 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E18 | 68 | BrkFailStage2 | SIL0 | IEC104:M_SP_NA_1 | 3721 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3721 | 0 | 1 | deiPWRBPSCL33KVBBBBPR_E18BrkFailStage2 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-2 Operated
262 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E28 | 69 | BrkFailStage1 | SIL0 | IEC104:M_SP_NA_1 | 3760 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3760 | 0 | 1 | deiPWRBPSCL33KVBBBBPR_E28BrkFailStage1 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-1 Operated
263 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E28 | 69 | BrkFailStage2 | SIL0 | IEC104:M_SP_NA_1 | 3761 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3761 | 0 | 1 | deiPWRBPSCL33KVBBBBPR_E28BrkFailStage2 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-2 Operated
264 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E10 | 70 | BrkFailStage1 | SIL0 | IEC104:M_SP_NA_1 | 3800 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3800 | 0 | 1 | deiPWRBPSCL33KVBBBBPR_E10BrkFailStage1 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-1 Operated
265 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E10 | 70 | BrkFailStage2 | SIL0 | IEC104:M_SP_NA_1 | 3801 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3801 | 0 | 1 | deiPWRBPSCL33KVBBBBPR_E10BrkFailStage2 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-2 Operated
266 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E20 | 71 | BrkFailStage1 | SIL0 | IEC104:M_SP_NA_1 | 3840 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3840 | 0 | 1 | deiPWRBPSCL33KVBBBBPR_E20BrkFailStage1 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-1 Operated
267 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E20 | 71 | BrkFailStage2 | SIL0 | IEC104:M_SP_NA_1 | 3841 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3841 | 0 | 1 | deiPWRBPSCL33KVBBBBPR_E20BrkFailStage2 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-2 Operated
268 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E30 | 72 | BrkFailStage1 | SIL0 | IEC104:M_SP_NA_1 | 3880 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3880 | 0 | 1 | deiPWRBPSCL33KVBBBBPR_E30BrkFailStage1 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-1 Operated
269 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E30 | 72 | BrkFailStage2 | SIL0 | IEC104:M_SP_NA_1 | 3881 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3881 | 0 | 1 | deiPWRBPSCL33KVBBBBPR_E30BrkFailStage2 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-2 Operated
270 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E40 | 73 | BrkFailStage1 | SIL0 | IEC104:M_SP_NA_1 | 3920 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3920 | 0 | 1 | deiPWRBPSCL33KVBBBBPR_E40BrkFailStage1 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-1 Operated
271 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E40 | 73 | BrkFailStage2 | SIL0 | IEC104:M_SP_NA_1 | 3921 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3921 | 0 | 1 | deiPWRBPSCL33KVBBBBPR_E40BrkFailStage2 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-2 Operated
272 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E50 | 74 | BrkFailStage1 | SIL0 | IEC104:M_SP_NA_1 | 3960 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3960 | 0 | 1 | deiPWRBPSCL33KVBBBBPR_E50BrkFailStage1 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-1 Operated
273 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E50 | 74 | BrkFailStage2 | SIL0 | IEC104:M_SP_NA_1 | 3961 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 3961 | 0 | 1 | deiPWRBPSCL33KVBBBBPR_E50BrkFailStage2 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-2 Operated
274 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E60 | 75 | BrkFailStage1 | SIL0 | IEC104:M_SP_NA_1 | 4000 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4000 | 0 | 1 | deiPWRBPSCL33KVBBBBPR_E60BrkFailStage1 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-1 Operated
275 | BPS01_RTU | PWR:BPS:CL | 33KVBB | BBPR | BBPR_E60 | 75 | BrkFailStage2 | SIL0 | IEC104:M_SP_NA_1 | 4001 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4001 | 0 | 1 | deiPWRBPSCL33KVBBBBPR_E60BrkFailStage2 | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-2 Operated
276 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BSCP | BSCP_E12 | 76 | BrkFailS1M1Op | SIL0 | IEC104:M_SP_NA_1 | 4040 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4040 | 0 | 1 | deiPWRBPSCL66KVBBBSCP_E12BrkFailS1M1Op | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-1 Operated - M1
277 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BSCP | BSCP_E12 | 76 | BrkFailS2M1Op | SIL0 | IEC104:M_SP_NA_1 | 4041 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4041 | 0 | 1 | deiPWRBPSCL66KVBBBSCP_E12BrkFailS2M1Op | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-2 Operated - M1
278 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BSCP | BSCP_E12 | 76 | BrkFailS1M2Op | SIL0 | IEC104:M_SP_NA_1 | 4042 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4042 | 0 | 1 | deiPWRBPSCL66KVBBBSCP_E12BrkFailS1M2Op | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-1 Operated - M2
279 | BPS01_RTU | PWR:BPS:CL | 66KVBB | BSCP | BSCP_E12 | 76 | BrkFailS2M2Op | SIL0 | IEC104:M_SP_NA_1 | 4043 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4043 | 0 | 1 | deiPWRBPSCL66KVBBBSCP_E12BrkFailS2M2Op | 4 |  |  | 0 | $ComStatus , , | #[CBFO] : Breaker Failure Stage-2 Operated - M2
280 | BPS01_RTU | PWR:BPS:CL | 33KVBB | 33KVVM | VM_E166VT | 77 | VoltageMesure | SIL0 | IEC104:M_ME_NA_1 | 10080 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10080 | 0 | 16 | aeiPWRBPSCL33KVBBVM_E166VTVoltageMesure | 4 |  |  | 0 | $ComStatus , , | #Voltage Measurement
281 | BPS01_RTU | PWR:BPS:CL | 33KVBB | 33KVVM | VM_E266VT | 78 | VoltageMesure | SIL0 | IEC104:M_ME_NA_1 | 10120 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10120 | 0 | 16 | aeiPWRBPSCL33KVBBVM_E266VTVoltageMesure | 4 |  |  | 0 | $ComStatus , , | #Voltage Measurement
282 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFBA | 33KVIFBA_E18 | 79 | ACFailRPLcc | SIL0 | IEC104:M_SP_NA_1 | 4160 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4160 | 0 | 1 | deiPWRBPSCLE1833KVIFBA_E18ACFailRPLcc | 4 |  |  | 0 | $ComStatus , , | #[ACFL] : AC Fail Relay Panel / LCC
283 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFBA | 33KVIFBA_E18 | 79 | DCFailRP | SIL0 | IEC104:M_SP_NA_1 | 4161 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4161 | 0 | 1 | deiPWRBPSCLE1833KVIFBA_E18DCFailRP | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : DC Fail Relay Panel
284 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFBA | 33KVIFBA_E18 | 79 | DCFailCell | SIL0 | IEC104:M_SP_NA_1 | 4162 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4162 | 0 | 1 | deiPWRBPSCLE1833KVIFBA_E18DCFailCell | 4 |  |  | 0 | $ComStatus , , | #[DCFA] : DC Fail Cell
285 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFBA | 33KVIFBA_E18 | 79 | WdgIedStatus | SIL0 | IEC104:M_SP_NA_1 | 4163 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4163 | 0 | 1 | deiPWRBPSCLE1833KVIFBA_E18WdgIedStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : IED WatchDog
286 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFBA | 33KVIFBA_E18 | 79 | WdgBcuStatus | SIL2_Monitoring | IEC104:M_SP_NA_1 | 4164 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 4164 | 0 | 1 | deiPWRBPSCLE1833KVIFBA_E18WdgBcuStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Watchdog
287 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFBA | 33KVIFBA_E18 | 79 | VoltTransStatus | SIL0 | IEC104:M_SP_NA_1 | 4165 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4165 | 0 | 1 | deiPWRBPSCLE1833KVIFBA_E18VoltTransStatus | 4 |  |  | 0 | $ComStatus , , | #[VTFA] : Voltage Transformer Fault alarm
288 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFBA | 33KVIFBA_E18 | 79 | WindTempTrip | SIL0 | IEC104:M_SP_NA_1 | 4166 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4166 | 0 | 1 | deiPWRBPSCLE1833KVIFBA_E18WindTempTrip | 4 |  |  | 0 | $ComStatus , , | #[WGTT] : 40MVA T-1 Winding Temperature Trip
289 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFBA | 33KVIFBA_E18 | 79 | WindTempAl | SIL0 | IEC104:M_SP_NA_1 | 4167 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4167 | 0 | 1 | deiPWRBPSCLE1833KVIFBA_E18WindTempAl | 4 |  |  | 0 | $ComStatus , , | #[WGTA] : 40MVA T-1 Winding Temperature Alarm
290 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFBA | 33KVIFBA_E18 | 79 | TapChLimit | SIL0 | IEC104:M_SP_NA_1 | 4168 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4168 | 0 | 1 | deiPWRBPSCLE1833KVIFBA_E18TapChLimit | 4 |  |  | 0 | $ComStatus , , | #[TCER] : Tap Changer Limit
291 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFBA | 33KVIFBA_E18 | 79 | TransfOilStatus | SIL0 | IEC104:M_SP_NA_1 | 4169 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4169 | 0 | 1 | deiPWRBPSCLE1833KVIFBA_E18TransfOilStatus | 4 |  |  | 0 | $ComStatus , , | #[MTOA] : Main Transformer Oil Level Alarm
292 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFBA | 33KVIFBA_E18 | 79 | TapChOilLevelAl | SIL0 | IEC104:M_SP_NA_1 | 4170 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4170 | 0 | 1 | deiPWRBPSCLE1833KVIFBA_E18TapChOilLevelAl | 4 |  |  | 0 | $ComStatus , , | #[TOLA] : Tap Changer Oil Level Alarm
293 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFBA | 33KVIFBA_E18 | 79 | FanAlarm | SIL0 | IEC104:M_SP_NA_1 | 4171 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4171 | 0 | 1 | deiPWRBPSCLE1833KVIFBA_E18FanAlarm | 4 |  |  | 0 | $ComStatus , , | #[FACA] : Transformer Fan Cooler Alarm
294 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFBA | 33KVIFBA_E18 | 79 | DehydratingAl | SIL0 | IEC104:M_SP_NA_1 | 4172 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4172 | 0 | 1 | deiPWRBPSCLE1833KVIFBA_E18DehydratingAl | 4 |  |  | 0 | $ComStatus , , | #[SSBA] : 40MVA T-1 Dehydrating Alarm
295 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFBA | 33KVIFBA_E18 | 79 | BCUCardFail | SIL0 | IEC104:M_SP_NA_1 | 4173 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4173 | 0 | 1 | deiPWRBPSCLE1833KVIFBA_E18BCUCardFail | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Card Fail
296 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFBA | 33KVIFBA_E28 | 80 | ACFailRPLcc | SIL0 | IEC104:M_SP_NA_1 | 4200 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4200 | 0 | 1 | deiPWRBPSCLE2833KVIFBA_E28ACFailRPLcc | 4 |  |  | 0 | $ComStatus , , | #[ACFL] : AC Fail Relay Panel / LCC
297 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFBA | 33KVIFBA_E28 | 80 | DCFailRP | SIL0 | IEC104:M_SP_NA_1 | 4201 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4201 | 0 | 1 | deiPWRBPSCLE2833KVIFBA_E28DCFailRP | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : DC Fail Relay Panel
298 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFBA | 33KVIFBA_E28 | 80 | DCFailCell | SIL0 | IEC104:M_SP_NA_1 | 4202 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4202 | 0 | 1 | deiPWRBPSCLE2833KVIFBA_E28DCFailCell | 4 |  |  | 0 | $ComStatus , , | #[DCFA] : DC Fail Cell
299 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFBA | 33KVIFBA_E28 | 80 | WdgIedStatus | SIL0 | IEC104:M_SP_NA_1 | 4203 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4203 | 0 | 1 | deiPWRBPSCLE2833KVIFBA_E28WdgIedStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : IED WatchDog
300 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFBA | 33KVIFBA_E28 | 80 | WdgBcuStatus | SIL2_Monitoring | IEC104:M_SP_NA_1 | 4204 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 4204 | 0 | 1 | deiPWRBPSCLE2833KVIFBA_E28WdgBcuStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Watchdog
301 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFBA | 33KVIFBA_E28 | 80 | VoltTransStatus | SIL0 | IEC104:M_SP_NA_1 | 4205 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4205 | 0 | 1 | deiPWRBPSCLE2833KVIFBA_E28VoltTransStatus | 4 |  |  | 0 | $ComStatus , , | #[VTFA] : Voltage Transformer Fault alarm
302 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFBA | 33KVIFBA_E28 | 80 | WindTempTrip | SIL0 | IEC104:M_SP_NA_1 | 4206 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4206 | 0 | 1 | deiPWRBPSCLE2833KVIFBA_E28WindTempTrip | 4 |  |  | 0 | $ComStatus , , | #[WGTT] : 40MVA T-1 Winding Temperature Trip
303 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFBA | 33KVIFBA_E28 | 80 | WindTempAl | SIL0 | IEC104:M_SP_NA_1 | 4207 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4207 | 0 | 1 | deiPWRBPSCLE2833KVIFBA_E28WindTempAl | 4 |  |  | 0 | $ComStatus , , | #[WGTA] : 40MVA T-1 Winding Temperature Alarm
304 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFBA | 33KVIFBA_E28 | 80 | TapChLimit | SIL0 | IEC104:M_SP_NA_1 | 4208 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4208 | 0 | 1 | deiPWRBPSCLE2833KVIFBA_E28TapChLimit | 4 |  |  | 0 | $ComStatus , , | #[TCER] : Tap Changer Limit
305 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFBA | 33KVIFBA_E28 | 80 | TransfOilStatus | SIL0 | IEC104:M_SP_NA_1 | 4209 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4209 | 0 | 1 | deiPWRBPSCLE2833KVIFBA_E28TransfOilStatus | 4 |  |  | 0 | $ComStatus , , | #[MTOA] : Main Transformer Oil Level Alarm
306 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFBA | 33KVIFBA_E28 | 80 | TapChOilLevelAl | SIL0 | IEC104:M_SP_NA_1 | 4210 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4210 | 0 | 1 | deiPWRBPSCLE2833KVIFBA_E28TapChOilLevelAl | 4 |  |  | 0 | $ComStatus , , | #[TOLA] : Tap Changer Oil Level Alarm
307 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFBA | 33KVIFBA_E28 | 80 | FanAlarm | SIL0 | IEC104:M_SP_NA_1 | 4211 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4211 | 0 | 1 | deiPWRBPSCLE2833KVIFBA_E28FanAlarm | 4 |  |  | 0 | $ComStatus , , | #[FACA] : Transformer Fan Cooler Alarm
308 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFBA | 33KVIFBA_E28 | 80 | DehydratingAl | SIL0 | IEC104:M_SP_NA_1 | 4212 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4212 | 0 | 1 | deiPWRBPSCLE2833KVIFBA_E28DehydratingAl | 4 |  |  | 0 | $ComStatus , , | #[SSBA] : 40MVA T-1 Dehydrating Alarm
309 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFBA | 33KVIFBA_E28 | 80 | BCUCardFail | SIL0 | IEC104:M_SP_NA_1 | 4213 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4213 | 0 | 1 | deiPWRBPSCLE2833KVIFBA_E28BCUCardFail | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Card Fail
310 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFPR | 33KVIFPR_E180 | 81 | DirCurTrip | SIL0 | IEC104:M_SP_NA_1 | 4240 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4240 | 0 | 1 | deiPWRBPSCLE1833KVIFPR_E180DirCurTrip | 4 |  |  | 0 | $ComStatus , , | #[DOEP] : Dir Overcurrent I>Trip
311 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFPR | 33KVIFPR_E180 | 81 | LVRefTrip | SIL0 | IEC104:M_SP_NA_1 | 4241 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4241 | 0 | 1 | deiPWRBPSCLE1833KVIFPR_E180LVRefTrip | 4 |  |  | 0 | $ComStatus , , | #[REPO] : 40MVA-T1 LV REF Trip
312 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFPR | 33KVIFPR_E180 | 81 | TripInGTStage1 | SIL0 | IEC104:M_SP_NA_1 | 4242 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4242 | 0 | 1 | deiPWRBPSCLE1833KVIFPR_E180TripInGTStage1 | 4 |  |  | 0 | $ComStatus , , | #[SBE1] : Standby EF In>St-1 Trip
313 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFPR | 33KVIFPR_E180 | 81 | TripInGTStage2 | SIL0 | IEC104:M_SP_NA_1 | 4243 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4243 | 0 | 1 | deiPWRBPSCLE1833KVIFPR_E180TripInGTStage2 | 4 |  |  | 0 | $ComStatus , , | #[SBE2] : Standby EF In>St-2 Trip
314 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFPR | 33KVIFPR_E180 | 81 | StartInGTAI | SIL0 | IEC104:M_SP_NA_1 | 4244 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4244 | 0 | 1 | deiPWRBPSCLE1833KVIFPR_E180StartInGTAI | 4 |  |  | 0 | $ComStatus , , | #[SBES] : Standby EF In>Start
315 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFPR | 33KVIFPR_E180 | 81 | NERFail | SIL0 | IEC104:M_SP_NA_1 | 4245 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4245 | 0 | 1 | deiPWRBPSCLE1833KVIFPR_E180NERFail | 4 |  |  | 0 | $ComStatus , , | #[NERF] : NER Faulty
316 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFPR | 33KVIFPR_E180 | 81 | GroundFault | SIL0 | IEC104:M_SP_NA_1 | 4246 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4246 | 0 | 1 | deiPWRBPSCLE1833KVIFPR_E180GroundFault | 4 |  |  | 0 | $ComStatus , , | #[NERG] : NER Ground Fault
317 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFPR | 33KVIFPR_E180 | 81 | MonitorUnHlthy | SIL0 | IEC104:M_SP_NA_1 | 4247 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4247 | 0 | 1 | deiPWRBPSCLE1833KVIFPR_E180MonitorUnHlthy | 4 |  |  | 0 | $ComStatus , , | #[NERM] : NER Monitor Unhealthy
318 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFPR | 33KVIFPR_E280 | 82 | DirCurTrip | SIL0 | IEC104:M_SP_NA_1 | 4280 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4280 | 0 | 1 | deiPWRBPSCLE2833KVIFPR_E280DirCurTrip | 4 |  |  | 0 | $ComStatus , , | #[DOEP] : Dir Overcurrent I>Trip
319 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFPR | 33KVIFPR_E280 | 82 | LVRefTrip | SIL0 | IEC104:M_SP_NA_1 | 4281 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4281 | 0 | 1 | deiPWRBPSCLE2833KVIFPR_E280LVRefTrip | 4 |  |  | 0 | $ComStatus , , | #[REPO] : 40MVA-T1 LV REF Trip
320 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFPR | 33KVIFPR_E280 | 82 | TripInGTStage1 | SIL0 | IEC104:M_SP_NA_1 | 4282 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4282 | 0 | 1 | deiPWRBPSCLE2833KVIFPR_E280TripInGTStage1 | 4 |  |  | 0 | $ComStatus , , | #[SBE1] : Standby EF In>St-1 Trip
321 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFPR | 33KVIFPR_E280 | 82 | TripInGTStage2 | SIL0 | IEC104:M_SP_NA_1 | 4283 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4283 | 0 | 1 | deiPWRBPSCLE2833KVIFPR_E280TripInGTStage2 | 4 |  |  | 0 | $ComStatus , , | #[SBE2] : Standby EF In>St-2 Trip
322 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFPR | 33KVIFPR_E280 | 82 | StartInGTAI | SIL0 | IEC104:M_SP_NA_1 | 4284 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4284 | 0 | 1 | deiPWRBPSCLE2833KVIFPR_E280StartInGTAI | 4 |  |  | 0 | $ComStatus , , | #[SBES] : Standby EF In>Start
323 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFPR | 33KVIFPR_E280 | 82 | NERFail | SIL0 | IEC104:M_SP_NA_1 | 4285 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4285 | 0 | 1 | deiPWRBPSCLE2833KVIFPR_E280NERFail | 4 |  |  | 0 | $ComStatus , , | #[NERF] : NER Faulty
324 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFPR | 33KVIFPR_E280 | 82 | GroundFault | SIL0 | IEC104:M_SP_NA_1 | 4286 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4286 | 0 | 1 | deiPWRBPSCLE2833KVIFPR_E280GroundFault | 4 |  |  | 0 | $ComStatus , , | #[NERG] : NER Ground Fault
325 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFPR | 33KVIFPR_E280 | 82 | MonitorUnHlthy | SIL0 | IEC104:M_SP_NA_1 | 4287 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4287 | 0 | 1 | deiPWRBPSCLE2833KVIFPR_E280MonitorUnHlthy | 4 |  |  | 0 | $ComStatus , , | #[NERM] : NER Monitor Unhealthy
326 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFMV | 33KVIFMV_E18 | 83 | RPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 10320 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10320 | 0 | 16 | aeiPWRBPSCLE1833KVIFMV_E18RPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #R Phase Current
327 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFMV | 33KVIFMV_E18 | 83 | YPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 10321 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10321 | 0 | 16 | aeiPWRBPSCLE1833KVIFMV_E18YPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #Y Phase Current
328 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFMV | 33KVIFMV_E18 | 83 | BPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 10322 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10322 | 0 | 16 | aeiPWRBPSCLE1833KVIFMV_E18BPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #B Phase Current
329 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFMV | 33KVIFMV_E18 | 83 | NeutralCur | SIL0 | IEC104:M_ME_NA_1 | 10323 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10323 | 0 | 16 | aeiPWRBPSCLE1833KVIFMV_E18NeutralCur | 4 |  |  | 0 | $ComStatus , , | #Neutral Current (In)
330 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFMV | 33KVIFMV_E18 | 83 | RYPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 10324 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10324 | 0 | 16 | aeiPWRBPSCLE1833KVIFMV_E18RYPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #RY Phase Voltage
331 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFMV | 33KVIFMV_E18 | 83 | YBPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 10325 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10325 | 0 | 16 | aeiPWRBPSCLE1833KVIFMV_E18YBPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #YB Phase Voltage
332 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFMV | 33KVIFMV_E18 | 83 | BRPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 10326 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10326 | 0 | 16 | aeiPWRBPSCLE1833KVIFMV_E18BRPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #BR Phase Voltage
333 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFMV | 33KVIFMV_E18 | 83 | ZeroSeqVolt | SIL0 | IEC104:M_ME_NA_1 | 10327 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10327 | 0 | 16 | aeiPWRBPSCLE1833KVIFMV_E18ZeroSeqVolt | 4 |  |  | 0 | $ComStatus , , | #Zero Sequence Voltage (V0)
334 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFMV | 33KVIFMV_E18 | 83 | ActivePower | SIL0 | IEC104:M_ME_NA_1 | 10328 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10328 | 0 | 16 | aeiPWRBPSCLE1833KVIFMV_E18ActivePower | 4 |  |  | 0 | $ComStatus , , | #[MW] : Active Power
335 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFMV | 33KVIFMV_E18 | 83 | ReacPower | SIL0 | IEC104:M_ME_NA_1 | 10329 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10329 | 0 | 16 | aeiPWRBPSCLE1833KVIFMV_E18ReacPower | 4 |  |  | 0 | $ComStatus , , | #[MVAR] : Reactive Power
336 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFMV | 33KVIFMV_E18 | 83 | AppPower | SIL0 | IEC104:M_ME_NA_1 | 10330 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10330 | 0 | 16 | aeiPWRBPSCLE1833KVIFMV_E18AppPower | 4 |  |  | 0 | $ComStatus , , | #Apparent Power (S)
337 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFMV | 33KVIFMV_E18 | 83 | PowerFactor | SIL0 | IEC104:M_ME_NA_1 | 10331 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10331 | 0 | 16 | aeiPWRBPSCLE1833KVIFMV_E18PowerFactor | 4 |  |  | 0 | $ComStatus , , | #Power Factor (P.F)
338 | BPS01_RTU | PWR:BPS:CL | E18 | 33KVIFMV | 33KVIFMV_E18 | 83 | Frequency | SIL0 | IEC104:M_ME_NA_1 | 10332 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10332 | 0 | 16 | aeiPWRBPSCLE1833KVIFMV_E18Frequency | 4 |  |  | 0 | $ComStatus , , | #Frequency (Hz)
339 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFMV | 33KVIFMV_E28 | 84 | RPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 10360 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10360 | 0 | 16 | aeiPWRBPSCLE2833KVIFMV_E28RPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #R Phase Current
340 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFMV | 33KVIFMV_E28 | 84 | YPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 10361 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10361 | 0 | 16 | aeiPWRBPSCLE2833KVIFMV_E28YPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #Y Phase Current
341 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFMV | 33KVIFMV_E28 | 84 | BPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 10362 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10362 | 0 | 16 | aeiPWRBPSCLE2833KVIFMV_E28BPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #B Phase Current
342 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFMV | 33KVIFMV_E28 | 84 | NeutralCur | SIL0 | IEC104:M_ME_NA_1 | 10363 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10363 | 0 | 16 | aeiPWRBPSCLE2833KVIFMV_E28NeutralCur | 4 |  |  | 0 | $ComStatus , , | #Neutral Current (In)
343 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFMV | 33KVIFMV_E28 | 84 | RYPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 10364 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10364 | 0 | 16 | aeiPWRBPSCLE2833KVIFMV_E28RYPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #RY Phase Voltage
344 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFMV | 33KVIFMV_E28 | 84 | YBPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 10365 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10365 | 0 | 16 | aeiPWRBPSCLE2833KVIFMV_E28YBPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #YB Phase Voltage
345 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFMV | 33KVIFMV_E28 | 84 | BRPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 10366 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10366 | 0 | 16 | aeiPWRBPSCLE2833KVIFMV_E28BRPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #BR Phase Voltage
346 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFMV | 33KVIFMV_E28 | 84 | ZeroSeqVolt | SIL0 | IEC104:M_ME_NA_1 | 10367 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10367 | 0 | 16 | aeiPWRBPSCLE2833KVIFMV_E28ZeroSeqVolt | 4 |  |  | 0 | $ComStatus , , | #Zero Sequence Voltage (V0)
347 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFMV | 33KVIFMV_E28 | 84 | ActivePower | SIL0 | IEC104:M_ME_NA_1 | 10368 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10368 | 0 | 16 | aeiPWRBPSCLE2833KVIFMV_E28ActivePower | 4 |  |  | 0 | $ComStatus , , | #[MW] : Active Power
348 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFMV | 33KVIFMV_E28 | 84 | ReacPower | SIL0 | IEC104:M_ME_NA_1 | 10369 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10369 | 0 | 16 | aeiPWRBPSCLE2833KVIFMV_E28ReacPower | 4 |  |  | 0 | $ComStatus , , | #[MVAR] : Reactive Power
349 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFMV | 33KVIFMV_E28 | 84 | AppPower | SIL0 | IEC104:M_ME_NA_1 | 10370 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10370 | 0 | 16 | aeiPWRBPSCLE2833KVIFMV_E28AppPower | 4 |  |  | 0 | $ComStatus , , | #Apparent Power (S)
350 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFMV | 33KVIFMV_E28 | 84 | PowerFactor | SIL0 | IEC104:M_ME_NA_1 | 10371 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10371 | 0 | 16 | aeiPWRBPSCLE2833KVIFMV_E28PowerFactor | 4 |  |  | 0 | $ComStatus , , | #Power Factor (P.F)
351 | BPS01_RTU | PWR:BPS:CL | E28 | 33KVIFMV | 33KVIFMV_E28 | 84 | Frequency | SIL0 | IEC104:M_ME_NA_1 | 10372 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 10372 | 0 | 16 | aeiPWRBPSCLE2833KVIFMV_E28Frequency | 4 |  |  | 0 | $ComStatus , , | #Frequency (Hz)
352 | BPS01_RTU | PWR:BPS:CL | E18 | ISST | ISST_E184 | 85 | BusIsolStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 5700 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 5700 | 0 | 2 | deiPWRBPSCLE18ISST_E184BusIsolStatus | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
353 | BPS01_RTU | PWR:BPS:CL | E18 | ISST | ISST_E184 | 85 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 26700 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26700 | 0 | 2 | deoPWRBPSCLE18ISST_E184CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Open
354 | BPS01_RTU | PWR:BPS:CL | E18 | ISST | ISST_E184 | 85 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26700 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26700 | 4 | 2 | deiPWRBPSCLE18ISST_E184AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open Ack
355 | BPS01_RTU | PWR:BPS:CL | E18 | ISST | ISST_E184 | 85 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 26700 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26700 | 0 | 2 | deoPWRBPSCLE18ISST_E184CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open
356 | BPS01_RTU | PWR:BPS:CL | E18 | ISST | ISST_E184 | 85 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26700 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26700 | 2 | 2 | deiPWRBPSCLE18ISST_E184AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Open Ack
357 | BPS01_RTU | PWR:BPS:CL | E18 | ISST | ISST_E184 | 85 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 26700 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26700 | 0 | 2 | deoPWRBPSCLE18ISST_E184CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Close
358 | BPS01_RTU | PWR:BPS:CL | E18 | ISST | ISST_E184 | 85 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26700 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26700 | 4 | 2 | deiPWRBPSCLE18ISST_E184AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close Ack
359 | BPS01_RTU | PWR:BPS:CL | E18 | ISST | ISST_E184 | 85 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 26700 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26700 | 0 | 2 | deoPWRBPSCLE18ISST_E184CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close
360 | BPS01_RTU | PWR:BPS:CL | E18 | ISST | ISST_E184 | 85 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26700 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26700 | 2 | 2 | deiPWRBPSCLE18ISST_E184AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Close Ack
361 | BPS01_RTU | PWR:BPS:CL | E28 | ISST | ISST_E284 | 86 | BusIsolStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 5720 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 5720 | 0 | 2 | deiPWRBPSCLE28ISST_E284BusIsolStatus | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
362 | BPS01_RTU | PWR:BPS:CL | E28 | ISST | ISST_E284 | 86 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 26720 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26720 | 0 | 2 | deoPWRBPSCLE28ISST_E284CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Open
363 | BPS01_RTU | PWR:BPS:CL | E28 | ISST | ISST_E284 | 86 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26720 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26720 | 4 | 2 | deiPWRBPSCLE28ISST_E284AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open Ack
364 | BPS01_RTU | PWR:BPS:CL | E28 | ISST | ISST_E284 | 86 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 26720 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26720 | 0 | 2 | deoPWRBPSCLE28ISST_E284CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open
365 | BPS01_RTU | PWR:BPS:CL | E28 | ISST | ISST_E284 | 86 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26720 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26720 | 2 | 2 | deiPWRBPSCLE28ISST_E284AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Open Ack
366 | BPS01_RTU | PWR:BPS:CL | E28 | ISST | ISST_E284 | 86 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 26720 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26720 | 0 | 2 | deoPWRBPSCLE28ISST_E284CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Close
367 | BPS01_RTU | PWR:BPS:CL | E28 | ISST | ISST_E284 | 86 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26720 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26720 | 4 | 2 | deiPWRBPSCLE28ISST_E284AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close Ack
368 | BPS01_RTU | PWR:BPS:CL | E28 | ISST | ISST_E284 | 86 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 26720 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26720 | 0 | 2 | deoPWRBPSCLE28ISST_E284CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close
369 | BPS01_RTU | PWR:BPS:CL | E28 | ISST | ISST_E284 | 86 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26720 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26720 | 2 | 2 | deiPWRBPSCLE28ISST_E284AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Close Ack
370 | BPS01_RTU | PWR:BPS:CL | E18 | ESST | E18M1 | 87 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 5740 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 5740 | 0 | 2 | deiPWRBPSCLE18E18M1EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
371 | BPS01_RTU | PWR:BPS:CL | E18 | ESST | E18M1 | 87 | CmdOpen | SIL0 | IEC104:C_DC_NA_1 | 26740 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 26740 | 0 | 2 | deoPWRBPSCLE18E18M1CmdOpen | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Open
372 | BPS01_RTU | PWR:BPS:CL | E18 | ESST | E18M1 | 87 | CmdClose | SIL0 | IEC104:C_DC_NA_1 | 26740 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 26740 | 0 | 2 | deoPWRBPSCLE18E18M1CmdClose | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Close
373 | BPS01_RTU | PWR:BPS:CL | E28 | ESST | E28M1 | 88 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 5760 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 5760 | 0 | 2 | deiPWRBPSCLE28E28M1EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
374 | BPS01_RTU | PWR:BPS:CL | E28 | ESST | E28M1 | 88 | CmdOpen | SIL0 | IEC104:C_DC_NA_1 | 26760 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 26760 | 0 | 2 | deoPWRBPSCLE28E28M1CmdOpen | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Open
375 | BPS01_RTU | PWR:BPS:CL | E28 | ESST | E28M1 | 88 | CmdClose | SIL0 | IEC104:C_DC_NA_1 | 26760 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 26760 | 0 | 2 | deoPWRBPSCLE28E28M1CmdClose | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Close
376 | BPS01_RTU | PWR:BPS:CL | E18 | CB | E180 | 89 | CirBrkStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 5780 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 5780 | 0 | 2 | deiPWRBPSCLE18E180CirBrkStatus | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Status
377 | BPS01_RTU | PWR:BPS:CL | E18 | CB | E180 | 89 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 26780 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26780 | 0 | 2 | deoPWRBPSCLE18E180CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Open
378 | BPS01_RTU | PWR:BPS:CL | E18 | CB | E180 | 89 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26780 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26780 | 4 | 2 | deiPWRBPSCLE18E180AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open Ack
379 | BPS01_RTU | PWR:BPS:CL | E18 | CB | E180 | 89 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 26780 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26780 | 0 | 2 | deoPWRBPSCLE18E180CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open
380 | BPS01_RTU | PWR:BPS:CL | E18 | CB | E180 | 89 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26780 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26780 | 2 | 2 | deiPWRBPSCLE18E180AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Open Ack
381 | BPS01_RTU | PWR:BPS:CL | E18 | CB | E180 | 89 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 26780 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26780 | 0 | 2 | deoPWRBPSCLE18E180CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Close
382 | BPS01_RTU | PWR:BPS:CL | E18 | CB | E180 | 89 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26780 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26780 | 4 | 2 | deiPWRBPSCLE18E180AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close Ack
383 | BPS01_RTU | PWR:BPS:CL | E18 | CB | E180 | 89 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 26780 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26780 | 0 | 2 | deoPWRBPSCLE18E180CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close
384 | BPS01_RTU | PWR:BPS:CL | E18 | CB | E180 | 89 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26780 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26780 | 2 | 2 | deiPWRBPSCLE18E180AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Close Ack
385 | BPS01_RTU | PWR:BPS:CL | E28 | CB | E280 | 90 | CirBrkStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 5800 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 5800 | 0 | 2 | deiPWRBPSCLE28E280CirBrkStatus | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Status
386 | BPS01_RTU | PWR:BPS:CL | E28 | CB | E280 | 90 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 26800 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26800 | 0 | 2 | deoPWRBPSCLE28E280CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Open
387 | BPS01_RTU | PWR:BPS:CL | E28 | CB | E280 | 90 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26800 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26800 | 4 | 2 | deiPWRBPSCLE28E280AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open Ack
388 | BPS01_RTU | PWR:BPS:CL | E28 | CB | E280 | 90 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 26800 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26800 | 0 | 2 | deoPWRBPSCLE28E280CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open
389 | BPS01_RTU | PWR:BPS:CL | E28 | CB | E280 | 90 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26800 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26800 | 2 | 2 | deiPWRBPSCLE28E280AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Open Ack
390 | BPS01_RTU | PWR:BPS:CL | E28 | CB | E280 | 90 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 26800 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26800 | 0 | 2 | deoPWRBPSCLE28E280CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Close
391 | BPS01_RTU | PWR:BPS:CL | E28 | CB | E280 | 90 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26800 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26800 | 4 | 2 | deiPWRBPSCLE28E280AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close Ack
392 | BPS01_RTU | PWR:BPS:CL | E28 | CB | E280 | 90 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 26800 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26800 | 0 | 2 | deoPWRBPSCLE28E280CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close
393 | BPS01_RTU | PWR:BPS:CL | E28 | CB | E280 | 90 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26800 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26800 | 2 | 2 | deiPWRBPSCLE28E280AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Close Ack
394 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTBA | 33KVSTBA_E10 | 91 | ACFailRPSwgr | SIL0 | IEC104:M_SP_NA_1 | 4640 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4640 | 0 | 1 | deiPWRBPSCLE1033KVSTBA_E10ACFailRPSwgr | 4 |  |  | 0 | $ComStatus , , | #[ACFL] : AC Fail Relay Panel / SWGR
395 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTBA | 33KVSTBA_E10 | 91 | DCFailRP | SIL0 | IEC104:M_SP_NA_1 | 4641 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4641 | 0 | 1 | deiPWRBPSCLE1033KVSTBA_E10DCFailRP | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : DC Fail Relay Panel
396 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTBA | 33KVSTBA_E10 | 91 | DCFailSwgr | SIL0 | IEC104:M_SP_NA_1 | 4642 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4642 | 0 | 1 | deiPWRBPSCLE1033KVSTBA_E10DCFailSwgr | 4 |  |  | 0 | $ComStatus , , | #[DCFA] : DC Fail SWGR
397 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTBA | 33KVSTBA_E10 | 91 | WdgIedStatus | SIL0 | IEC104:M_SP_NA_1 | 4643 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4643 | 0 | 1 | deiPWRBPSCLE1033KVSTBA_E10WdgIedStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : IED WatchDog
398 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTBA | 33KVSTBA_E10 | 91 | WdgBcuStatus | SIL2_Monitoring | IEC104:M_SP_NA_1 | 4644 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 4644 | 0 | 1 | deiPWRBPSCLE1033KVSTBA_E10WdgBcuStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Watchdog
399 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTBA | 33KVSTBA_E10 | 91 | VoltTransStatus | SIL0 | IEC104:M_SP_NA_1 | 4645 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4645 | 0 | 1 | deiPWRBPSCLE1033KVSTBA_E10VoltTransStatus | 4 |  |  | 0 | $ComStatus , , | #[VTFA] : Voltage Transformer Fault alarm
400 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTBA | 33KVSTBA_E10 | 91 | BCUCardFail | SIL0 | IEC104:M_SP_NA_1 | 4646 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4646 | 0 | 1 | deiPWRBPSCLE1033KVSTBA_E10BCUCardFail | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Card Fail
401 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTBA | 33KVSTBA_E20 | 92 | ACFailRPSwgr | SIL0 | IEC104:M_SP_NA_1 | 4680 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4680 | 0 | 1 | deiPWRBPSCLE2033KVSTBA_E20ACFailRPSwgr | 4 |  |  | 0 | $ComStatus , , | #[ACFL] : AC Fail Relay Panel / SWGR
402 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTBA | 33KVSTBA_E20 | 92 | DCFailRP | SIL0 | IEC104:M_SP_NA_1 | 4681 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4681 | 0 | 1 | deiPWRBPSCLE2033KVSTBA_E20DCFailRP | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : DC Fail Relay Panel
403 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTBA | 33KVSTBA_E20 | 92 | DCFailSwgr | SIL0 | IEC104:M_SP_NA_1 | 4682 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4682 | 0 | 1 | deiPWRBPSCLE2033KVSTBA_E20DCFailSwgr | 4 |  |  | 0 | $ComStatus , , | #[DCFA] : DC Fail SWGR
404 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTBA | 33KVSTBA_E20 | 92 | WdgIedStatus | SIL0 | IEC104:M_SP_NA_1 | 4683 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4683 | 0 | 1 | deiPWRBPSCLE2033KVSTBA_E20WdgIedStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : IED WatchDog
405 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTBA | 33KVSTBA_E20 | 92 | WdgBcuStatus | SIL2_Monitoring | IEC104:M_SP_NA_1 | 4684 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 4684 | 0 | 1 | deiPWRBPSCLE2033KVSTBA_E20WdgBcuStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Watchdog
406 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTBA | 33KVSTBA_E20 | 92 | VoltTransStatus | SIL0 | IEC104:M_SP_NA_1 | 4685 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4685 | 0 | 1 | deiPWRBPSCLE2033KVSTBA_E20VoltTransStatus | 4 |  |  | 0 | $ComStatus , , | #[VTFA] : Voltage Transformer Fault alarm
407 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTBA | 33KVSTBA_E20 | 92 | BCUCardFail | SIL0 | IEC104:M_SP_NA_1 | 4686 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 4686 | 0 | 1 | deiPWRBPSCLE2033KVSTBA_E20BCUCardFail | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Card Fail
408 | BPS01_RTU | PWR:BPS:CL | E10 | ISST | ISST_E164 | 93 | BusIsolStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 5860 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 5860 | 0 | 2 | deiPWRBPSCLE10ISST_E164BusIsolStatus | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
409 | BPS01_RTU | PWR:BPS:CL | E10 | ISST | ISST_E164 | 93 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 26860 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26860 | 0 | 2 | deoPWRBPSCLE10ISST_E164CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Open
410 | BPS01_RTU | PWR:BPS:CL | E10 | ISST | ISST_E164 | 93 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26860 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26860 | 4 | 2 | deiPWRBPSCLE10ISST_E164AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open Ack
411 | BPS01_RTU | PWR:BPS:CL | E10 | ISST | ISST_E164 | 93 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 26860 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26860 | 0 | 2 | deoPWRBPSCLE10ISST_E164CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open
412 | BPS01_RTU | PWR:BPS:CL | E10 | ISST | ISST_E164 | 93 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26860 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26860 | 2 | 2 | deiPWRBPSCLE10ISST_E164AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Open Ack
413 | BPS01_RTU | PWR:BPS:CL | E10 | ISST | ISST_E164 | 93 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 26860 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26860 | 0 | 2 | deoPWRBPSCLE10ISST_E164CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Close
414 | BPS01_RTU | PWR:BPS:CL | E10 | ISST | ISST_E164 | 93 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26860 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26860 | 4 | 2 | deiPWRBPSCLE10ISST_E164AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close Ack
415 | BPS01_RTU | PWR:BPS:CL | E10 | ISST | ISST_E164 | 93 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 26860 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26860 | 0 | 2 | deoPWRBPSCLE10ISST_E164CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close
416 | BPS01_RTU | PWR:BPS:CL | E10 | ISST | ISST_E164 | 93 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26860 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26860 | 2 | 2 | deiPWRBPSCLE10ISST_E164AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Close Ack
417 | BPS01_RTU | PWR:BPS:CL | E20 | ISST | ISST_E264 | 94 | BusIsolStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 5880 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 5880 | 0 | 2 | deiPWRBPSCLE20ISST_E264BusIsolStatus | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
418 | BPS01_RTU | PWR:BPS:CL | E20 | ISST | ISST_E264 | 94 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 26880 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26880 | 0 | 2 | deoPWRBPSCLE20ISST_E264CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Open
419 | BPS01_RTU | PWR:BPS:CL | E20 | ISST | ISST_E264 | 94 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26880 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26880 | 4 | 2 | deiPWRBPSCLE20ISST_E264AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open Ack
420 | BPS01_RTU | PWR:BPS:CL | E20 | ISST | ISST_E264 | 94 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 26880 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26880 | 0 | 2 | deoPWRBPSCLE20ISST_E264CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open
421 | BPS01_RTU | PWR:BPS:CL | E20 | ISST | ISST_E264 | 94 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26880 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26880 | 2 | 2 | deiPWRBPSCLE20ISST_E264AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Open Ack
422 | BPS01_RTU | PWR:BPS:CL | E20 | ISST | ISST_E264 | 94 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 26880 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26880 | 0 | 2 | deoPWRBPSCLE20ISST_E264CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Close
423 | BPS01_RTU | PWR:BPS:CL | E20 | ISST | ISST_E264 | 94 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26880 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26880 | 4 | 2 | deiPWRBPSCLE20ISST_E264AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close Ack
424 | BPS01_RTU | PWR:BPS:CL | E20 | ISST | ISST_E264 | 94 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 26880 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26880 | 0 | 2 | deoPWRBPSCLE20ISST_E264CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close
425 | BPS01_RTU | PWR:BPS:CL | E20 | ISST | ISST_E264 | 94 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26880 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26880 | 2 | 2 | deiPWRBPSCLE20ISST_E264AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Close Ack
426 | BPS01_RTU | PWR:BPS:CL | E10 | ISST | ISST_E104 | 95 | BusIsolStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 5900 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 5900 | 0 | 2 | deiPWRBPSCLE10ISST_E104BusIsolStatus | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
427 | BPS01_RTU | PWR:BPS:CL | E10 | ISST | ISST_E104 | 95 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 26900 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26900 | 0 | 2 | deoPWRBPSCLE10ISST_E104CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Open
428 | BPS01_RTU | PWR:BPS:CL | E10 | ISST | ISST_E104 | 95 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26900 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26900 | 4 | 2 | deiPWRBPSCLE10ISST_E104AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open Ack
429 | BPS01_RTU | PWR:BPS:CL | E10 | ISST | ISST_E104 | 95 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 26900 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26900 | 0 | 2 | deoPWRBPSCLE10ISST_E104CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open
430 | BPS01_RTU | PWR:BPS:CL | E10 | ISST | ISST_E104 | 95 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26900 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26900 | 2 | 2 | deiPWRBPSCLE10ISST_E104AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Open Ack
431 | BPS01_RTU | PWR:BPS:CL | E10 | ISST | ISST_E104 | 95 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 26900 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26900 | 0 | 2 | deoPWRBPSCLE10ISST_E104CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Close
432 | BPS01_RTU | PWR:BPS:CL | E10 | ISST | ISST_E104 | 95 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26900 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26900 | 4 | 2 | deiPWRBPSCLE10ISST_E104AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close Ack
433 | BPS01_RTU | PWR:BPS:CL | E10 | ISST | ISST_E104 | 95 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 26900 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26900 | 0 | 2 | deoPWRBPSCLE10ISST_E104CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close
434 | BPS01_RTU | PWR:BPS:CL | E10 | ISST | ISST_E104 | 95 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26900 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26900 | 2 | 2 | deiPWRBPSCLE10ISST_E104AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Close Ack
435 | BPS01_RTU | PWR:BPS:CL | E20 | ISST | ISST_E204 | 96 | BusIsolStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 5920 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 5920 | 0 | 2 | deiPWRBPSCLE20ISST_E204BusIsolStatus | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
436 | BPS01_RTU | PWR:BPS:CL | E20 | ISST | ISST_E204 | 96 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 26920 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26920 | 0 | 2 | deoPWRBPSCLE20ISST_E204CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Open
437 | BPS01_RTU | PWR:BPS:CL | E20 | ISST | ISST_E204 | 96 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26920 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26920 | 4 | 2 | deiPWRBPSCLE20ISST_E204AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open Ack
438 | BPS01_RTU | PWR:BPS:CL | E20 | ISST | ISST_E204 | 96 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 26920 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26920 | 0 | 2 | deoPWRBPSCLE20ISST_E204CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open
439 | BPS01_RTU | PWR:BPS:CL | E20 | ISST | ISST_E204 | 96 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26920 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26920 | 2 | 2 | deiPWRBPSCLE20ISST_E204AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Open Ack
440 | BPS01_RTU | PWR:BPS:CL | E20 | ISST | ISST_E204 | 96 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 26920 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26920 | 0 | 2 | deoPWRBPSCLE20ISST_E204CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Close
441 | BPS01_RTU | PWR:BPS:CL | E20 | ISST | ISST_E204 | 96 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26920 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26920 | 4 | 2 | deiPWRBPSCLE20ISST_E204AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close Ack
442 | BPS01_RTU | PWR:BPS:CL | E20 | ISST | ISST_E204 | 96 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 26920 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 26920 | 0 | 2 | deoPWRBPSCLE20ISST_E204CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close
443 | BPS01_RTU | PWR:BPS:CL | E20 | ISST | ISST_E204 | 96 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 26920 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 26920 | 2 | 2 | deiPWRBPSCLE20ISST_E204AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Close Ack
444 | BPS01_RTU | PWR:BPS:CL | E10 | ESST | E16M1 | 97 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 5940 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 5940 | 0 | 2 | deiPWRBPSCLE10E16M1EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
445 | BPS01_RTU | PWR:BPS:CL | E10 | ESST | E16M1 | 97 | CmdOpen | SIL0 | IEC104:C_DC_NA_1 | 26940 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 26940 | 0 | 2 | deoPWRBPSCLE10E16M1CmdOpen | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Open
446 | BPS01_RTU | PWR:BPS:CL | E10 | ESST | E16M1 | 97 | CmdClose | SIL0 | IEC104:C_DC_NA_1 | 26940 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 26940 | 0 | 2 | deoPWRBPSCLE10E16M1CmdClose | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Close
447 | BPS01_RTU | PWR:BPS:CL | E20 | ESST | E26M1 | 98 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 5960 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 5960 | 0 | 2 | deiPWRBPSCLE20E26M1EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
448 | BPS01_RTU | PWR:BPS:CL | E20 | ESST | E26M1 | 98 | CmdOpen | SIL0 | IEC104:C_DC_NA_1 | 26960 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 26960 | 0 | 2 | deoPWRBPSCLE20E26M1CmdOpen | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Open
449 | BPS01_RTU | PWR:BPS:CL | E20 | ESST | E26M1 | 98 | CmdClose | SIL0 | IEC104:C_DC_NA_1 | 26960 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 26960 | 0 | 2 | deoPWRBPSCLE20E26M1CmdClose | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Close
450 | BPS01_RTU | PWR:BPS:CL | E10 | ESST | E10M1 | 99 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 5980 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 5980 | 0 | 2 | deiPWRBPSCLE10E10M1EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
451 | BPS01_RTU | PWR:BPS:CL | E10 | ESST | E10M1 | 99 | CmdOpen | SIL0 | IEC104:C_DC_NA_1 | 26980 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 26980 | 0 | 2 | deoPWRBPSCLE10E10M1CmdOpen | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Open
452 | BPS01_RTU | PWR:BPS:CL | E10 | ESST | E10M1 | 99 | CmdClose | SIL0 | IEC104:C_DC_NA_1 | 26980 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 26980 | 0 | 2 | deoPWRBPSCLE10E10M1CmdClose | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Close
453 | BPS01_RTU | PWR:BPS:CL | E20 | ESST | E20M1 | 100 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 6000 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 6000 | 0 | 2 | deiPWRBPSCLE20E20M1EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
454 | BPS01_RTU | PWR:BPS:CL | E20 | ESST | E20M1 | 100 | CmdOpen | SIL0 | IEC104:C_DC_NA_1 | 27000 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27000 | 0 | 2 | deoPWRBPSCLE20E20M1CmdOpen | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Open
455 | BPS01_RTU | PWR:BPS:CL | E20 | ESST | E20M1 | 100 | CmdClose | SIL0 | IEC104:C_DC_NA_1 | 27000 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27000 | 0 | 2 | deoPWRBPSCLE20E20M1CmdClose | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Close
456 | BPS01_RTU | PWR:BPS:CL | E10 | CB | E100 | 101 | CirBrkStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 6020 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 6020 | 0 | 2 | deiPWRBPSCLE10E100CirBrkStatus | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Status
457 | BPS01_RTU | PWR:BPS:CL | E10 | CB | E100 | 101 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27020 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27020 | 0 | 2 | deoPWRBPSCLE10E100CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Open
458 | BPS01_RTU | PWR:BPS:CL | E10 | CB | E100 | 101 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27020 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27020 | 4 | 2 | deiPWRBPSCLE10E100AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open Ack
459 | BPS01_RTU | PWR:BPS:CL | E10 | CB | E100 | 101 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27020 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27020 | 0 | 2 | deoPWRBPSCLE10E100CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open
460 | BPS01_RTU | PWR:BPS:CL | E10 | CB | E100 | 101 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27020 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27020 | 2 | 2 | deiPWRBPSCLE10E100AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Open Ack
461 | BPS01_RTU | PWR:BPS:CL | E10 | CB | E100 | 101 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 27020 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27020 | 0 | 2 | deoPWRBPSCLE10E100CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Close
462 | BPS01_RTU | PWR:BPS:CL | E10 | CB | E100 | 101 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27020 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27020 | 4 | 2 | deiPWRBPSCLE10E100AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close Ack
463 | BPS01_RTU | PWR:BPS:CL | E10 | CB | E100 | 101 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 27020 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27020 | 0 | 2 | deoPWRBPSCLE10E100CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close
464 | BPS01_RTU | PWR:BPS:CL | E10 | CB | E100 | 101 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27020 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27020 | 2 | 2 | deiPWRBPSCLE10E100AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Close Ack
465 | BPS01_RTU | PWR:BPS:CL | E20 | CB | E200 | 102 | CirBrkStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 6040 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 6040 | 0 | 2 | deiPWRBPSCLE20E200CirBrkStatus | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Status
466 | BPS01_RTU | PWR:BPS:CL | E20 | CB | E200 | 102 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27040 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27040 | 0 | 2 | deoPWRBPSCLE20E200CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Open
467 | BPS01_RTU | PWR:BPS:CL | E20 | CB | E200 | 102 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27040 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27040 | 4 | 2 | deiPWRBPSCLE20E200AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open Ack
468 | BPS01_RTU | PWR:BPS:CL | E20 | CB | E200 | 102 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27040 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27040 | 0 | 2 | deoPWRBPSCLE20E200CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open
469 | BPS01_RTU | PWR:BPS:CL | E20 | CB | E200 | 102 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27040 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27040 | 2 | 2 | deiPWRBPSCLE20E200AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Open Ack
470 | BPS01_RTU | PWR:BPS:CL | E20 | CB | E200 | 102 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 27040 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27040 | 0 | 2 | deoPWRBPSCLE20E200CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Close
471 | BPS01_RTU | PWR:BPS:CL | E20 | CB | E200 | 102 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27040 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27040 | 4 | 2 | deiPWRBPSCLE20E200AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close Ack
472 | BPS01_RTU | PWR:BPS:CL | E20 | CB | E200 | 102 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 27040 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27040 | 0 | 2 | deoPWRBPSCLE20E200CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close
473 | BPS01_RTU | PWR:BPS:CL | E20 | CB | E200 | 102 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27040 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27040 | 2 | 2 | deiPWRBPSCLE20E200AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Close Ack
474 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTPR | 33KVSTPR_E100 | 103 | GenTrip | SIL0 | IEC104:M_SP_NA_1 | 5120 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5120 | 0 | 1 | deiPWRBPSCLE1033KVSTPR_E100GenTrip | 4 |  |  | 0 | $ComStatus , , | #[ETOO] : General Trip
475 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTPR | 33KVSTPR_E100 | 103 | LVRefTrip | SIL0 | IEC104:M_SP_NA_1 | 5121 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5121 | 0 | 1 | deiPWRBPSCLE1033KVSTPR_E100LVRefTrip | 4 |  |  | 0 | $ComStatus , , | #[REPO] : 1000kVA AT-1 LV REF Trip
476 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTPR | 33KVSTPR_E200 | 104 | GenTrip | SIL0 | IEC104:M_SP_NA_1 | 5160 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5160 | 0 | 1 | deiPWRBPSCLE2033KVSTPR_E200GenTrip | 4 |  |  | 0 | $ComStatus , , | #[ETOO] : General Trip
477 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTPR | 33KVSTPR_E200 | 104 | LVRefTrip | SIL0 | IEC104:M_SP_NA_1 | 5161 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5161 | 0 | 1 | deiPWRBPSCLE2033KVSTPR_E200LVRefTrip | 4 |  |  | 0 | $ComStatus , , | #[REPO] : 1000kVA AT-1 LV REF Trip
478 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTMV | 33KVSTMV_E10 | 105 | RPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 11200 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11200 | 0 | 16 | aeiPWRBPSCLE1033KVSTMV_E10RPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #R Phase Current
479 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTMV | 33KVSTMV_E10 | 105 | YPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 11201 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11201 | 0 | 16 | aeiPWRBPSCLE1033KVSTMV_E10YPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #Y Phase Current
480 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTMV | 33KVSTMV_E10 | 105 | BPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 11202 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11202 | 0 | 16 | aeiPWRBPSCLE1033KVSTMV_E10BPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #B Phase Current
481 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTMV | 33KVSTMV_E10 | 105 | NeutralCur | SIL0 | IEC104:M_ME_NA_1 | 11203 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11203 | 0 | 16 | aeiPWRBPSCLE1033KVSTMV_E10NeutralCur | 4 |  |  | 0 | $ComStatus , , | #Neutral Current (In)
482 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTMV | 33KVSTMV_E10 | 105 | RYPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 11204 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11204 | 0 | 16 | aeiPWRBPSCLE1033KVSTMV_E10RYPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #RY Phase Voltage
483 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTMV | 33KVSTMV_E10 | 105 | YBPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 11205 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11205 | 0 | 16 | aeiPWRBPSCLE1033KVSTMV_E10YBPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #YB Phase Voltage
484 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTMV | 33KVSTMV_E10 | 105 | BRPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 11206 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11206 | 0 | 16 | aeiPWRBPSCLE1033KVSTMV_E10BRPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #BR Phase Voltage
485 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTMV | 33KVSTMV_E10 | 105 | ZeroSeqVolt | SIL0 | IEC104:M_ME_NA_1 | 11207 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11207 | 0 | 16 | aeiPWRBPSCLE1033KVSTMV_E10ZeroSeqVolt | 4 |  |  | 0 | $ComStatus , , | #Zero Sequence Voltage (V0)
486 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTMV | 33KVSTMV_E10 | 105 | ActivePower | SIL0 | IEC104:M_ME_NA_1 | 11208 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11208 | 0 | 16 | aeiPWRBPSCLE1033KVSTMV_E10ActivePower | 4 |  |  | 0 | $ComStatus , , | #[MW] : Active Power
487 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTMV | 33KVSTMV_E10 | 105 | ReacPower | SIL0 | IEC104:M_ME_NA_1 | 11209 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11209 | 0 | 16 | aeiPWRBPSCLE1033KVSTMV_E10ReacPower | 4 |  |  | 0 | $ComStatus , , | #[MVAR] : Reactive Power
488 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTMV | 33KVSTMV_E10 | 105 | AppPower | SIL0 | IEC104:M_ME_NA_1 | 11210 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11210 | 0 | 16 | aeiPWRBPSCLE1033KVSTMV_E10AppPower | 4 |  |  | 0 | $ComStatus , , | #Apparent Power (S)
489 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTMV | 33KVSTMV_E10 | 105 | PowerFactor | SIL0 | IEC104:M_ME_NA_1 | 11211 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11211 | 0 | 16 | aeiPWRBPSCLE1033KVSTMV_E10PowerFactor | 4 |  |  | 0 | $ComStatus , , | #Power Factor (P.F)
490 | BPS01_RTU | PWR:BPS:CL | E10 | 33KVSTMV | 33KVSTMV_E10 | 105 | Frequency | SIL0 | IEC104:M_ME_NA_1 | 11212 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11212 | 0 | 16 | aeiPWRBPSCLE1033KVSTMV_E10Frequency | 4 |  |  | 0 | $ComStatus , , | #Frequency (Hz)
491 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTMV | 33KVSTMV_E20 | 106 | RPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 11240 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11240 | 0 | 16 | aeiPWRBPSCLE2033KVSTMV_E20RPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #R Phase Current
492 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTMV | 33KVSTMV_E20 | 106 | YPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 11241 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11241 | 0 | 16 | aeiPWRBPSCLE2033KVSTMV_E20YPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #Y Phase Current
493 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTMV | 33KVSTMV_E20 | 106 | BPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 11242 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11242 | 0 | 16 | aeiPWRBPSCLE2033KVSTMV_E20BPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #B Phase Current
494 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTMV | 33KVSTMV_E20 | 106 | NeutralCur | SIL0 | IEC104:M_ME_NA_1 | 11243 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11243 | 0 | 16 | aeiPWRBPSCLE2033KVSTMV_E20NeutralCur | 4 |  |  | 0 | $ComStatus , , | #Neutral Current (In)
495 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTMV | 33KVSTMV_E20 | 106 | RYPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 11244 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11244 | 0 | 16 | aeiPWRBPSCLE2033KVSTMV_E20RYPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #RY Phase Voltage
496 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTMV | 33KVSTMV_E20 | 106 | YBPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 11245 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11245 | 0 | 16 | aeiPWRBPSCLE2033KVSTMV_E20YBPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #YB Phase Voltage
497 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTMV | 33KVSTMV_E20 | 106 | BRPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 11246 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11246 | 0 | 16 | aeiPWRBPSCLE2033KVSTMV_E20BRPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #BR Phase Voltage
498 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTMV | 33KVSTMV_E20 | 106 | ZeroSeqVolt | SIL0 | IEC104:M_ME_NA_1 | 11247 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11247 | 0 | 16 | aeiPWRBPSCLE2033KVSTMV_E20ZeroSeqVolt | 4 |  |  | 0 | $ComStatus , , | #Zero Sequence Voltage (V0)
499 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTMV | 33KVSTMV_E20 | 106 | ActivePower | SIL0 | IEC104:M_ME_NA_1 | 11248 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11248 | 0 | 16 | aeiPWRBPSCLE2033KVSTMV_E20ActivePower | 4 |  |  | 0 | $ComStatus , , | #[MW] : Active Power
500 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTMV | 33KVSTMV_E20 | 106 | ReacPower | SIL0 | IEC104:M_ME_NA_1 | 11249 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11249 | 0 | 16 | aeiPWRBPSCLE2033KVSTMV_E20ReacPower | 4 |  |  | 0 | $ComStatus , , | #[MVAR] : Reactive Power
501 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTMV | 33KVSTMV_E20 | 106 | AppPower | SIL0 | IEC104:M_ME_NA_1 | 11250 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11250 | 0 | 16 | aeiPWRBPSCLE2033KVSTMV_E20AppPower | 4 |  |  | 0 | $ComStatus , , | #Apparent Power (S)
502 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTMV | 33KVSTMV_E20 | 106 | PowerFactor | SIL0 | IEC104:M_ME_NA_1 | 11251 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11251 | 0 | 16 | aeiPWRBPSCLE2033KVSTMV_E20PowerFactor | 4 |  |  | 0 | $ComStatus , , | #Power Factor (P.F)
503 | BPS01_RTU | PWR:BPS:CL | E20 | 33KVSTMV | 33KVSTMV_E20 | 106 | Frequency | SIL0 | IEC104:M_ME_NA_1 | 11252 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11252 | 0 | 16 | aeiPWRBPSCLE2033KVSTMV_E20Frequency | 4 |  |  | 0 | $ComStatus , , | #Frequency (Hz)
504 | BPS01_RTU | PWR:BPS:CL | E10 | BCA | BCA_E10 | 107 | DGCCCtrl | SIL0 | IEC104:M_SP_NA_1 | 5281 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5281 | 0 | 1 | deiPWRBPSCLE10BCA_E10DGCCCtrl | 4 |  |  | 0 | $ComStatus , , | #[CBLC] : DGCC Control
505 | BPS01_RTU | PWR:BPS:CL | E10 | BCA | BCA_E10 | 107 | BCUCardStatus | SIL0 | IEC104:M_SP_NA_1 | 5282 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5282 | 0 | 1 | deiPWRBPSCLE10BCA_E10BCUCardStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : Card Fail
506 | BPS01_RTU | PWR:BPS:CL | E20 | BCA | BCA_E20 | 108 | DGCCCtrl | SIL0 | IEC104:M_SP_NA_1 | 5321 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5321 | 0 | 1 | deiPWRBPSCLE20BCA_E20DGCCCtrl | 4 |  |  | 0 | $ComStatus , , | #[CBLC] : DGCC Control
507 | BPS01_RTU | PWR:BPS:CL | E20 | BCA | BCA_E20 | 108 | BCUCardStatus | SIL0 | IEC104:M_SP_NA_1 | 5322 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5322 | 0 | 1 | deiPWRBPSCLE20BCA_E20BCUCardStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : Card Fail
508 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSBA | 33KVBSBA_E12 | 109 | ACFailRPCell | SIL0 | IEC104:M_SP_NA_1 | 5360 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5360 | 0 | 1 | deiPWRBPSCLE1233KVBSBA_E12ACFailRPCell | 4 |  |  | 0 | $ComStatus , , | #[ACFL] : AC Fail Relay Panel / Cell
509 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSBA | 33KVBSBA_E12 | 109 | DCFailRP | SIL0 | IEC104:M_SP_NA_1 | 5361 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5361 | 0 | 1 | deiPWRBPSCLE1233KVBSBA_E12DCFailRP | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : DC Fail Relay Panel
510 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSBA | 33KVBSBA_E12 | 109 | DCFailCell | SIL0 | IEC104:M_SP_NA_1 | 5362 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5362 | 0 | 1 | deiPWRBPSCLE1233KVBSBA_E12DCFailCell | 4 |  |  | 0 | $ComStatus , , | #[DCFA] : DC Fail Cell
511 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSBA | 33KVBSBA_E12 | 109 | MstrTrpRyOp | SIL2_Monitoring | IEC104:M_SP_NA_1 | 5363 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 5363 | 0 | 1 | deiPWRBPSCLE1233KVBSBA_E12MstrTrpRyOp | 4 |  |  | 0 | $ComStatus , , | #[MTRO] : Master Trip relay operated
512 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSBA | 33KVBSBA_E12 | 109 | WdgIedStatus | SIL0 | IEC104:M_SP_NA_1 | 5364 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5364 | 0 | 1 | deiPWRBPSCLE1233KVBSBA_E12WdgIedStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG**] : IED WatchDog
513 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSBA | 33KVBSBA_E12 | 109 | WdgBcuStatus | SIL2_Monitoring | IEC104:M_SP_NA_1 | 5365 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 5365 | 0 | 1 | deiPWRBPSCLE1233KVBSBA_E12WdgBcuStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG**] : BCU Watchdog
514 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSBA | 33KVBSBA_E12 | 109 | VoltTransStatus | SIL0 | IEC104:M_SP_NA_1 | 5366 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5366 | 0 | 1 | deiPWRBPSCLE1233KVBSBA_E12VoltTransStatus | 4 |  |  | 0 | $ComStatus , , | #[VTFA] : Voltage Transformer Fault alarm
515 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSBA | 33KVBSBA_E12 | 109 | SyncFail | SIL0 | IEC104:M_SP_NA_1 | 5367 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5367 | 0 | 1 | deiPWRBPSCLE1233KVBSBA_E12SyncFail | 4 |  |  | 0 | $ComStatus , , | #[SYCO] : Synchronisation Fail
516 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSBA | 33KVBSBA_E12 | 109 | BCUCardFail | SIL0 | IEC104:M_SP_NA_1 | 5368 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5368 | 0 | 1 | deiPWRBPSCLE1233KVBSBA_E12BCUCardFail | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Card Fail
517 | BPS01_RTU | PWR:BPS:CL | E12 | CB | E120 | 110 | CirBrkStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 6200 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 6200 | 0 | 2 | deiPWRBPSCLE12E120CirBrkStatus | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Status
518 | BPS01_RTU | PWR:BPS:CL | E12 | CB | E120 | 110 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27200 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27200 | 0 | 2 | deoPWRBPSCLE12E120CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Open
519 | BPS01_RTU | PWR:BPS:CL | E12 | CB | E120 | 110 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27200 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27200 | 4 | 2 | deiPWRBPSCLE12E120AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open Ack
520 | BPS01_RTU | PWR:BPS:CL | E12 | CB | E120 | 110 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27200 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27200 | 0 | 2 | deoPWRBPSCLE12E120CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open
521 | BPS01_RTU | PWR:BPS:CL | E12 | CB | E120 | 110 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27200 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27200 | 2 | 2 | deiPWRBPSCLE12E120AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Open Ack
522 | BPS01_RTU | PWR:BPS:CL | E12 | CB | E120 | 110 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 27200 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27200 | 0 | 2 | deoPWRBPSCLE12E120CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Close
523 | BPS01_RTU | PWR:BPS:CL | E12 | CB | E120 | 110 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27200 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27200 | 4 | 2 | deiPWRBPSCLE12E120AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close Ack
524 | BPS01_RTU | PWR:BPS:CL | E12 | CB | E120 | 110 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 27200 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27200 | 0 | 2 | deoPWRBPSCLE12E120CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close
525 | BPS01_RTU | PWR:BPS:CL | E12 | CB | E120 | 110 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27200 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27200 | 2 | 2 | deiPWRBPSCLE12E120AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Close Ack
526 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSPR | 33KVBSPR_E120 | 111 | OverCurTrip | SIL0 | IEC104:M_SP_NA_1 | 5440 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5440 | 0 | 1 | deiPWRBPSCLE1233KVBSPR_E120OverCurTrip | 4 |  |  | 0 | $ComStatus , , | #[OEPO] : Over Current Trip
527 | BPS01_RTU | PWR:BPS:CL | E12 | ISST | ISST_E124 | 112 | BusIsolStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 6240 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 6240 | 0 | 2 | deiPWRBPSCLE12ISST_E124BusIsolStatus | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
528 | BPS01_RTU | PWR:BPS:CL | E12 | ISST | ISST_E124 | 112 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27240 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27240 | 0 | 2 | deoPWRBPSCLE12ISST_E124CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Open
529 | BPS01_RTU | PWR:BPS:CL | E12 | ISST | ISST_E124 | 112 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27240 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27240 | 4 | 2 | deiPWRBPSCLE12ISST_E124AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open Ack
530 | BPS01_RTU | PWR:BPS:CL | E12 | ISST | ISST_E124 | 112 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27240 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27240 | 0 | 2 | deoPWRBPSCLE12ISST_E124CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open
531 | BPS01_RTU | PWR:BPS:CL | E12 | ISST | ISST_E124 | 112 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27240 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27240 | 2 | 2 | deiPWRBPSCLE12ISST_E124AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Open Ack
532 | BPS01_RTU | PWR:BPS:CL | E12 | ISST | ISST_E124 | 112 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 27240 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27240 | 0 | 2 | deoPWRBPSCLE12ISST_E124CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Close
533 | BPS01_RTU | PWR:BPS:CL | E12 | ISST | ISST_E124 | 112 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27240 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27240 | 4 | 2 | deiPWRBPSCLE12ISST_E124AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close Ack
534 | BPS01_RTU | PWR:BPS:CL | E12 | ISST | ISST_E124 | 112 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 27240 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27240 | 0 | 2 | deoPWRBPSCLE12ISST_E124CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close
535 | BPS01_RTU | PWR:BPS:CL | E12 | ISST | ISST_E124 | 112 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27240 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27240 | 2 | 2 | deiPWRBPSCLE12ISST_E124AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Close Ack
536 | BPS01_RTU | PWR:BPS:CL | E12 | ISST | ISST_E126 | 113 | BusIsolStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 6260 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 6260 | 0 | 2 | deiPWRBPSCLE12ISST_E126BusIsolStatus | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
537 | BPS01_RTU | PWR:BPS:CL | E12 | ISST | ISST_E126 | 113 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27260 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27260 | 0 | 2 | deoPWRBPSCLE12ISST_E126CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Open
538 | BPS01_RTU | PWR:BPS:CL | E12 | ISST | ISST_E126 | 113 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27260 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27260 | 4 | 2 | deiPWRBPSCLE12ISST_E126AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open Ack
539 | BPS01_RTU | PWR:BPS:CL | E12 | ISST | ISST_E126 | 113 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27260 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27260 | 0 | 2 | deoPWRBPSCLE12ISST_E126CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open
540 | BPS01_RTU | PWR:BPS:CL | E12 | ISST | ISST_E126 | 113 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27260 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27260 | 2 | 2 | deiPWRBPSCLE12ISST_E126AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Open Ack
541 | BPS01_RTU | PWR:BPS:CL | E12 | ISST | ISST_E126 | 113 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 27260 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27260 | 0 | 2 | deoPWRBPSCLE12ISST_E126CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Close
542 | BPS01_RTU | PWR:BPS:CL | E12 | ISST | ISST_E126 | 113 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27260 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27260 | 4 | 2 | deiPWRBPSCLE12ISST_E126AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close Ack
543 | BPS01_RTU | PWR:BPS:CL | E12 | ISST | ISST_E126 | 113 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 27260 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27260 | 0 | 2 | deoPWRBPSCLE12ISST_E126CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close
544 | BPS01_RTU | PWR:BPS:CL | E12 | ISST | ISST_E126 | 113 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27260 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27260 | 2 | 2 | deiPWRBPSCLE12ISST_E126AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Close Ack
545 | BPS01_RTU | PWR:BPS:CL | E12 | ESST | E12M1 | 114 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 6280 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 6280 | 0 | 2 | deiPWRBPSCLE12E12M1EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
546 | BPS01_RTU | PWR:BPS:CL | E12 | ESST | E12M1 | 114 | CmdOpen | SIL0 | IEC104:C_DC_NA_1 | 27280 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27280 | 0 | 2 | deoPWRBPSCLE12E12M1CmdOpen | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Open
547 | BPS01_RTU | PWR:BPS:CL | E12 | ESST | E12M1 | 114 | CmdClose | SIL0 | IEC104:C_DC_NA_1 | 27280 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27280 | 0 | 2 | deoPWRBPSCLE12E12M1CmdClose | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Close
548 | BPS01_RTU | PWR:BPS:CL | E12 | ESST | E12M2 | 115 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 6300 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 6300 | 0 | 2 | deiPWRBPSCLE12E12M2EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
549 | BPS01_RTU | PWR:BPS:CL | E12 | ESST | E12M2 | 115 | CmdOpen | SIL0 | IEC104:C_DC_NA_1 | 27300 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27300 | 0 | 2 | deoPWRBPSCLE12E12M2CmdOpen | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Open
550 | BPS01_RTU | PWR:BPS:CL | E12 | ESST | E12M2 | 115 | CmdClose | SIL0 | IEC104:C_DC_NA_1 | 27300 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27300 | 0 | 2 | deoPWRBPSCLE12E12M2CmdClose | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Close
551 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSMV | 33KVBSMV_E12 | 116 | RPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 11640 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11640 | 0 | 16 | aeiPWRBPSCLE1233KVBSMV_E12RPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #R Phase Current
552 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSMV | 33KVBSMV_E12 | 116 | YPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 11641 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11641 | 0 | 16 | aeiPWRBPSCLE1233KVBSMV_E12YPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #Y Phase Current
553 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSMV | 33KVBSMV_E12 | 116 | BPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 11642 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11642 | 0 | 16 | aeiPWRBPSCLE1233KVBSMV_E12BPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #B Phase Current
554 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSMV | 33KVBSMV_E12 | 116 | NeutralCur | SIL0 | IEC104:M_ME_NA_1 | 11643 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11643 | 0 | 16 | aeiPWRBPSCLE1233KVBSMV_E12NeutralCur | 4 |  |  | 0 | $ComStatus , , | #Neutral Current (In)
555 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSMV | 33KVBSMV_E12 | 116 | RYPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 11644 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11644 | 0 | 16 | aeiPWRBPSCLE1233KVBSMV_E12RYPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #RY Phase Voltage
556 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSMV | 33KVBSMV_E12 | 116 | YBPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 11645 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11645 | 0 | 16 | aeiPWRBPSCLE1233KVBSMV_E12YBPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #YB Phase Voltage
557 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSMV | 33KVBSMV_E12 | 116 | BRPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 11646 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11646 | 0 | 16 | aeiPWRBPSCLE1233KVBSMV_E12BRPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #BR Phase Voltage
558 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSMV | 33KVBSMV_E12 | 116 | ZeroSeqVolt | SIL0 | IEC104:M_ME_NA_1 | 11647 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11647 | 0 | 16 | aeiPWRBPSCLE1233KVBSMV_E12ZeroSeqVolt | 4 |  |  | 0 | $ComStatus , , | #Zero Sequence Voltage (V0)
559 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSMV | 33KVBSMV_E12 | 116 | ActivePower | SIL0 | IEC104:M_ME_NA_1 | 11648 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11648 | 0 | 16 | aeiPWRBPSCLE1233KVBSMV_E12ActivePower | 4 |  |  | 0 | $ComStatus , , | #[MW] : Active Power
560 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSMV | 33KVBSMV_E12 | 116 | ReacPower | SIL0 | IEC104:M_ME_NA_1 | 11649 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11649 | 0 | 16 | aeiPWRBPSCLE1233KVBSMV_E12ReacPower | 4 |  |  | 0 | $ComStatus , , | #[MVAR] : Reactive Power
561 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSMV | 33KVBSMV_E12 | 116 | AppPower | SIL0 | IEC104:M_ME_NA_1 | 11650 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11650 | 0 | 16 | aeiPWRBPSCLE1233KVBSMV_E12AppPower | 4 |  |  | 0 | $ComStatus , , | #Apparent Power (S)
562 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSMV | 33KVBSMV_E12 | 116 | PowerFactor | SIL0 | IEC104:M_ME_NA_1 | 11651 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11651 | 0 | 16 | aeiPWRBPSCLE1233KVBSMV_E12PowerFactor | 4 |  |  | 0 | $ComStatus , , | #Power Factor (P.F)
563 | BPS01_RTU | PWR:BPS:CL | E12 | 33KVBSMV | 33KVBSMV_E12 | 116 | Frequency | SIL0 | IEC104:M_ME_NA_1 | 11652 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 11652 | 0 | 16 | aeiPWRBPSCLE1233KVBSMV_E12Frequency | 4 |  |  | 0 | $ComStatus , , | #Frequency (Hz)
564 | BPS01_RTU | PWR:BPS:CL | E12 | BCA | BCA_E12 | 117 | DGCCCtrl | SIL0 | IEC104:M_SP_NA_1 | 5681 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5681 | 0 | 1 | deiPWRBPSCLE12BCA_E12DGCCCtrl | 4 |  |  | 0 | $ComStatus , , | #[CBLC] : DGCC Control
565 | BPS01_RTU | PWR:BPS:CL | E12 | BCA | BCA_E12 | 117 | BCUCardStatus | SIL0 | IEC104:M_SP_NA_1 | 5682 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5682 | 0 | 1 | deiPWRBPSCLE12BCA_E12BCUCardStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : Card Fail
566 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFBA | 33KVOFBA_E30 | 118 | ACFailRPSwgr | SIL0 | IEC104:M_SP_NA_1 | 5720 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5720 | 0 | 1 | deiPWRBPSCLE3033KVOFBA_E30ACFailRPSwgr | 4 |  |  | 0 | $ComStatus , , | #[ACFL] : AC Fail Relay Panel / SWGR
567 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFBA | 33KVOFBA_E30 | 118 | DCFailRP | SIL0 | IEC104:M_SP_NA_1 | 5721 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5721 | 0 | 1 | deiPWRBPSCLE3033KVOFBA_E30DCFailRP | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : DC Fail Relay Panel
568 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFBA | 33KVOFBA_E30 | 118 | DCFailSwgr | SIL0 | IEC104:M_SP_NA_1 | 5722 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5722 | 0 | 1 | deiPWRBPSCLE3033KVOFBA_E30DCFailSwgr | 4 |  |  | 0 | $ComStatus , , | #[DCFA] : DC Fail SWGR
569 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFBA | 33KVOFBA_E30 | 118 | WdgIedStatus | SIL0 | IEC104:M_SP_NA_1 | 5723 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5723 | 0 | 1 | deiPWRBPSCLE3033KVOFBA_E30WdgIedStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG**] : IED WatchDog
570 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFBA | 33KVOFBA_E30 | 118 | WdgBcuStatus | SIL2_Monitoring | IEC104:M_SP_NA_1 | 5724 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 5724 | 0 | 1 | deiPWRBPSCLE3033KVOFBA_E30WdgBcuStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG**] : BCU Watchdog
571 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFBA | 33KVOFBA_E30 | 118 | VoltTransStatus | SIL0 | IEC104:M_SP_NA_1 | 5725 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5725 | 0 | 1 | deiPWRBPSCLE3033KVOFBA_E30VoltTransStatus | 4 |  |  | 0 | $ComStatus , , | #[VTFA] : Voltage Transformer Fault alarm
572 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFBA | 33KVOFBA_E30 | 118 | BCUCardFail | SIL0 | IEC104:M_SP_NA_1 | 5726 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5726 | 0 | 1 | deiPWRBPSCLE3033KVOFBA_E30BCUCardFail | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Card Fail
573 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFBA | 33KVOFBA_E40 | 119 | ACFailRPSwgr | SIL0 | IEC104:M_SP_NA_1 | 5760 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5760 | 0 | 1 | deiPWRBPSCLE4033KVOFBA_E40ACFailRPSwgr | 4 |  |  | 0 | $ComStatus , , | #[ACFL] : AC Fail Relay Panel / SWGR
574 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFBA | 33KVOFBA_E40 | 119 | DCFailRP | SIL0 | IEC104:M_SP_NA_1 | 5761 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5761 | 0 | 1 | deiPWRBPSCLE4033KVOFBA_E40DCFailRP | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : DC Fail Relay Panel
575 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFBA | 33KVOFBA_E40 | 119 | DCFailSwgr | SIL0 | IEC104:M_SP_NA_1 | 5762 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5762 | 0 | 1 | deiPWRBPSCLE4033KVOFBA_E40DCFailSwgr | 4 |  |  | 0 | $ComStatus , , | #[DCFA] : DC Fail SWGR
576 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFBA | 33KVOFBA_E40 | 119 | WdgIedStatus | SIL0 | IEC104:M_SP_NA_1 | 5763 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5763 | 0 | 1 | deiPWRBPSCLE4033KVOFBA_E40WdgIedStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG**] : IED WatchDog
577 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFBA | 33KVOFBA_E40 | 119 | WdgBcuStatus | SIL2_Monitoring | IEC104:M_SP_NA_1 | 5764 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 5764 | 0 | 1 | deiPWRBPSCLE4033KVOFBA_E40WdgBcuStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG**] : BCU Watchdog
578 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFBA | 33KVOFBA_E40 | 119 | VoltTransStatus | SIL0 | IEC104:M_SP_NA_1 | 5765 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5765 | 0 | 1 | deiPWRBPSCLE4033KVOFBA_E40VoltTransStatus | 4 |  |  | 0 | $ComStatus , , | #[VTFA] : Voltage Transformer Fault alarm
579 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFBA | 33KVOFBA_E40 | 119 | BCUCardFail | SIL0 | IEC104:M_SP_NA_1 | 5766 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5766 | 0 | 1 | deiPWRBPSCLE4033KVOFBA_E40BCUCardFail | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Card Fail
580 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFBA | 33KVOFBA_E50 | 120 | ACFailRPSwgr | SIL0 | IEC104:M_SP_NA_1 | 5800 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5800 | 0 | 1 | deiPWRBPSCLE5033KVOFBA_E50ACFailRPSwgr | 4 |  |  | 0 | $ComStatus , , | #[ACFL] : AC Fail Relay Panel / SWGR
581 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFBA | 33KVOFBA_E50 | 120 | DCFailRP | SIL0 | IEC104:M_SP_NA_1 | 5801 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5801 | 0 | 1 | deiPWRBPSCLE5033KVOFBA_E50DCFailRP | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : DC Fail Relay Panel
582 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFBA | 33KVOFBA_E50 | 120 | DCFailSwgr | SIL0 | IEC104:M_SP_NA_1 | 5802 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5802 | 0 | 1 | deiPWRBPSCLE5033KVOFBA_E50DCFailSwgr | 4 |  |  | 0 | $ComStatus , , | #[DCFA] : DC Fail SWGR
583 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFBA | 33KVOFBA_E50 | 120 | WdgIedStatus | SIL0 | IEC104:M_SP_NA_1 | 5803 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5803 | 0 | 1 | deiPWRBPSCLE5033KVOFBA_E50WdgIedStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG**] : IED WatchDog
584 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFBA | 33KVOFBA_E50 | 120 | WdgBcuStatus | SIL2_Monitoring | IEC104:M_SP_NA_1 | 5804 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 5804 | 0 | 1 | deiPWRBPSCLE5033KVOFBA_E50WdgBcuStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG**] : BCU Watchdog
585 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFBA | 33KVOFBA_E50 | 120 | VoltTransStatus | SIL0 | IEC104:M_SP_NA_1 | 5805 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5805 | 0 | 1 | deiPWRBPSCLE5033KVOFBA_E50VoltTransStatus | 4 |  |  | 0 | $ComStatus , , | #[VTFA] : Voltage Transformer Fault alarm
586 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFBA | 33KVOFBA_E50 | 120 | BCUCardFail | SIL0 | IEC104:M_SP_NA_1 | 5806 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5806 | 0 | 1 | deiPWRBPSCLE5033KVOFBA_E50BCUCardFail | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Card Fail
587 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFBA | 33KVOFBA_E60 | 121 | ACFailRPSwgr | SIL0 | IEC104:M_SP_NA_1 | 5840 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5840 | 0 | 1 | deiPWRBPSCLE6033KVOFBA_E60ACFailRPSwgr | 4 |  |  | 0 | $ComStatus , , | #[ACFL] : AC Fail Relay Panel / SWGR
588 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFBA | 33KVOFBA_E60 | 121 | DCFailRP | SIL0 | IEC104:M_SP_NA_1 | 5841 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5841 | 0 | 1 | deiPWRBPSCLE6033KVOFBA_E60DCFailRP | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : DC Fail Relay Panel
589 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFBA | 33KVOFBA_E60 | 121 | DCFailSwgr | SIL0 | IEC104:M_SP_NA_1 | 5842 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5842 | 0 | 1 | deiPWRBPSCLE6033KVOFBA_E60DCFailSwgr | 4 |  |  | 0 | $ComStatus , , | #[DCFA] : DC Fail SWGR
590 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFBA | 33KVOFBA_E60 | 121 | WdgIedStatus | SIL0 | IEC104:M_SP_NA_1 | 5843 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5843 | 0 | 1 | deiPWRBPSCLE6033KVOFBA_E60WdgIedStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG**] : IED WatchDog
591 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFBA | 33KVOFBA_E60 | 121 | WdgBcuStatus | SIL2_Monitoring | IEC104:M_SP_NA_1 | 5844 | 0 | 1 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_SP_TB | 1 | 5844 | 0 | 1 | deiPWRBPSCLE6033KVOFBA_E60WdgBcuStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG**] : BCU Watchdog
592 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFBA | 33KVOFBA_E60 | 121 | VoltTransStatus | SIL0 | IEC104:M_SP_NA_1 | 5845 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5845 | 0 | 1 | deiPWRBPSCLE6033KVOFBA_E60VoltTransStatus | 4 |  |  | 0 | $ComStatus , , | #[VTFA] : Voltage Transformer Fault alarm
593 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFBA | 33KVOFBA_E60 | 121 | BCUCardFail | SIL0 | IEC104:M_SP_NA_1 | 5846 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 5846 | 0 | 1 | deiPWRBPSCLE6033KVOFBA_E60BCUCardFail | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : BCU Card Fail
594 | BPS01_RTU | PWR:BPS:CL | E30 | ISST | ISST_E304 | 122 | BusIsolStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 6440 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 6440 | 0 | 2 | deiPWRBPSCLE30ISST_E304BusIsolStatus | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
595 | BPS01_RTU | PWR:BPS:CL | E30 | ISST | ISST_E304 | 122 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27440 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27440 | 0 | 2 | deoPWRBPSCLE30ISST_E304CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Open
596 | BPS01_RTU | PWR:BPS:CL | E30 | ISST | ISST_E304 | 122 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27440 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27440 | 4 | 2 | deiPWRBPSCLE30ISST_E304AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open Ack
597 | BPS01_RTU | PWR:BPS:CL | E30 | ISST | ISST_E304 | 122 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27440 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27440 | 0 | 2 | deoPWRBPSCLE30ISST_E304CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open
598 | BPS01_RTU | PWR:BPS:CL | E30 | ISST | ISST_E304 | 122 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27440 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27440 | 2 | 2 | deiPWRBPSCLE30ISST_E304AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Open Ack
599 | BPS01_RTU | PWR:BPS:CL | E30 | ISST | ISST_E304 | 122 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 27440 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27440 | 0 | 2 | deoPWRBPSCLE30ISST_E304CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Close
600 | BPS01_RTU | PWR:BPS:CL | E30 | ISST | ISST_E304 | 122 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27440 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27440 | 4 | 2 | deiPWRBPSCLE30ISST_E304AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close Ack
601 | BPS01_RTU | PWR:BPS:CL | E30 | ISST | ISST_E304 | 122 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 27440 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27440 | 0 | 2 | deoPWRBPSCLE30ISST_E304CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close
602 | BPS01_RTU | PWR:BPS:CL | E30 | ISST | ISST_E304 | 122 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27440 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27440 | 2 | 2 | deiPWRBPSCLE30ISST_E304AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Close Ack
603 | BPS01_RTU | PWR:BPS:CL | E40 | ISST | ISST_E404 | 123 | BusIsolStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 6460 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 6460 | 0 | 2 | deiPWRBPSCLE40ISST_E404BusIsolStatus | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
604 | BPS01_RTU | PWR:BPS:CL | E40 | ISST | ISST_E404 | 123 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27460 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27460 | 0 | 2 | deoPWRBPSCLE40ISST_E404CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Open
605 | BPS01_RTU | PWR:BPS:CL | E40 | ISST | ISST_E404 | 123 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27460 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27460 | 4 | 2 | deiPWRBPSCLE40ISST_E404AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open Ack
606 | BPS01_RTU | PWR:BPS:CL | E40 | ISST | ISST_E404 | 123 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27460 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27460 | 0 | 2 | deoPWRBPSCLE40ISST_E404CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open
607 | BPS01_RTU | PWR:BPS:CL | E40 | ISST | ISST_E404 | 123 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27460 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27460 | 2 | 2 | deiPWRBPSCLE40ISST_E404AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Open Ack
608 | BPS01_RTU | PWR:BPS:CL | E40 | ISST | ISST_E404 | 123 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 27460 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27460 | 0 | 2 | deoPWRBPSCLE40ISST_E404CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Close
609 | BPS01_RTU | PWR:BPS:CL | E40 | ISST | ISST_E404 | 123 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27460 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27460 | 4 | 2 | deiPWRBPSCLE40ISST_E404AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close Ack
610 | BPS01_RTU | PWR:BPS:CL | E40 | ISST | ISST_E404 | 123 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 27460 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27460 | 0 | 2 | deoPWRBPSCLE40ISST_E404CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close
611 | BPS01_RTU | PWR:BPS:CL | E40 | ISST | ISST_E404 | 123 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27460 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27460 | 2 | 2 | deiPWRBPSCLE40ISST_E404AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Close Ack
612 | BPS01_RTU | PWR:BPS:CL | E50 | ISST | ISST_E504 | 124 | BusIsolStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 6480 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 6480 | 0 | 2 | deiPWRBPSCLE50ISST_E504BusIsolStatus | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
613 | BPS01_RTU | PWR:BPS:CL | E50 | ISST | ISST_E504 | 124 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27480 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27480 | 0 | 2 | deoPWRBPSCLE50ISST_E504CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Open
614 | BPS01_RTU | PWR:BPS:CL | E50 | ISST | ISST_E504 | 124 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27480 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27480 | 4 | 2 | deiPWRBPSCLE50ISST_E504AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open Ack
615 | BPS01_RTU | PWR:BPS:CL | E50 | ISST | ISST_E504 | 124 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27480 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27480 | 0 | 2 | deoPWRBPSCLE50ISST_E504CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open
616 | BPS01_RTU | PWR:BPS:CL | E50 | ISST | ISST_E504 | 124 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27480 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27480 | 2 | 2 | deiPWRBPSCLE50ISST_E504AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Open Ack
617 | BPS01_RTU | PWR:BPS:CL | E50 | ISST | ISST_E504 | 124 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 27480 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27480 | 0 | 2 | deoPWRBPSCLE50ISST_E504CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Close
618 | BPS01_RTU | PWR:BPS:CL | E50 | ISST | ISST_E504 | 124 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27480 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27480 | 4 | 2 | deiPWRBPSCLE50ISST_E504AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close Ack
619 | BPS01_RTU | PWR:BPS:CL | E50 | ISST | ISST_E504 | 124 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 27480 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27480 | 0 | 2 | deoPWRBPSCLE50ISST_E504CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close
620 | BPS01_RTU | PWR:BPS:CL | E50 | ISST | ISST_E504 | 124 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27480 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27480 | 2 | 2 | deiPWRBPSCLE50ISST_E504AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Close Ack
621 | BPS01_RTU | PWR:BPS:CL | E60 | ISST | ISST_E604 | 125 | BusIsolStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 6500 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 6500 | 0 | 2 | deiPWRBPSCLE60ISST_E604BusIsolStatus | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Status
622 | BPS01_RTU | PWR:BPS:CL | E60 | ISST | ISST_E604 | 125 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27500 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27500 | 0 | 2 | deoPWRBPSCLE60ISST_E604CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Open
623 | BPS01_RTU | PWR:BPS:CL | E60 | ISST | ISST_E604 | 125 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27500 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27500 | 4 | 2 | deiPWRBPSCLE60ISST_E604AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open Ack
624 | BPS01_RTU | PWR:BPS:CL | E60 | ISST | ISST_E604 | 125 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27500 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27500 | 0 | 2 | deoPWRBPSCLE60ISST_E604CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Open
625 | BPS01_RTU | PWR:BPS:CL | E60 | ISST | ISST_E604 | 125 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27500 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27500 | 2 | 2 | deiPWRBPSCLE60ISST_E604AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Open Ack
626 | BPS01_RTU | PWR:BPS:CL | E60 | ISST | ISST_E604 | 125 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 27500 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27500 | 0 | 2 | deoPWRBPSCLE60ISST_E604CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Close
627 | BPS01_RTU | PWR:BPS:CL | E60 | ISST | ISST_E604 | 125 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27500 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27500 | 4 | 2 | deiPWRBPSCLE60ISST_E604AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close Ack
628 | BPS01_RTU | PWR:BPS:CL | E60 | ISST | ISST_E604 | 125 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 27500 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27500 | 0 | 2 | deoPWRBPSCLE60ISST_E604CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Select Close
629 | BPS01_RTU | PWR:BPS:CL | E60 | ISST | ISST_E604 | 125 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27500 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27500 | 2 | 2 | deiPWRBPSCLE60ISST_E604AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[ISST] : Bus Isolator Control Execute Close Ack
630 | BPS01_RTU | PWR:BPS:CL | E30 | ESST | E30M1 | 126 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 6520 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 6520 | 0 | 2 | deiPWRBPSCLE30E30M1EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
631 | BPS01_RTU | PWR:BPS:CL | E30 | ESST | E30M1 | 126 | CmdOpen | SIL0 | IEC104:C_DC_NA_1 | 27520 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27520 | 0 | 2 | deoPWRBPSCLE30E30M1CmdOpen | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Open
632 | BPS01_RTU | PWR:BPS:CL | E30 | ESST | E30M1 | 126 | CmdClose | SIL0 | IEC104:C_DC_NA_1 | 27520 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27520 | 0 | 2 | deoPWRBPSCLE30E30M1CmdClose | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Close
633 | BPS01_RTU | PWR:BPS:CL | E40 | ESST | E40M1 | 127 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 6540 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 6540 | 0 | 2 | deiPWRBPSCLE40E40M1EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
634 | BPS01_RTU | PWR:BPS:CL | E40 | ESST | E40M1 | 127 | CmdOpen | SIL0 | IEC104:C_DC_NA_1 | 27540 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27540 | 0 | 2 | deoPWRBPSCLE40E40M1CmdOpen | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Open
635 | BPS01_RTU | PWR:BPS:CL | E40 | ESST | E40M1 | 127 | CmdClose | SIL0 | IEC104:C_DC_NA_1 | 27540 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27540 | 0 | 2 | deoPWRBPSCLE40E40M1CmdClose | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Close
636 | BPS01_RTU | PWR:BPS:CL | E50 | ESST | E50M1 | 128 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 6560 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 6560 | 0 | 2 | deiPWRBPSCLE50E50M1EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
637 | BPS01_RTU | PWR:BPS:CL | E50 | ESST | E50M1 | 128 | CmdOpen | SIL0 | IEC104:C_DC_NA_1 | 27560 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27560 | 0 | 2 | deoPWRBPSCLE50E50M1CmdOpen | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Open
638 | BPS01_RTU | PWR:BPS:CL | E50 | ESST | E50M1 | 128 | CmdClose | SIL0 | IEC104:C_DC_NA_1 | 27560 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27560 | 0 | 2 | deoPWRBPSCLE50E50M1CmdClose | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Close
639 | BPS01_RTU | PWR:BPS:CL | E60 | ESST | E60M1 | 129 | EarthSwtchStatus | SIL0 | IEC104:M_DP_NA_1 | 6580 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 6580 | 0 | 2 | deiPWRBPSCLE60E60M1EarthSwtchStatus | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Status
640 | BPS01_RTU | PWR:BPS:CL | E60 | ESST | E60M1 | 129 | CmdOpen | SIL0 | IEC104:C_DC_NA_1 | 27580 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27580 | 0 | 2 | deoPWRBPSCLE60E60M1CmdOpen | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Open
641 | BPS01_RTU | PWR:BPS:CL | E60 | ESST | E60M1 | 129 | CmdClose | SIL0 | IEC104:C_DC_NA_1 | 27580 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27580 | 0 | 2 | deoPWRBPSCLE60E60M1CmdClose | 4 |  |  | 0 | $ComStatus , , | #[ESST] : Earth Switch Control Close
642 | BPS01_RTU | PWR:BPS:CL | E30 | CB | E300 | 130 | CirBrkStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 6600 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 6600 | 0 | 2 | deiPWRBPSCLE30E300CirBrkStatus | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Status
643 | BPS01_RTU | PWR:BPS:CL | E30 | CB | E300 | 130 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27600 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27600 | 0 | 2 | deoPWRBPSCLE30E300CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Open
644 | BPS01_RTU | PWR:BPS:CL | E30 | CB | E300 | 130 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27600 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27600 | 4 | 2 | deiPWRBPSCLE30E300AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open Ack
645 | BPS01_RTU | PWR:BPS:CL | E30 | CB | E300 | 130 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27600 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27600 | 0 | 2 | deoPWRBPSCLE30E300CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open
646 | BPS01_RTU | PWR:BPS:CL | E30 | CB | E300 | 130 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27600 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27600 | 2 | 2 | deiPWRBPSCLE30E300AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Open Ack
647 | BPS01_RTU | PWR:BPS:CL | E30 | CB | E300 | 130 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 27600 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27600 | 0 | 2 | deoPWRBPSCLE30E300CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Close
648 | BPS01_RTU | PWR:BPS:CL | E30 | CB | E300 | 130 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27600 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27600 | 4 | 2 | deiPWRBPSCLE30E300AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close Ack
649 | BPS01_RTU | PWR:BPS:CL | E30 | CB | E300 | 130 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 27600 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27600 | 0 | 2 | deoPWRBPSCLE30E300CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close
650 | BPS01_RTU | PWR:BPS:CL | E30 | CB | E300 | 130 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27600 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27600 | 2 | 2 | deiPWRBPSCLE30E300AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Close Ack
651 | BPS01_RTU | PWR:BPS:CL | E40 | CB | E400 | 131 | CirBrkStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 6620 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 6620 | 0 | 2 | deiPWRBPSCLE40E400CirBrkStatus | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Status
652 | BPS01_RTU | PWR:BPS:CL | E40 | CB | E400 | 131 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27620 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27620 | 0 | 2 | deoPWRBPSCLE40E400CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Open
653 | BPS01_RTU | PWR:BPS:CL | E40 | CB | E400 | 131 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27620 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27620 | 4 | 2 | deiPWRBPSCLE40E400AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open Ack
654 | BPS01_RTU | PWR:BPS:CL | E40 | CB | E400 | 131 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27620 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27620 | 0 | 2 | deoPWRBPSCLE40E400CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open
655 | BPS01_RTU | PWR:BPS:CL | E40 | CB | E400 | 131 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27620 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27620 | 2 | 2 | deiPWRBPSCLE40E400AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Open Ack
656 | BPS01_RTU | PWR:BPS:CL | E40 | CB | E400 | 131 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 27620 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27620 | 0 | 2 | deoPWRBPSCLE40E400CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Close
657 | BPS01_RTU | PWR:BPS:CL | E40 | CB | E400 | 131 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27620 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27620 | 4 | 2 | deiPWRBPSCLE40E400AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close Ack
658 | BPS01_RTU | PWR:BPS:CL | E40 | CB | E400 | 131 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 27620 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27620 | 0 | 2 | deoPWRBPSCLE40E400CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close
659 | BPS01_RTU | PWR:BPS:CL | E40 | CB | E400 | 131 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27620 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27620 | 2 | 2 | deiPWRBPSCLE40E400AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Close Ack
660 | BPS01_RTU | PWR:BPS:CL | E50 | CB | E500 | 132 | CirBrkStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 6640 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 6640 | 0 | 2 | deiPWRBPSCLE50E500CirBrkStatus | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Status
661 | BPS01_RTU | PWR:BPS:CL | E50 | CB | E500 | 132 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27640 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27640 | 0 | 2 | deoPWRBPSCLE50E500CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Open
662 | BPS01_RTU | PWR:BPS:CL | E50 | CB | E500 | 132 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27640 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27640 | 4 | 2 | deiPWRBPSCLE50E500AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open Ack
663 | BPS01_RTU | PWR:BPS:CL | E50 | CB | E500 | 132 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27640 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27640 | 0 | 2 | deoPWRBPSCLE50E500CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open
664 | BPS01_RTU | PWR:BPS:CL | E50 | CB | E500 | 132 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27640 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27640 | 2 | 2 | deiPWRBPSCLE50E500AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Open Ack
665 | BPS01_RTU | PWR:BPS:CL | E50 | CB | E500 | 132 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 27640 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27640 | 0 | 2 | deoPWRBPSCLE50E500CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Close
666 | BPS01_RTU | PWR:BPS:CL | E50 | CB | E500 | 132 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27640 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27640 | 4 | 2 | deiPWRBPSCLE50E500AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close Ack
667 | BPS01_RTU | PWR:BPS:CL | E50 | CB | E500 | 132 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 27640 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27640 | 0 | 2 | deoPWRBPSCLE50E500CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close
668 | BPS01_RTU | PWR:BPS:CL | E50 | CB | E500 | 132 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27640 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27640 | 2 | 2 | deiPWRBPSCLE50E500AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Close Ack
669 | BPS01_RTU | PWR:BPS:CL | E60 | CB | E600 | 133 | CirBrkStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 6660 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 6660 | 0 | 2 | deiPWRBPSCLE60E600CirBrkStatus | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Status
670 | BPS01_RTU | PWR:BPS:CL | E60 | CB | E600 | 133 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27660 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27660 | 0 | 2 | deoPWRBPSCLE60E600CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Open
671 | BPS01_RTU | PWR:BPS:CL | E60 | CB | E600 | 133 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27660 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27660 | 4 | 2 | deiPWRBPSCLE60E600AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open Ack
672 | BPS01_RTU | PWR:BPS:CL | E60 | CB | E600 | 133 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 27660 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27660 | 0 | 2 | deoPWRBPSCLE60E600CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open
673 | BPS01_RTU | PWR:BPS:CL | E60 | CB | E600 | 133 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27660 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27660 | 2 | 2 | deiPWRBPSCLE60E600AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Open Ack
674 | BPS01_RTU | PWR:BPS:CL | E60 | CB | E600 | 133 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 27660 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27660 | 0 | 2 | deoPWRBPSCLE60E600CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Close
675 | BPS01_RTU | PWR:BPS:CL | E60 | CB | E600 | 133 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27660 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27660 | 4 | 2 | deiPWRBPSCLE60E600AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close Ack
676 | BPS01_RTU | PWR:BPS:CL | E60 | CB | E600 | 133 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 27660 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 27660 | 0 | 2 | deoPWRBPSCLE60E600CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close
677 | BPS01_RTU | PWR:BPS:CL | E60 | CB | E600 | 133 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 27660 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 27660 | 2 | 2 | deiPWRBPSCLE60E600AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Close Ack
678 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFPR | 33KVOFPR_E300 | 134 | GenTrip | SIL0 | IEC104:M_SP_NA_1 | 6360 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6360 | 0 | 1 | deiPWRBPSCLE3033KVOFPR_E300GenTrip | 4 |  |  | 0 | $ComStatus , , | #[ETOO] : General Trip
679 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFPR | 33KVOFPR_E300 | 134 | DiffProtTrip | SIL0 | IEC104:M_SP_NA_1 | 6361 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6361 | 0 | 1 | deiPWRBPSCLE3033KVOFPR_E300DiffProtTrip | 4 |  |  | 0 | $ComStatus , , | #[CDPT] : Diff. Prot. Trip
680 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFPR | 33KVOFPR_E300 | 134 | ThermAlSt1 | SIL0 | IEC104:M_SP_NA_1 | 6362 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6362 | 0 | 1 | deiPWRBPSCLE3033KVOFPR_E300ThermAlSt1 | 4 |  |  | 0 | $ComStatus , , | #[QAFA] : Thermal Overload Alarm St-1
681 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFPR | 33KVOFPR_E300 | 134 | FOCFail | SIL0 | IEC104:M_SP_NA_1 | 6363 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6363 | 0 | 1 | deiPWRBPSCLE3033KVOFPR_E300FOCFail | 4 |  |  | 0 | $ComStatus , , | #[CDFA] : Diff Communication Fail
682 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFPR | 33KVOFPR_E300 | 134 | VTFuseFail | SIL0 | IEC104:M_SP_NA_1 | 6364 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6364 | 0 | 1 | deiPWRBPSCLE3033KVOFPR_E300VTFuseFail | 4 |  |  | 0 | $ComStatus , , | #[1VTF] : VT Fuse Failure / MCB Trip
683 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFPR | 33KVOFPR_E300 | 134 | BckpCurTrip | SIL0 | IEC104:M_SP_NA_1 | 6365 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6365 | 0 | 1 | deiPWRBPSCLE3033KVOFPR_E300BckpCurTrip | 4 |  |  | 0 | $ComStatus , , | #[OCPO] : Backup Overcurrent I>Trip
684 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFPR | 33KVOFPR_E300 | 134 | InterTripR | SIL0 | IEC104:M_SP_NA_1 | 6366 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6366 | 0 | 1 | deiPWRBPSCLE3033KVOFPR_E300InterTripR | 4 |  |  | 0 | $ComStatus , , | #[INTR] : Intertrip Received
685 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFPR | 33KVOFPR_E300 | 134 | InterTripS | SIL0 | IEC104:M_SP_NA_1 | 6367 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6367 | 0 | 1 | deiPWRBPSCLE3033KVOFPR_E300InterTripS | 4 |  |  | 0 | $ComStatus , , | #[INTS] : Intertrip Sent
686 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFPR | 33KVOFPR_E400 | 135 | GenTrip | SIL0 | IEC104:M_SP_NA_1 | 6400 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6400 | 0 | 1 | deiPWRBPSCLE4033KVOFPR_E400GenTrip | 4 |  |  | 0 | $ComStatus , , | #[ETOO] : General Trip
687 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFPR | 33KVOFPR_E400 | 135 | DiffProtTrip | SIL0 | IEC104:M_SP_NA_1 | 6401 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6401 | 0 | 1 | deiPWRBPSCLE4033KVOFPR_E400DiffProtTrip | 4 |  |  | 0 | $ComStatus , , | #[CDPT] : Diff. Prot. Trip
688 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFPR | 33KVOFPR_E400 | 135 | ThermAlSt1 | SIL0 | IEC104:M_SP_NA_1 | 6402 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6402 | 0 | 1 | deiPWRBPSCLE4033KVOFPR_E400ThermAlSt1 | 4 |  |  | 0 | $ComStatus , , | #[QAFA] : Thermal Overload Alarm St-1
689 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFPR | 33KVOFPR_E400 | 135 | FOCFail | SIL0 | IEC104:M_SP_NA_1 | 6403 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6403 | 0 | 1 | deiPWRBPSCLE4033KVOFPR_E400FOCFail | 4 |  |  | 0 | $ComStatus , , | #[CDFA] : Diff Communication Fail
690 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFPR | 33KVOFPR_E400 | 135 | VTFuseFail | SIL0 | IEC104:M_SP_NA_1 | 6404 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6404 | 0 | 1 | deiPWRBPSCLE4033KVOFPR_E400VTFuseFail | 4 |  |  | 0 | $ComStatus , , | #[1VTF] : VT Fuse Failure / MCB Trip
691 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFPR | 33KVOFPR_E400 | 135 | BckpCurTrip | SIL0 | IEC104:M_SP_NA_1 | 6405 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6405 | 0 | 1 | deiPWRBPSCLE4033KVOFPR_E400BckpCurTrip | 4 |  |  | 0 | $ComStatus , , | #[OCPO] : Backup Overcurrent I>Trip
692 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFPR | 33KVOFPR_E400 | 135 | InterTripR | SIL0 | IEC104:M_SP_NA_1 | 6406 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6406 | 0 | 1 | deiPWRBPSCLE4033KVOFPR_E400InterTripR | 4 |  |  | 0 | $ComStatus , , | #[INTR] : Intertrip Received
693 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFPR | 33KVOFPR_E400 | 135 | InterTripS | SIL0 | IEC104:M_SP_NA_1 | 6407 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6407 | 0 | 1 | deiPWRBPSCLE4033KVOFPR_E400InterTripS | 4 |  |  | 0 | $ComStatus , , | #[INTS] : Intertrip Sent
694 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFPR | 33KVOFPR_E500 | 136 | GenTrip | SIL0 | IEC104:M_SP_NA_1 | 6440 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6440 | 0 | 1 | deiPWRBPSCLE5033KVOFPR_E500GenTrip | 4 |  |  | 0 | $ComStatus , , | #[ETOO] : General Trip
695 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFPR | 33KVOFPR_E500 | 136 | DiffProtTrip | SIL0 | IEC104:M_SP_NA_1 | 6441 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6441 | 0 | 1 | deiPWRBPSCLE5033KVOFPR_E500DiffProtTrip | 4 |  |  | 0 | $ComStatus , , | #[CDPT] : Diff. Prot. Trip
696 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFPR | 33KVOFPR_E500 | 136 | ThermAlSt1 | SIL0 | IEC104:M_SP_NA_1 | 6442 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6442 | 0 | 1 | deiPWRBPSCLE5033KVOFPR_E500ThermAlSt1 | 4 |  |  | 0 | $ComStatus , , | #[QAFA] : Thermal Overload Alarm St-1
697 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFPR | 33KVOFPR_E500 | 136 | FOCFail | SIL0 | IEC104:M_SP_NA_1 | 6443 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6443 | 0 | 1 | deiPWRBPSCLE5033KVOFPR_E500FOCFail | 4 |  |  | 0 | $ComStatus , , | #[CDFA] : Diff Communication Fail
698 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFPR | 33KVOFPR_E500 | 136 | VTFuseFail | SIL0 | IEC104:M_SP_NA_1 | 6444 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6444 | 0 | 1 | deiPWRBPSCLE5033KVOFPR_E500VTFuseFail | 4 |  |  | 0 | $ComStatus , , | #[1VTF] : VT Fuse Failure / MCB Trip
699 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFPR | 33KVOFPR_E500 | 136 | BckpCurTrip | SIL0 | IEC104:M_SP_NA_1 | 6445 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6445 | 0 | 1 | deiPWRBPSCLE5033KVOFPR_E500BckpCurTrip | 4 |  |  | 0 | $ComStatus , , | #[OCPO] : Backup Overcurrent I>Trip
700 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFPR | 33KVOFPR_E500 | 136 | InterTripR | SIL0 | IEC104:M_SP_NA_1 | 6446 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6446 | 0 | 1 | deiPWRBPSCLE5033KVOFPR_E500InterTripR | 4 |  |  | 0 | $ComStatus , , | #[INTR] : Intertrip Received
701 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFPR | 33KVOFPR_E500 | 136 | InterTripS | SIL0 | IEC104:M_SP_NA_1 | 6447 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6447 | 0 | 1 | deiPWRBPSCLE5033KVOFPR_E500InterTripS | 4 |  |  | 0 | $ComStatus , , | #[INTS] : Intertrip Sent
702 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFPR | 33KVOFPR_E600 | 137 | GenTrip | SIL0 | IEC104:M_SP_NA_1 | 6480 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6480 | 0 | 1 | deiPWRBPSCLE6033KVOFPR_E600GenTrip | 4 |  |  | 0 | $ComStatus , , | #[ETOO] : General Trip
703 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFPR | 33KVOFPR_E600 | 137 | DiffProtTrip | SIL0 | IEC104:M_SP_NA_1 | 6481 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6481 | 0 | 1 | deiPWRBPSCLE6033KVOFPR_E600DiffProtTrip | 4 |  |  | 0 | $ComStatus , , | #[CDPT] : Diff. Prot. Trip
704 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFPR | 33KVOFPR_E600 | 137 | ThermAlSt1 | SIL0 | IEC104:M_SP_NA_1 | 6482 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6482 | 0 | 1 | deiPWRBPSCLE6033KVOFPR_E600ThermAlSt1 | 4 |  |  | 0 | $ComStatus , , | #[QAFA] : Thermal Overload Alarm St-1
705 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFPR | 33KVOFPR_E600 | 137 | FOCFail | SIL0 | IEC104:M_SP_NA_1 | 6483 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6483 | 0 | 1 | deiPWRBPSCLE6033KVOFPR_E600FOCFail | 4 |  |  | 0 | $ComStatus , , | #[CDFA] : Diff Communication Fail
706 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFPR | 33KVOFPR_E600 | 137 | VTFuseFail | SIL0 | IEC104:M_SP_NA_1 | 6484 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6484 | 0 | 1 | deiPWRBPSCLE6033KVOFPR_E600VTFuseFail | 4 |  |  | 0 | $ComStatus , , | #[1VTF] : VT Fuse Failure / MCB Trip
707 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFPR | 33KVOFPR_E600 | 137 | BckpCurTrip | SIL0 | IEC104:M_SP_NA_1 | 6485 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6485 | 0 | 1 | deiPWRBPSCLE6033KVOFPR_E600BckpCurTrip | 4 |  |  | 0 | $ComStatus , , | #[OCPO] : Backup Overcurrent I>Trip
708 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFPR | 33KVOFPR_E600 | 137 | InterTripR | SIL0 | IEC104:M_SP_NA_1 | 6486 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6486 | 0 | 1 | deiPWRBPSCLE6033KVOFPR_E600InterTripR | 4 |  |  | 0 | $ComStatus , , | #[INTR] : Intertrip Received
709 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFPR | 33KVOFPR_E600 | 137 | InterTripS | SIL0 | IEC104:M_SP_NA_1 | 6487 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6487 | 0 | 1 | deiPWRBPSCLE6033KVOFPR_E600InterTripS | 4 |  |  | 0 | $ComStatus , , | #[INTS] : Intertrip Sent
710 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFMV | 33KVOFMV_E30 | 138 | RPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 12520 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12520 | 0 | 16 | aeiPWRBPSCLE3033KVOFMV_E30RPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #R Phase Current
711 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFMV | 33KVOFMV_E30 | 138 | YPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 12521 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12521 | 0 | 16 | aeiPWRBPSCLE3033KVOFMV_E30YPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #Y Phase Current
712 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFMV | 33KVOFMV_E30 | 138 | BPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 12522 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12522 | 0 | 16 | aeiPWRBPSCLE3033KVOFMV_E30BPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #B Phase Current
713 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFMV | 33KVOFMV_E30 | 138 | NeutralCur | SIL0 | IEC104:M_ME_NA_1 | 12523 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12523 | 0 | 16 | aeiPWRBPSCLE3033KVOFMV_E30NeutralCur | 4 |  |  | 0 | $ComStatus , , | #Neutral Current (In)
714 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFMV | 33KVOFMV_E30 | 138 | RYPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 12524 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12524 | 0 | 16 | aeiPWRBPSCLE3033KVOFMV_E30RYPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #RY Phase Voltage
715 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFMV | 33KVOFMV_E30 | 138 | YBPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 12525 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12525 | 0 | 16 | aeiPWRBPSCLE3033KVOFMV_E30YBPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #YB Phase Voltage
716 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFMV | 33KVOFMV_E30 | 138 | BRPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 12526 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12526 | 0 | 16 | aeiPWRBPSCLE3033KVOFMV_E30BRPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #BR Phase Voltage
717 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFMV | 33KVOFMV_E30 | 138 | ZeroSeqVolt | SIL0 | IEC104:M_ME_NA_1 | 12527 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12527 | 0 | 16 | aeiPWRBPSCLE3033KVOFMV_E30ZeroSeqVolt | 4 |  |  | 0 | $ComStatus , , | #Zero Sequence Voltage (V0)
718 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFMV | 33KVOFMV_E30 | 138 | ActivePower | SIL0 | IEC104:M_ME_NA_1 | 12528 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12528 | 0 | 16 | aeiPWRBPSCLE3033KVOFMV_E30ActivePower | 4 |  |  | 0 | $ComStatus , , | #[MW] : Active Power
719 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFMV | 33KVOFMV_E30 | 138 | ReacPower | SIL0 | IEC104:M_ME_NA_1 | 12529 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12529 | 0 | 16 | aeiPWRBPSCLE3033KVOFMV_E30ReacPower | 4 |  |  | 0 | $ComStatus , , | #[MVAR] : Reactive Power
720 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFMV | 33KVOFMV_E30 | 138 | AppPower | SIL0 | IEC104:M_ME_NA_1 | 12530 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12530 | 0 | 16 | aeiPWRBPSCLE3033KVOFMV_E30AppPower | 4 |  |  | 0 | $ComStatus , , | #Apparent Power (S)
721 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFMV | 33KVOFMV_E30 | 138 | PowerFactor | SIL0 | IEC104:M_ME_NA_1 | 12531 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12531 | 0 | 16 | aeiPWRBPSCLE3033KVOFMV_E30PowerFactor | 4 |  |  | 0 | $ComStatus , , | #Power Factor (P.F)
722 | BPS01_RTU | PWR:BPS:CL | E30 | 33KVOFMV | 33KVOFMV_E30 | 138 | Frequency | SIL0 | IEC104:M_ME_NA_1 | 12532 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12532 | 0 | 16 | aeiPWRBPSCLE3033KVOFMV_E30Frequency | 4 |  |  | 0 | $ComStatus , , | #Frequency (Hz)
723 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFMV | 33KVOFMV_E40 | 139 | RPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 12560 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12560 | 0 | 16 | aeiPWRBPSCLE4033KVOFMV_E40RPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #R Phase Current
724 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFMV | 33KVOFMV_E40 | 139 | YPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 12561 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12561 | 0 | 16 | aeiPWRBPSCLE4033KVOFMV_E40YPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #Y Phase Current
725 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFMV | 33KVOFMV_E40 | 139 | BPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 12562 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12562 | 0 | 16 | aeiPWRBPSCLE4033KVOFMV_E40BPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #B Phase Current
726 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFMV | 33KVOFMV_E40 | 139 | NeutralCur | SIL0 | IEC104:M_ME_NA_1 | 12563 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12563 | 0 | 16 | aeiPWRBPSCLE4033KVOFMV_E40NeutralCur | 4 |  |  | 0 | $ComStatus , , | #Neutral Current (In)
727 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFMV | 33KVOFMV_E40 | 139 | RYPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 12564 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12564 | 0 | 16 | aeiPWRBPSCLE4033KVOFMV_E40RYPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #RY Phase Voltage
728 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFMV | 33KVOFMV_E40 | 139 | YBPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 12565 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12565 | 0 | 16 | aeiPWRBPSCLE4033KVOFMV_E40YBPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #YB Phase Voltage
729 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFMV | 33KVOFMV_E40 | 139 | BRPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 12566 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12566 | 0 | 16 | aeiPWRBPSCLE4033KVOFMV_E40BRPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #BR Phase Voltage
730 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFMV | 33KVOFMV_E40 | 139 | ZeroSeqVolt | SIL0 | IEC104:M_ME_NA_1 | 12567 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12567 | 0 | 16 | aeiPWRBPSCLE4033KVOFMV_E40ZeroSeqVolt | 4 |  |  | 0 | $ComStatus , , | #Zero Sequence Voltage (V0)
731 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFMV | 33KVOFMV_E40 | 139 | ActivePower | SIL0 | IEC104:M_ME_NA_1 | 12568 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12568 | 0 | 16 | aeiPWRBPSCLE4033KVOFMV_E40ActivePower | 4 |  |  | 0 | $ComStatus , , | #[MW] : Active Power
732 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFMV | 33KVOFMV_E40 | 139 | ReacPower | SIL0 | IEC104:M_ME_NA_1 | 12569 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12569 | 0 | 16 | aeiPWRBPSCLE4033KVOFMV_E40ReacPower | 4 |  |  | 0 | $ComStatus , , | #[MVAR] : Reactive Power
733 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFMV | 33KVOFMV_E40 | 139 | AppPower | SIL0 | IEC104:M_ME_NA_1 | 12570 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12570 | 0 | 16 | aeiPWRBPSCLE4033KVOFMV_E40AppPower | 4 |  |  | 0 | $ComStatus , , | #Apparent Power (S)
734 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFMV | 33KVOFMV_E40 | 139 | PowerFactor | SIL0 | IEC104:M_ME_NA_1 | 12571 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12571 | 0 | 16 | aeiPWRBPSCLE4033KVOFMV_E40PowerFactor | 4 |  |  | 0 | $ComStatus , , | #Power Factor (P.F)
735 | BPS01_RTU | PWR:BPS:CL | E40 | 33KVOFMV | 33KVOFMV_E40 | 139 | Frequency | SIL0 | IEC104:M_ME_NA_1 | 12572 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12572 | 0 | 16 | aeiPWRBPSCLE4033KVOFMV_E40Frequency | 4 |  |  | 0 | $ComStatus , , | #Frequency (Hz)
736 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFMV | 33KVOFMV_E50 | 140 | RPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 12600 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12600 | 0 | 16 | aeiPWRBPSCLE5033KVOFMV_E50RPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #R Phase Current
737 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFMV | 33KVOFMV_E50 | 140 | YPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 12601 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12601 | 0 | 16 | aeiPWRBPSCLE5033KVOFMV_E50YPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #Y Phase Current
738 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFMV | 33KVOFMV_E50 | 140 | BPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 12602 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12602 | 0 | 16 | aeiPWRBPSCLE5033KVOFMV_E50BPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #B Phase Current
739 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFMV | 33KVOFMV_E50 | 140 | NeutralCur | SIL0 | IEC104:M_ME_NA_1 | 12603 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12603 | 0 | 16 | aeiPWRBPSCLE5033KVOFMV_E50NeutralCur | 4 |  |  | 0 | $ComStatus , , | #Neutral Current (In)
740 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFMV | 33KVOFMV_E50 | 140 | RYPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 12604 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12604 | 0 | 16 | aeiPWRBPSCLE5033KVOFMV_E50RYPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #RY Phase Voltage
741 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFMV | 33KVOFMV_E50 | 140 | YBPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 12605 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12605 | 0 | 16 | aeiPWRBPSCLE5033KVOFMV_E50YBPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #YB Phase Voltage
742 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFMV | 33KVOFMV_E50 | 140 | BRPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 12606 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12606 | 0 | 16 | aeiPWRBPSCLE5033KVOFMV_E50BRPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #BR Phase Voltage
743 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFMV | 33KVOFMV_E50 | 140 | ZeroSeqVolt | SIL0 | IEC104:M_ME_NA_1 | 12607 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12607 | 0 | 16 | aeiPWRBPSCLE5033KVOFMV_E50ZeroSeqVolt | 4 |  |  | 0 | $ComStatus , , | #Zero Sequence Voltage (V0)
744 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFMV | 33KVOFMV_E50 | 140 | ActivePower | SIL0 | IEC104:M_ME_NA_1 | 12608 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12608 | 0 | 16 | aeiPWRBPSCLE5033KVOFMV_E50ActivePower | 4 |  |  | 0 | $ComStatus , , | #[MW] : Active Power
745 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFMV | 33KVOFMV_E50 | 140 | ReacPower | SIL0 | IEC104:M_ME_NA_1 | 12609 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12609 | 0 | 16 | aeiPWRBPSCLE5033KVOFMV_E50ReacPower | 4 |  |  | 0 | $ComStatus , , | #[MVAR] : Reactive Power
746 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFMV | 33KVOFMV_E50 | 140 | AppPower | SIL0 | IEC104:M_ME_NA_1 | 12610 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12610 | 0 | 16 | aeiPWRBPSCLE5033KVOFMV_E50AppPower | 4 |  |  | 0 | $ComStatus , , | #Apparent Power (S)
747 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFMV | 33KVOFMV_E50 | 140 | PowerFactor | SIL0 | IEC104:M_ME_NA_1 | 12611 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12611 | 0 | 16 | aeiPWRBPSCLE5033KVOFMV_E50PowerFactor | 4 |  |  | 0 | $ComStatus , , | #Power Factor (P.F)
748 | BPS01_RTU | PWR:BPS:CL | E50 | 33KVOFMV | 33KVOFMV_E50 | 140 | Frequency | SIL0 | IEC104:M_ME_NA_1 | 12612 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12612 | 0 | 16 | aeiPWRBPSCLE5033KVOFMV_E50Frequency | 4 |  |  | 0 | $ComStatus , , | #Frequency (Hz)
749 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFMV | 33KVOFMV_E60 | 141 | RPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 12640 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12640 | 0 | 16 | aeiPWRBPSCLE6033KVOFMV_E60RPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #R Phase Current
750 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFMV | 33KVOFMV_E60 | 141 | YPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 12641 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12641 | 0 | 16 | aeiPWRBPSCLE6033KVOFMV_E60YPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #Y Phase Current
751 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFMV | 33KVOFMV_E60 | 141 | BPhaseCurr | SIL0 | IEC104:M_ME_NA_1 | 12642 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12642 | 0 | 16 | aeiPWRBPSCLE6033KVOFMV_E60BPhaseCurr | 4 |  |  | 0 | $ComStatus , , | #B Phase Current
752 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFMV | 33KVOFMV_E60 | 141 | NeutralCur | SIL0 | IEC104:M_ME_NA_1 | 12643 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12643 | 0 | 16 | aeiPWRBPSCLE6033KVOFMV_E60NeutralCur | 4 |  |  | 0 | $ComStatus , , | #Neutral Current (In)
753 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFMV | 33KVOFMV_E60 | 141 | RYPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 12644 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12644 | 0 | 16 | aeiPWRBPSCLE6033KVOFMV_E60RYPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #RY Phase Voltage
754 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFMV | 33KVOFMV_E60 | 141 | YBPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 12645 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12645 | 0 | 16 | aeiPWRBPSCLE6033KVOFMV_E60YBPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #YB Phase Voltage
755 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFMV | 33KVOFMV_E60 | 141 | BRPhaseVolt | SIL0 | IEC104:M_ME_NA_1 | 12646 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12646 | 0 | 16 | aeiPWRBPSCLE6033KVOFMV_E60BRPhaseVolt | 4 |  |  | 0 | $ComStatus , , | #BR Phase Voltage
756 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFMV | 33KVOFMV_E60 | 141 | ZeroSeqVolt | SIL0 | IEC104:M_ME_NA_1 | 12647 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12647 | 0 | 16 | aeiPWRBPSCLE6033KVOFMV_E60ZeroSeqVolt | 4 |  |  | 0 | $ComStatus , , | #Zero Sequence Voltage (V0)
757 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFMV | 33KVOFMV_E60 | 141 | ActivePower | SIL0 | IEC104:M_ME_NA_1 | 12648 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12648 | 0 | 16 | aeiPWRBPSCLE6033KVOFMV_E60ActivePower | 4 |  |  | 0 | $ComStatus , , | #[MW] : Active Power
758 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFMV | 33KVOFMV_E60 | 141 | ReacPower | SIL0 | IEC104:M_ME_NA_1 | 12649 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12649 | 0 | 16 | aeiPWRBPSCLE6033KVOFMV_E60ReacPower | 4 |  |  | 0 | $ComStatus , , | #[MVAR] : Reactive Power
759 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFMV | 33KVOFMV_E60 | 141 | AppPower | SIL0 | IEC104:M_ME_NA_1 | 12650 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12650 | 0 | 16 | aeiPWRBPSCLE6033KVOFMV_E60AppPower | 4 |  |  | 0 | $ComStatus , , | #Apparent Power (S)
760 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFMV | 33KVOFMV_E60 | 141 | PowerFactor | SIL0 | IEC104:M_ME_NA_1 | 12651 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12651 | 0 | 16 | aeiPWRBPSCLE6033KVOFMV_E60PowerFactor | 4 |  |  | 0 | $ComStatus , , | #Power Factor (P.F)
761 | BPS01_RTU | PWR:BPS:CL | E60 | 33KVOFMV | 33KVOFMV_E60 | 141 | Frequency | SIL0 | IEC104:M_ME_NA_1 | 12652 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12652 | 0 | 16 | aeiPWRBPSCLE6033KVOFMV_E60Frequency | 4 |  |  | 0 | $ComStatus , , | #Frequency (Hz)
762 | BPS01_RTU | PWR:BPS:CL | E30 | BCA | BCA_E30 | 142 | DGCCCtrl | SIL0 | IEC104:M_SP_NA_1 | 6681 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6681 | 0 | 1 | deiPWRBPSCLE30BCA_E30DGCCCtrl | 4 |  |  | 0 | $ComStatus , , | #[CBLC] : DGCC Control
763 | BPS01_RTU | PWR:BPS:CL | E30 | BCA | BCA_E30 | 142 | BCUCardStatus | SIL0 | IEC104:M_SP_NA_1 | 6682 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6682 | 0 | 1 | deiPWRBPSCLE30BCA_E30BCUCardStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : Card Fail
764 | BPS01_RTU | PWR:BPS:CL | E40 | BCA | BCA_E40 | 143 | DGCCCtrl | SIL0 | IEC104:M_SP_NA_1 | 6721 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6721 | 0 | 1 | deiPWRBPSCLE40BCA_E40DGCCCtrl | 4 |  |  | 0 | $ComStatus , , | #[CBLC] : DGCC Control
765 | BPS01_RTU | PWR:BPS:CL | E40 | BCA | BCA_E40 | 143 | BCUCardStatus | SIL0 | IEC104:M_SP_NA_1 | 6722 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6722 | 0 | 1 | deiPWRBPSCLE40BCA_E40BCUCardStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : Card Fail
766 | BPS01_RTU | PWR:BPS:CL | E50 | BCA | BCA_E50 | 144 | DGCCCtrl | SIL0 | IEC104:M_SP_NA_1 | 6761 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6761 | 0 | 1 | deiPWRBPSCLE50BCA_E50DGCCCtrl | 4 |  |  | 0 | $ComStatus , , | #[CBLC] : DGCC Control
767 | BPS01_RTU | PWR:BPS:CL | E50 | BCA | BCA_E50 | 144 | BCUCardStatus | SIL0 | IEC104:M_SP_NA_1 | 6762 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6762 | 0 | 1 | deiPWRBPSCLE50BCA_E50BCUCardStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : Card Fail
768 | BPS01_RTU | PWR:BPS:CL | E60 | BCA | BCA_E60 | 145 | DGCCCtrl | SIL0 | IEC104:M_SP_NA_1 | 6801 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6801 | 0 | 1 | deiPWRBPSCLE60BCA_E60DGCCCtrl | 4 |  |  | 0 | $ComStatus , , | #[CBLC] : DGCC Control
769 | BPS01_RTU | PWR:BPS:CL | E60 | BCA | BCA_E60 | 145 | BCUCardStatus | SIL0 | IEC104:M_SP_NA_1 | 6802 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6802 | 0 | 1 | deiPWRBPSCLE60BCA_E60BCUCardStatus | 4 |  |  | 0 | $ComStatus , , | #[WDOG] : Card Fail
770 | BPS01_RTU | PWR:BPS:CL | E10 | AUXTF | AT1 | 146 | ATBuchAlm | SIL0 | IEC104:M_SP_NA_1 | 6840 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6840 | 0 | 1 | deiPWRBPSCLE10AT1ATBuchAlm | 4 |  |  | 0 | $ComStatus , , | #[ETBA] : 1000kVA Auxiliary Transformer Buchholz Alarm
771 | BPS01_RTU | PWR:BPS:CL | E10 | AUXTF | AT1 | 146 | ATBuchTrip | SIL0 | IEC104:M_SP_NA_1 | 6841 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6841 | 0 | 1 | deiPWRBPSCLE10AT1ATBuchTrip | 4 |  |  | 0 | $ComStatus , , | #[ETBT] : 1000kVA Auxiliary Transformer Buchholz Trip
772 | BPS01_RTU | PWR:BPS:CL | E10 | AUXTF | AT1 | 146 | OilLevelAlmMin | SIL0 | IEC104:M_SP_NA_1 | 6842 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6842 | 0 | 1 | deiPWRBPSCLE10AT1OilLevelAlmMin | 4 |  |  | 0 | $ComStatus , , | #[OLEA] : Oil Level Alarm Min
773 | BPS01_RTU | PWR:BPS:CL | E10 | AUXTF | AT1 | 146 | OilLevelAlmMax | SIL0 | IEC104:M_SP_NA_1 | 6843 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6843 | 0 | 1 | deiPWRBPSCLE10AT1OilLevelAlmMax | 4 |  |  | 0 | $ComStatus , , | #[OLEA] : Oil Level Alarm Max
774 | BPS01_RTU | PWR:BPS:CL | E10 | AUXTF | AT1 | 146 | OilTempAlm | SIL0 | IEC104:M_SP_NA_1 | 6844 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6844 | 0 | 1 | deiPWRBPSCLE10AT1OilTempAlm | 4 |  |  | 0 | $ComStatus , , | #[OTAL] : 1000kVA Auxiliary Transformer Oil Temperature Alarm
775 | BPS01_RTU | PWR:BPS:CL | E10 | AUXTF | AT1 | 146 | ATPRVAlm | SIL0 | IEC104:M_SP_NA_1 | 6845 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6845 | 0 | 1 | deiPWRBPSCLE10AT1ATPRVAlm | 4 |  |  | 0 | $ComStatus , , | #[ETPA] : 1000kVA Auxiliary Transformer PRV Alarm
776 | BPS01_RTU | PWR:BPS:CL | E10 | AUXTF | AT1 | 146 | ATOilTempTrip | SIL0 | IEC104:M_SP_NA_1 | 6846 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6846 | 0 | 1 | deiPWRBPSCLE10AT1ATOilTempTrip | 4 |  |  | 0 | $ComStatus , , | #[OTTR] : 1000kVA Auxiliary Transformer Oil Temp Trip
777 | BPS01_RTU | PWR:BPS:CL | E10 | AUXTF | AT1 | 146 | ATPRDTrip | SIL0 | IEC104:M_SP_NA_1 | 6847 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6847 | 0 | 1 | deiPWRBPSCLE10AT1ATPRDTrip | 4 |  |  | 0 | $ComStatus , , | #[PRVT] : 1000kVA Auxiliary Transformer PRD Trip
778 | BPS01_RTU | PWR:BPS:CL | E10 | AUXTF | AT1 | 146 | ATWindTempAlm | SIL0 | IEC104:M_SP_NA_1 | 6848 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6848 | 0 | 1 | deiPWRBPSCLE10AT1ATWindTempAlm | 4 |  |  | 0 | $ComStatus , , | #[WGTA] : 1000 kVA Auxilary Transformer Winding Temperature Alarm
779 | BPS01_RTU | PWR:BPS:CL | E10 | AUXTF | AT1 | 146 | ATWindTempTrip | SIL0 | IEC104:M_SP_NA_1 | 6849 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6849 | 0 | 1 | deiPWRBPSCLE10AT1ATWindTempTrip | 4 |  |  | 0 | $ComStatus , , | #[WGTT] : 1000 kVA Auxiliary Transformer Winding Temperature Trip
780 | BPS01_RTU | PWR:BPS:CL | E10 | AUXTF | AT1 | 146 | SpringChargeFail | SIL0 | IEC104:M_SP_NA_1 | 6850 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6850 | 0 | 1 | deiPWRBPSCLE10AT1SpringChargeFail | 4 |  |  | 0 | $ComStatus , , | #[SPCF] : CB Spring Charge Fail
781 | BPS01_RTU | PWR:BPS:CL | E20 | AUXTF | AT2 | 147 | ATBuchAlm | SIL0 | IEC104:M_SP_NA_1 | 6880 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6880 | 0 | 1 | deiPWRBPSCLE20AT2ATBuchAlm | 4 |  |  | 0 | $ComStatus , , | #[ETBA] : 1000kVA Auxiliary Transformer Buchholz Alarm
782 | BPS01_RTU | PWR:BPS:CL | E20 | AUXTF | AT2 | 147 | ATBuchTrip | SIL0 | IEC104:M_SP_NA_1 | 6881 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6881 | 0 | 1 | deiPWRBPSCLE20AT2ATBuchTrip | 4 |  |  | 0 | $ComStatus , , | #[ETBT] : 1000kVA Auxiliary Transformer Buchholz Trip
783 | BPS01_RTU | PWR:BPS:CL | E20 | AUXTF | AT2 | 147 | OilLevelAlmMin | SIL0 | IEC104:M_SP_NA_1 | 6882 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6882 | 0 | 1 | deiPWRBPSCLE20AT2OilLevelAlmMin | 4 |  |  | 0 | $ComStatus , , | #[OLEA] : Oil Level Alarm Min
784 | BPS01_RTU | PWR:BPS:CL | E20 | AUXTF | AT2 | 147 | OilLevelAlmMax | SIL0 | IEC104:M_SP_NA_1 | 6883 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6883 | 0 | 1 | deiPWRBPSCLE20AT2OilLevelAlmMax | 4 |  |  | 0 | $ComStatus , , | #[OLEA] : Oil Level Alarm Max
785 | BPS01_RTU | PWR:BPS:CL | E20 | AUXTF | AT2 | 147 | OilTempAlm | SIL0 | IEC104:M_SP_NA_1 | 6884 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6884 | 0 | 1 | deiPWRBPSCLE20AT2OilTempAlm | 4 |  |  | 0 | $ComStatus , , | #[OTAL] : 1000kVA Auxiliary Transformer Oil Temperature Alarm
786 | BPS01_RTU | PWR:BPS:CL | E20 | AUXTF | AT2 | 147 | ATPRVAlm | SIL0 | IEC104:M_SP_NA_1 | 6885 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6885 | 0 | 1 | deiPWRBPSCLE20AT2ATPRVAlm | 4 |  |  | 0 | $ComStatus , , | #[ETPA] : 1000kVA Auxiliary Transformer PRV Alarm
787 | BPS01_RTU | PWR:BPS:CL | E20 | AUXTF | AT2 | 147 | ATOilTempTrip | SIL0 | IEC104:M_SP_NA_1 | 6886 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6886 | 0 | 1 | deiPWRBPSCLE20AT2ATOilTempTrip | 4 |  |  | 0 | $ComStatus , , | #[OTTR] : 1000kVA Auxiliary Transformer Oil Temp Trip
788 | BPS01_RTU | PWR:BPS:CL | E20 | AUXTF | AT2 | 147 | ATPRDTrip | SIL0 | IEC104:M_SP_NA_1 | 6887 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6887 | 0 | 1 | deiPWRBPSCLE20AT2ATPRDTrip | 4 |  |  | 0 | $ComStatus , , | #[PRVT] : 1000kVA Auxiliary Transformer PRD Trip
789 | BPS01_RTU | PWR:BPS:CL | E20 | AUXTF | AT2 | 147 | ATWindTempAlm | SIL0 | IEC104:M_SP_NA_1 | 6888 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6888 | 0 | 1 | deiPWRBPSCLE20AT2ATWindTempAlm | 4 |  |  | 0 | $ComStatus , , | #[WGTA] : 1000 kVA Auxilary Transformer Winding Temperature Alarm
790 | BPS01_RTU | PWR:BPS:CL | E20 | AUXTF | AT2 | 147 | ATWindTempTrip | SIL0 | IEC104:M_SP_NA_1 | 6889 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6889 | 0 | 1 | deiPWRBPSCLE20AT2ATWindTempTrip | 4 |  |  | 0 | $ComStatus , , | #[WGTT] : 1000 kVA Auxiliary Transformer Winding Temperature Trip
791 | BPS01_RTU | PWR:BPS:CL | E20 | AUXTF | AT2 | 147 | SpringChargeFail | SIL0 | IEC104:M_SP_NA_1 | 6890 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6890 | 0 | 1 | deiPWRBPSCLE20AT2SpringChargeFail | 4 |  |  | 0 | $ComStatus , , | #[SPCF] : CB Spring Charge Fail
792 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | PRDTrip | SIL0 | IEC104:M_SP_NA_1 | 6920 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6920 | 0 | 1 | deiPWRBPSCLE18BE-T1PRDTrip | 4 |  |  | 0 | $ComStatus , , | #[PRVT] : Press Relief Device Trip M1/M2
793 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | PRDOltcTrip | SIL0 | IEC104:M_SP_NA_1 | 6921 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6921 | 0 | 1 | deiPWRBPSCLE18BE-T1PRDOltcTrip | 4 |  |  | 0 | $ComStatus , , | #[PREL] : Press Relief Device OLTC Trip
794 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | PRDCableBoxTrip | SIL0 | IEC104:M_SP_NA_1 | 6922 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6922 | 0 | 1 | deiPWRBPSCLE18BE-T1PRDCableBoxTrip | 4 |  |  | 0 | $ComStatus , , | #[PREL] : Press Relief Device Trip HV Cable Box
795 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | WindTempHV | SIL0 | IEC104:M_SP_NA_1 | 6923 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6923 | 0 | 1 | deiPWRBPSCLE18BE-T1WindTempHV | 4 |  |  | 0 | $ComStatus , , | #[WGTA] : Winding Temp HV Alarm
796 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | WindTempLV | SIL0 | IEC104:M_SP_NA_1 | 6924 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6924 | 0 | 1 | deiPWRBPSCLE18BE-T1WindTempLV | 4 |  |  | 0 | $ComStatus , , | #[WGTA] : Winding Temp LV Alarm
797 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | OilTempTrip | SIL0 | IEC104:M_SP_NA_1 | 6925 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6925 | 0 | 1 | deiPWRBPSCLE18BE-T1OilTempTrip | 4 |  |  | 0 | $ComStatus , , | #[OITT] : Oil Temperature Trip
798 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | BuchTrip | SIL0 | IEC104:M_SP_NA_1 | 6926 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6926 | 0 | 1 | deiPWRBPSCLE18BE-T1BuchTrip | 4 |  |  | 0 | $ComStatus , , | #[MTBT] : Buchholz Relay Trip - Main Tank
799 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | BuchDSTrip | SIL0 | IEC104:M_SP_NA_1 | 6927 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6927 | 0 | 1 | deiPWRBPSCLE18BE-T1BuchDSTrip | 4 |  |  | 0 | $ComStatus , , | #[MTBT] : Buchholz Relay Trip - Diverter Sw
800 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | BuchCblBoxTrip | SIL0 | IEC104:M_SP_NA_1 | 6928 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6928 | 0 | 1 | deiPWRBPSCLE18BE-T1BuchCblBoxTrip | 4 |  |  | 0 | $ComStatus , , | #[BUTH] : Buchholz Relay Trip - CBL Box HV
801 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | AVRFail | SIL0 | IEC104:M_SP_NA_1 | 6929 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6929 | 0 | 1 | deiPWRBPSCLE18BE-T1AVRFail | 4 |  |  | 0 | $ComStatus , , | #[IRFA] : AVR Relay Fail
802 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | AVRDCFail | SIL0 | IEC104:M_SP_NA_1 | 6930 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6930 | 0 | 1 | deiPWRBPSCLE18BE-T1AVRDCFail | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : AVR DC Supply MCB Fail
803 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | TapHigh | SIL0 | IEC104:M_SP_NA_1 | 6931 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6931 | 0 | 1 | deiPWRBPSCLE18BE-T1TapHigh | 4 |  |  | 0 | $ComStatus , , | #[TCER] : Tap Changer High Limit
804 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | TapLow | SIL0 | IEC104:M_SP_NA_1 | 6932 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6932 | 0 | 1 | deiPWRBPSCLE18BE-T1TapLow | 4 |  |  | 0 | $ComStatus , , | #[TCER] : Tap Changer Low Limit
805 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | TapOutofStep | SIL0 | IEC104:M_SP_NA_1 | 6933 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6933 | 0 | 1 | deiPWRBPSCLE18BE-T1TapOutofStep | 4 |  |  | 0 | $ComStatus , , | #[TCOS] : Tap Changer Out of Step
806 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | TCIncomplete | SIL0 | IEC104:M_SP_NA_1 | 6934 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6934 | 0 | 1 | deiPWRBPSCLE18BE-T1TCIncomplete | 4 |  |  | 0 | $ComStatus , , | #[TCIN] : Tap Changer Incomplete
807 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | AVRBlkRls | SIL0 | IEC104:M_DP_NA_1 | 6975 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 6975 | 0 | 2 | deiPWRBPSCLE18BE-T1AVRBlkRls | 4 |  |  | 0 | $ComStatus , , | #[B/R] : AVR Block Release Status
808 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | WdgTmpHV | SIL0 | IEC104:M_ME_NA_1 | 12922 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12922 | 0 | 16 | aeiPWRBPSCLE18BE-T1WdgTmpHV | 4 |  |  | 0 | $ComStatus , , | #[WTEM]: Wdg Temp Indicator (HV)
809 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | WdgTmpLV | SIL0 | IEC104:M_ME_NA_1 | 12923 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12923 | 0 | 16 | aeiPWRBPSCLE18BE-T1WdgTmpLV | 4 |  |  | 0 | $ComStatus , , | #[WTEM]: Wdg Temp Indicator (LV)
810 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | CmdBlock | SIL0 | IEC104:C_DC_NA_1 | 27961 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27961 | 0 | 2 | deoPWRBPSCLE18BE-T1CmdBlock | 4 |  |  | 0 | $ComStatus , , | #[B/R] : AVR BLK/REL Cmd
811 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | CmdAuto | SIL0 | IEC104:C_DC_NA_1 | 27962 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27962 | 0 | 2 | deoPWRBPSCLE18BE-T1CmdAuto | 4 |  |  | 0 | $ComStatus , , | #[A/M] : AVR Auto/Man Cmd
812 | BPS01_RTU | PWR:BPS:CL | E18 | POWTF | BE-T1 | 148 | CmdRaise | SIL0 | IEC104:C_DC_NA_1 | 27963 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27963 | 0 | 2 | deoPWRBPSCLE18BE-T1CmdRaise | 4 |  |  | 0 | $ComStatus , , | #[TCSN] : TAP RA/LO
813 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | PRDTrip | SIL0 | IEC104:M_SP_NA_1 | 6960 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6960 | 0 | 1 | deiPWRBPSCLE28BE-T2PRDTrip | 4 |  |  | 0 | $ComStatus , , | #[PRVT] : Press Relief Device Trip M1/M2
814 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | PRDOltcTrip | SIL0 | IEC104:M_SP_NA_1 | 6961 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6961 | 0 | 1 | deiPWRBPSCLE28BE-T2PRDOltcTrip | 4 |  |  | 0 | $ComStatus , , | #[PREL] : Press Relief Device OLTC Trip
815 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | PRDCableBoxTrip | SIL0 | IEC104:M_SP_NA_1 | 6962 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6962 | 0 | 1 | deiPWRBPSCLE28BE-T2PRDCableBoxTrip | 4 |  |  | 0 | $ComStatus , , | #[PREL] : Press Relief Device Trip HV Cable Box
816 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | WindTempHV | SIL0 | IEC104:M_SP_NA_1 | 6963 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6963 | 0 | 1 | deiPWRBPSCLE28BE-T2WindTempHV | 4 |  |  | 0 | $ComStatus , , | #[WGTA] : Winding Temp HV Alarm
817 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | WindTempLV | SIL0 | IEC104:M_SP_NA_1 | 6964 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6964 | 0 | 1 | deiPWRBPSCLE28BE-T2WindTempLV | 4 |  |  | 0 | $ComStatus , , | #[WGTA] : Winding Temp LV Alarm
818 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | OilTempTrip | SIL0 | IEC104:M_SP_NA_1 | 6965 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6965 | 0 | 1 | deiPWRBPSCLE28BE-T2OilTempTrip | 4 |  |  | 0 | $ComStatus , , | #[OITT] : Oil Temperature Trip
819 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | BuchTrip | SIL0 | IEC104:M_SP_NA_1 | 6966 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6966 | 0 | 1 | deiPWRBPSCLE28BE-T2BuchTrip | 4 |  |  | 0 | $ComStatus , , | #[MTBT] : Buchholz Relay Trip - Main Tank
820 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | BuchDSTrip | SIL0 | IEC104:M_SP_NA_1 | 6967 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6967 | 0 | 1 | deiPWRBPSCLE28BE-T2BuchDSTrip | 4 |  |  | 0 | $ComStatus , , | #[MTBT] : Buchholz Relay Trip - Diverter Sw
821 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | BuchCblBoxTrip | SIL0 | IEC104:M_SP_NA_1 | 6968 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6968 | 0 | 1 | deiPWRBPSCLE28BE-T2BuchCblBoxTrip | 4 |  |  | 0 | $ComStatus , , | #[BUTH] : Buchholz Relay Trip - CBL Box HV
822 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | AVRFail | SIL0 | IEC104:M_SP_NA_1 | 6969 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6969 | 0 | 1 | deiPWRBPSCLE28BE-T2AVRFail | 4 |  |  | 0 | $ComStatus , , | #[IRFA] : AVR Relay Fail
823 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | AVRDCFail | SIL0 | IEC104:M_SP_NA_1 | 6970 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6970 | 0 | 1 | deiPWRBPSCLE28BE-T2AVRDCFail | 4 |  |  | 0 | $ComStatus , , | #[DCAB] : AVR DC Supply MCB Fail
824 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | TapHigh | SIL0 | IEC104:M_SP_NA_1 | 6971 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6971 | 0 | 1 | deiPWRBPSCLE28BE-T2TapHigh | 4 |  |  | 0 | $ComStatus , , | #[TCER] : Tap Changer High Limit
825 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | TapLow | SIL0 | IEC104:M_SP_NA_1 | 6972 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6972 | 0 | 1 | deiPWRBPSCLE28BE-T2TapLow | 4 |  |  | 0 | $ComStatus , , | #[TCER] : Tap Changer Low Limit
826 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | TapOutofStep | SIL0 | IEC104:M_SP_NA_1 | 6973 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6973 | 0 | 1 | deiPWRBPSCLE28BE-T2TapOutofStep | 4 |  |  | 0 | $ComStatus , , | #[TCOS] : Tap Changer Out of Step
827 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | TCIncomplete | SIL0 | IEC104:M_SP_NA_1 | 6974 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 6974 | 0 | 1 | deiPWRBPSCLE28BE-T2TCIncomplete | 4 |  |  | 0 | $ComStatus , , | #[TCIN] : Tap Changer Incomplete
828 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | AVRBlkRls | SIL0 | IEC104:M_DP_NA_1 | 6995 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_DP_TB | 1 | 6995 | 0 | 2 | deiPWRBPSCLE28BE-T2AVRBlkRls | 4 |  |  | 0 | $ComStatus , , | #[B/R] : AVR Block Release Status
829 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | WdgTmpHV | SIL0 | IEC104:M_ME_NA_1 | 12962 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12962 | 0 | 16 | aeiPWRBPSCLE28BE-T2WdgTmpHV | 4 |  |  | 0 | $ComStatus , , | #[WTEM]: Wdg Temp Indicator (HV)
830 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | WdgTmpLV | SIL0 | IEC104:M_ME_NA_1 | 12963 | 0 | 16 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | AEIV | M_ME_NA | 1 | 12963 | 0 | 16 | aeiPWRBPSCLE28BE-T2WdgTmpLV | 4 |  |  | 0 | $ComStatus , , | #[WTEM]: Wdg Temp Indicator (LV)
831 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | CmdBlock | SIL0 | IEC104:C_DC_NA_1 | 27981 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27981 | 0 | 2 | deoPWRBPSCLE28BE-T2CmdBlock | 4 |  |  | 0 | $ComStatus , , | #[B/R] : AVR BLK/REL Cmd
832 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | CmdAuto | SIL0 | IEC104:C_DC_NA_1 | 27982 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27982 | 0 | 2 | deoPWRBPSCLE28BE-T2CmdAuto | 4 |  |  | 0 | $ComStatus , , | #[A/M] : AVR Auto/Man Cmd
833 | BPS01_RTU | PWR:BPS:CL | E28 | POWTF | BE-T2 | 149 | CmdRaise | SIL0 | IEC104:C_DC_NA_1 | 27983 | 0 | 2 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEOV | C_DC_NA | 1 | 27983 | 0 | 2 | deoPWRBPSCLE28BE-T2CmdRaise | 4 |  |  | 0 | $ComStatus , , | #[TCSN] : TAP RA/LO
834 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVLVAC | LVAC_66KV | 150 | Inc1TrpStatus | SIL0 | IEC104:M_SP_NA_1 | 7000 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7000 | 0 | 1 | deiPWRBPSCLLVAC_66KVLVAC_66KVInc1TrpStatus | 4 |  |  | 0 | $ComStatus , , | #[IN1T] : Incomer 1 Breaker Trip
835 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVLVAC | LVAC_66KV | 150 | Inc2TrpStatus | SIL0 | IEC104:M_SP_NA_1 | 7001 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7001 | 0 | 1 | deiPWRBPSCLLVAC_66KVLVAC_66KVInc2TrpStatus | 4 |  |  | 0 | $ComStatus , , | #[IN2T] : Incomer 2 Breaker Trip
836 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVLVAC | LVAC_66KV | 150 | BSBreakerTrip | SIL0 | IEC104:M_SP_NA_1 | 7002 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7002 | 0 | 1 | deiPWRBPSCLLVAC_66KVLVAC_66KVBSBreakerTrip | 4 |  |  | 0 | $ComStatus , , | #[BUST] : Bus Section Breaker Trip
837 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVLVAC | LVAC_66KV | 150 | Bus1Fault | SIL0 | IEC104:M_SP_NA_1 | 7003 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7003 | 0 | 1 | deiPWRBPSCLLVAC_66KVLVAC_66KVBus1Fault | 4 |  |  | 0 | $ComStatus , , | #[FALB] : Bus-1 Feeder Fault
838 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVLVAC | LVAC_66KV | 150 | Bus2Fault | SIL0 | IEC104:M_SP_NA_1 | 7004 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7004 | 0 | 1 | deiPWRBPSCLLVAC_66KVLVAC_66KVBus2Fault | 4 |  |  | 0 | $ComStatus , , | #[FALR] : Bus-2 Feeder Fault
839 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVLVAC | LVAC_66KV | 150 | ACCtrlMCBStatus | SIL0 | IEC104:M_SP_NA_1 | 7005 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7005 | 0 | 1 | deiPWRBPSCLLVAC_66KVLVAC_66KVACCtrlMCBStatus | 4 |  |  | 0 | $ComStatus , , | #[TRAS] : AC Control MCB Off/Trip
840 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVLVAC | LVAC_66KV | 150 | DCCtrlMCBStatus | SIL0 | IEC104:M_SP_NA_1 | 7006 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7006 | 0 | 1 | deiPWRBPSCLLVAC_66KVLVAC_66KVDCCtrlMCBStatus | 4 |  |  | 0 | $ComStatus , , | #[LVDC] : DC Control MCB Off/Trip
841 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-1_66KV | 151 | ChargerFault | SIL0 | IEC104:M_SP_NA_1 | 7040 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7040 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-1_66KVChargerFault | 4 |  |  | 0 | $ComStatus , , | #[CH1F] : Charger Fault
842 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-1_66KV | 151 | ACFail | SIL0 | IEC104:M_SP_NA_1 | 7041 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7041 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-1_66KVACFail | 4 |  |  | 0 | $ComStatus , , | #[C1AS] : AC Supply Failure
843 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-1_66KV | 151 | BattCharge1Fail | SIL0 | IEC104:M_SP_NA_1 | 7042 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7042 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-1_66KVBattCharge1Fail | 4 |  |  | 0 | $ComStatus , , | #[CH1F] : Battery Charger Fail
844 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-1_66KV | 151 | EqualizerCharge | SIL0 | IEC104:M_SP_NA_1 | 7043 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7043 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-1_66KVEqualizerCharge | 4 |  |  | 0 | $ComStatus , , | #[CHBA] : Charger on Equalizer Charge
845 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-1_66KV | 151 | ChargerUV | SIL0 | IEC104:M_SP_NA_1 | 7044 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7044 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-1_66KVChargerUV | 4 |  |  | 0 | $ComStatus , , | #[C1UV] : Charger Under Voltage
846 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-1_66KV | 151 | ChargerBoost | SIL0 | IEC104:M_SP_NA_1 | 7045 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7045 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-1_66KVChargerBoost | 4 |  |  | 0 | $ComStatus , , | #[CHBA] : Charger on Boost Charge
847 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-1_66KV | 151 | BattFuseFail | SIL0 | IEC104:M_SP_NA_1 | 7046 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7046 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-1_66KVBattFuseFail | 4 |  |  | 0 | $ComStatus , , | #[B1FF] : Battery Fuse Failure
848 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-1_66KV | 151 | BattFanFail | SIL0 | IEC104:M_SP_NA_1 | 7047 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7047 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-1_66KVBattFanFail | 4 |  |  | 0 | $ComStatus , , | #[CH1F] : Battery Charger Fan Fail
849 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-1_66KV | 151 | ChargerOverload | SIL0 | IEC104:M_SP_NA_1 | 7048 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7048 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-1_66KVChargerOverload | 4 |  |  | 0 | $ComStatus , , | #[C1LF] : Charger Overload
850 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-1_66KV | 151 | DCFail | SIL0 | IEC104:M_SP_NA_1 | 7049 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7049 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-1_66KVDCFail | 4 |  |  | 0 | $ComStatus , , | #[C1AS] : DC Supply Failure
851 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-2_66KV | 152 | ChargerFault | SIL0 | IEC104:M_SP_NA_1 | 7080 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7080 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-2_66KVChargerFault | 4 |  |  | 0 | $ComStatus , , | #[CH1F] : Charger Fault
852 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-2_66KV | 152 | ACFail | SIL0 | IEC104:M_SP_NA_1 | 7081 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7081 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-2_66KVACFail | 4 |  |  | 0 | $ComStatus , , | #[C1AS] : AC Supply Failure
853 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-2_66KV | 152 | BattCharge1Fail | SIL0 | IEC104:M_SP_NA_1 | 7082 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7082 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-2_66KVBattCharge1Fail | 4 |  |  | 0 | $ComStatus , , | #[CH1F] : Battery Charger Fail
854 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-2_66KV | 152 | EqualizerCharge | SIL0 | IEC104:M_SP_NA_1 | 7083 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7083 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-2_66KVEqualizerCharge | 4 |  |  | 0 | $ComStatus , , | #[CHBA] : Charger on Equalizer Charge
855 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-2_66KV | 152 | ChargerUV | SIL0 | IEC104:M_SP_NA_1 | 7084 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7084 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-2_66KVChargerUV | 4 |  |  | 0 | $ComStatus , , | #[C1UV] : Charger Under Voltage
856 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-2_66KV | 152 | ChargerBoost | SIL0 | IEC104:M_SP_NA_1 | 7085 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7085 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-2_66KVChargerBoost | 4 |  |  | 0 | $ComStatus , , | #[CHBA] : Charger on Boost Charge
857 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-2_66KV | 152 | BattFuseFail | SIL0 | IEC104:M_SP_NA_1 | 7086 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7086 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-2_66KVBattFuseFail | 4 |  |  | 0 | $ComStatus , , | #[B1FF] : Battery Fuse Failure
858 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-2_66KV | 152 | BattFanFail | SIL0 | IEC104:M_SP_NA_1 | 7087 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7087 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-2_66KVBattFanFail | 4 |  |  | 0 | $ComStatus , , | #[CH1F] : Battery Charger Fan Fail
859 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-2_66KV | 152 | ChargerOverload | SIL0 | IEC104:M_SP_NA_1 | 7088 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7088 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-2_66KVChargerOverload | 4 |  |  | 0 | $ComStatus , , | #[C1LF] : Charger Overload
860 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVBATC | BATC-2_66KV | 152 | DCFail | SIL0 | IEC104:M_SP_NA_1 | 7089 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7089 | 0 | 1 | deiPWRBPSCLLVAC_66KVBATC-2_66KVDCFail | 4 |  |  | 0 | $ComStatus , , | #[C1AS] : DC Supply Failure
861 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVLVDC | LVDC_66KV | 153 | Inc1TrpStatus | SIL0 | IEC104:M_SP_NA_1 | 7120 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7120 | 0 | 1 | deiPWRBPSCLLVAC_66KVLVDC_66KVInc1TrpStatus | 4 |  |  | 0 | $ComStatus , , | #[LVOL] : Incomer 1 Trip
862 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVLVDC | LVDC_66KV | 153 | Inc2TrpStatus | SIL0 | IEC104:M_SP_NA_1 | 7121 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7121 | 0 | 1 | deiPWRBPSCLLVAC_66KVLVDC_66KVInc2TrpStatus | 4 |  |  | 0 | $ComStatus , , | #[LVOR] : Incomer 2 Trip
863 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVLVDC | LVDC_66KV | 153 | ACCtrlMCBStatus | SIL0 | IEC104:M_SP_NA_1 | 7122 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7122 | 0 | 1 | deiPWRBPSCLLVAC_66KVLVDC_66KVACCtrlMCBStatus | 4 |  |  | 0 | $ComStatus , , | #[TRAS] : AC Control MCB Off/Trip
864 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVLVDC | LVDC_66KV | 153 | DCLeftFdrTrip | SIL0 | IEC104:M_SP_NA_1 | 7123 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7123 | 0 | 1 | deiPWRBPSCLLVAC_66KVLVDC_66KVDCLeftFdrTrip | 4 |  |  | 0 | $ComStatus , , | #[FELF] : DC Feeder Left Bus Trip
865 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVLVDC | LVDC_66KV | 153 | DCRightFdrTrip | SIL0 | IEC104:M_SP_NA_1 | 7124 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7124 | 0 | 1 | deiPWRBPSCLLVAC_66KVLVDC_66KVDCRightFdrTrip | 4 |  |  | 0 | $ComStatus , , | #[FELR] : DC Feeder Right Bus Trip
866 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVLVDC | LVDC_66KV | 153 | UVLeftBB | SIL0 | IEC104:M_SP_NA_1 | 7125 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7125 | 0 | 1 | deiPWRBPSCLLVAC_66KVLVDC_66KVUVLeftBB | 4 |  |  | 0 | $ComStatus , , | #[LVOL] : Under Voltage Left Busbar
867 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVLVDC | LVDC_66KV | 153 | UVRightBB | SIL0 | IEC104:M_SP_NA_1 | 7126 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7126 | 0 | 1 | deiPWRBPSCLLVAC_66KVLVDC_66KVUVRightBB | 4 |  |  | 0 | $ComStatus , , | #[LVOR] : Under Voltage Right Busbar
868 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVLVDC | LVDC_66KV | 153 | Inc1EarthFault | SIL0 | IEC104:M_SP_NA_1 | 7127 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7127 | 0 | 1 | deiPWRBPSCLLVAC_66KVLVDC_66KVInc1EarthFault | 4 |  |  | 0 | $ComStatus , , | #[EXF1] : Incomer-1 Earthfault
869 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVLVDC | LVDC_66KV | 153 | Inc2EarthFault | SIL0 | IEC104:M_SP_NA_1 | 7128 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7128 | 0 | 1 | deiPWRBPSCLLVAC_66KVLVDC_66KVInc2EarthFault | 4 |  |  | 0 | $ComStatus , , | #[EXF2] : Incomer-2 Earthfault
870 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | 66KVLVDC | LVDC_66KV | 153 | DCCtrlMCBStatus | SIL0 | IEC104:M_SP_NA_1 | 7129 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7129 | 0 | 1 | deiPWRBPSCLLVAC_66KVLVDC_66KVDCCtrlMCBStatus | 4 |  |  | 0 | $ComStatus , , | #[TRDC] : DC Control MCB Off/Trip
871 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QM1 | 154 | CirBrkStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 7080 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 7080 | 0 | 2 | deiPWRBPSCLLVAC_66KVQM1CirBrkStatus | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Status
872 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QM1 | 154 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 28080 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 28080 | 0 | 2 | deoPWRBPSCLLVAC_66KVQM1CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Open
873 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QM1 | 154 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 28080 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 28080 | 4 | 2 | deiPWRBPSCLLVAC_66KVQM1AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open Ack
874 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QM1 | 154 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 28080 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 28080 | 0 | 2 | deoPWRBPSCLLVAC_66KVQM1CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open
875 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QM1 | 154 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 28080 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 28080 | 2 | 2 | deiPWRBPSCLLVAC_66KVQM1AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Open Ack
876 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QM1 | 154 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 28080 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 28080 | 0 | 2 | deoPWRBPSCLLVAC_66KVQM1CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Close
877 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QM1 | 154 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 28080 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 28080 | 4 | 2 | deiPWRBPSCLLVAC_66KVQM1AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close Ack
878 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QM1 | 154 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 28080 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 28080 | 0 | 2 | deoPWRBPSCLLVAC_66KVQM1CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close
879 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QM1 | 154 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 28080 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 28080 | 2 | 2 | deiPWRBPSCLLVAC_66KVQM1AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Close Ack
880 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QM2 | 155 | CirBrkStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 7100 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 7100 | 0 | 2 | deiPWRBPSCLLVAC_66KVQM2CirBrkStatus | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Status
881 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QM2 | 155 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 28100 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 28100 | 0 | 2 | deoPWRBPSCLLVAC_66KVQM2CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Open
882 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QM2 | 155 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 28100 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 28100 | 4 | 2 | deiPWRBPSCLLVAC_66KVQM2AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open Ack
883 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QM2 | 155 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 28100 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 28100 | 0 | 2 | deoPWRBPSCLLVAC_66KVQM2CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open
884 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QM2 | 155 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 28100 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 28100 | 2 | 2 | deiPWRBPSCLLVAC_66KVQM2AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Open Ack
885 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QM2 | 155 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 28100 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 28100 | 0 | 2 | deoPWRBPSCLLVAC_66KVQM2CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Close
886 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QM2 | 155 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 28100 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 28100 | 4 | 2 | deiPWRBPSCLLVAC_66KVQM2AckSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close Ack
887 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QM2 | 155 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 28100 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 28100 | 0 | 2 | deoPWRBPSCLLVAC_66KVQM2CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close
888 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QM2 | 155 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 28100 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 28100 | 2 | 2 | deiPWRBPSCLLVAC_66KVQM2AckExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Close Ack
889 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QBS | 156 | CirBrkStatus | SIL2_Monitoring | IEC104:M_DP_NA_1 | 7120 | 0 | 2 |  |  | BPS-SIL2_Monitoring | BPS_CL | BPS01_RTU_S2M_EVariables.dat | DEIV | M_DP_TB | 1 | 7120 | 0 | 2 | deiPWRBPSCLLVAC_66KVQBSCirBrkStatus | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Status
890 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QBS | 156 | CmdSelOpen | SIL2_Control | IEC104:C_DC_NA_1 | 28120 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 28120 | 0 | 2 | deoPWRBPSCLLVAC_66KVQBSCmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Open
891 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QBS | 156 | AckSelOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 28120 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 28120 | 4 | 2 | deiPWRBPSCLLVAC_66KVQBSAckSelOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open Ack
892 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QBS | 156 | CmdExeOpen | SIL2_Control | IEC104:C_DC_NA_1 | 28120 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 28120 | 0 | 2 | deoPWRBPSCLLVAC_66KVQBSCmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Open
893 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QBS | 156 | AckExeOpen | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 28120 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 28120 | 2 | 2 | deiPWRBPSCLLVAC_66KVQBSAckExeOpen | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Open Ack
894 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QBS | 156 | CmdSelClose | SIL2_Control | IEC104:C_DC_NA_1 | 28120 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 28120 | 0 | 2 | deoPWRBPSCLLVAC_66KVQBSCmdSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Close
895 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QBS | 156 | AckSelClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 28120 | 4 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 28120 | 4 | 2 | deiPWRBPSCLLVAC_66KVQBSAckSelClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close Ack
896 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QBS | 156 | CmdExeClose | SIL2_Control | IEC104:C_DC_NA_1 | 28120 | 0 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEOV | C_DC_NA | 1 | 28120 | 0 | 2 | deoPWRBPSCLLVAC_66KVQBSCmdExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Select Close
897 | BPS01_RTU | PWR:BPS:CL | LVAC_66KV | CB | QBS | 156 | AckExeClose | SIL2_Control | IEC104:C_DC_NA_RESULT_1 | 28120 | 2 | 2 |  |  | BPS-SIL2_Control | BPS_CL | BPS01_RTU_S2C_EVariables.dat | DEIV | C_DC_NA_RESULT | 1 | 28120 | 2 | 2 | deiPWRBPSCLLVAC_66KVQBSAckExeClose | 4 |  |  | 0 | $ComStatus , , | #[CBST] : Circuit Breaker Control Execute Close Ack
898 | BPS01_RTU | PWR:BPS:CL | LVDC_33KV | 33KVLVDC | LVDC_33KV | 157 | Inc1TrpStatus | SIL0 | IEC104:M_SP_NA_1 | 7280 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7280 | 0 | 1 | deiPWRBPSCLLVDC_33KVLVDC_33KVInc1TrpStatus | 4 |  |  | 0 | $ComStatus , , | #[IN1T] : Incomer-1 MCCB Trip
899 | BPS01_RTU | PWR:BPS:CL | LVDC_33KV | 33KVLVDC | LVDC_33KV | 157 | Inc2TrpStatus | SIL0 | IEC104:M_SP_NA_1 | 7281 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7281 | 0 | 1 | deiPWRBPSCLLVDC_33KVLVDC_33KVInc2TrpStatus | 4 |  |  | 0 | $ComStatus , , | #[IN2T] : Incomer-2 MCCB Trip
900 | BPS01_RTU | PWR:BPS:CL | LVDC_33KV | 33KVLVDC | LVDC_33KV | 157 | BSMCCBTrip | SIL0 | IEC104:M_SP_NA_1 | 7282 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7282 | 0 | 1 | deiPWRBPSCLLVDC_33KVLVDC_33KVBSMCCBTrip | 4 |  |  | 0 | $ComStatus , , | #[BUST] : Bus Section MCCB Trip
901 | BPS01_RTU | PWR:BPS:CL | LVDC_33KV | 33KVLVDC | LVDC_33KV | 157 | BS1OgTrip | SIL0 | IEC104:M_SP_NA_1 | 7283 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7283 | 0 | 1 | deiPWRBPSCLLVDC_33KVLVDC_33KVBS1OgTrip | 4 |  |  | 0 | $ComStatus , , | #[FALB] : Bus-1 O/G Trip
902 | BPS01_RTU | PWR:BPS:CL | LVDC_33KV | 33KVLVDC | LVDC_33KV | 157 | BS2OgTrip | SIL0 | IEC104:M_SP_NA_1 | 7284 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7284 | 0 | 1 | deiPWRBPSCLLVDC_33KVLVDC_33KVBS2OgTrip | 4 |  |  | 0 | $ComStatus , , | #[FALR] : Bus-2 O/G Trip
903 | BPS01_RTU | PWR:BPS:CL | LVDC_33KV | 33KVLVDC | LVDC_33KV | 157 | ACCtrlMCBStatus | SIL0 | IEC104:M_SP_NA_1 | 7285 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7285 | 0 | 1 | deiPWRBPSCLLVDC_33KVLVDC_33KVACCtrlMCBStatus | 4 |  |  | 0 | $ComStatus , , | #[TRAS] : AC Control MCB Off/Trip
904 | BPS01_RTU | PWR:BPS:CL | LVDC_33KV | 33KVLVDC | LVDC_33KV | 157 | DCCtrlMCBStatus | SIL0 | IEC104:M_SP_NA_1 | 7286 | 0 | 1 |  |  | BPS-SIL0 | BPS_CL | BPS01_RTU_S0_EVariables.dat | DEIV | M_SP_TB | 1 | 7286 | 0 | 1 | deiPWRBPSCLLVDC_33KVLVDC_33KVDCCtrlMCBStatus | 4 |  |  | 0 | $ComStatus , , | #[LVDC] : DC Control MCB Off/Trip
-END-

## A-Validation Data list
RTU_Protocol_Operation_Code | Memory_Block | RTU_Protocol | Operation Code List | Association with Memory Block | RTU_Undefined_Operation_Code | RTU_Undefined_Operation_Code | RTU_Modbus_Operation_Code | Modbus_Memory_Block | RTU_IEC104_Operation_Code | IEC104_Memory_Block | RTU_Data_Check_Function | RTU_Data_Translation_Function | Bit_Position
MODBUS:1:Read:Coils | MODBUS:MEMBLOCK01 | MODBUS-TCP | SE_RTU_Modbus_Operation_Code | SE_RTU_Modbus_Table |  |  | MODBUS:1:Read:Coils | MODBUS:MEMBLOCK01 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | cfRANGE | tfNOT | 0
MODBUS:2:Read:Discrete Inputs | MODBUS:MEMBLOCK02 | MODBUS-RTU | SE_RTU_Modbus_Operation_Code | SE_RTU_Modbus_Table |  |  | MODBUS:2:Read:Discrete Inputs | MODBUS:MEMBLOCK02 | IEC104:M_DP_NA_1 | IEC104:MEMBLOCK01 |  | tfLIN | 1
MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | IEC60870-5-104 | SE_RTU_IEC104_Operation_Code | SE_RTU_IEC104_Table |  |  | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 |  | BTL32 | 2
MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | IEC60870-5-101 | SE_RTU_IEC104_Operation_Code | SE_RTU_IEC104_Table |  |  | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | IEC104:M_ME_NB_1 | IEC104:MEMBLOCK01 |  | LTB16 | 3
MODBUS:5:Write:Coil | MODBUS:MEMBLOCK01 | DNP3.0 | SE_RTU_Undefined_Operation_Code | SE_RTU_Undefined_Table |  |  | MODBUS:5:Write:Coil | MODBUS:MEMBLOCK01 | IEC104:M_ME_NC_1 | IEC104:MEMBLOCK01 |  | USHORT | 4
MODBUS:6:Write:Holding Register | MODBUS:MEMBLOCK03 | BACNET-TCP | SE_RTU_Undefined_Operation_Code | SE_RTU_Undefined_Table |  |  | MODBUS:6:Write:Holding Register | MODBUS:MEMBLOCK03 | IEC104:M_IT_NA_1 | IEC104:MEMBLOCK01 |  |  | 5
MODBUS:15:Write:Coils | MODBUS:MEMBLOCK01 |  | SE_RTU_Undefined_Operation_Code | SE_RTU_Undefined_Table |  |  | MODBUS:15:Write:Coils | MODBUS:MEMBLOCK01 | IEC104:M_SP_TB_1 | IEC104:MEMBLOCK01 |  |  | 6
MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [5 empty] | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | IEC104:M_DP_TB_1 | IEC104:MEMBLOCK01 |  |  | 7
IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SC_NA_1 | IEC104:MEMBLOCK01 |  |  | 8
IEC104:M_DP_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SC_NA_RESULT_1 | IEC104:MEMBLOCK01 |  |  | 9
IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_DC_NA_RESULT_1 | IEC104:MEMBLOCK01 |  |  | 10
IEC104:M_ME_NB_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 |  |  | 11
IEC104:M_ME_NC_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_RC_NA_1 | IEC104:MEMBLOCK01 |  |  | 12
IEC104:M_IT_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SE_NA_1 | IEC104:MEMBLOCK01 |  |  | 13
IEC104:M_SP_TB_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SE_NB_1 | IEC104:MEMBLOCK01 |  |  | 14
IEC104:M_DP_TB_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SE_NC_1 | IEC104:MEMBLOCK01 |  |  | 15
IEC104:C_SC_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_IC_NA_1 | IEC104:MEMBLOCK01 |  |  | 16
IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_CI_NA_1 | IEC104:MEMBLOCK01 |  |  | 17
IEC104:C_SC_NA_RESULT_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_RD_NA_1 | IEC104:MEMBLOCK01 |  |  | 18
IEC104:C_DC_NA_RESULT_1 | IEC104:MEMBLOCK01 | [11 empty] | 19
IEC104:C_RC_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 20
IEC104:C_SE_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 21
IEC104:C_SE_NB_1 | IEC104:MEMBLOCK01 | [11 empty] | 22
IEC104:C_SE_NC_1 | IEC104:MEMBLOCK01 | [11 empty] | 23
IEC104:C_IC_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 24
IEC104:C_CI_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 25
IEC104:C_RD_NA_1 | IEC104:MEMBLOCK01 | Check of Validation Lists | [10 empty] | 26
|  | PLC Protocol | Available Operation Code | [9 empty] | 27
|  | IEC60870-5-104 | IEC104:M_ME_NA_1 | [9 empty] | 28
|  | MODBUS-RTU | MODBUS:4:Read:Input Registers | [9 empty] | 29
30
31
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
Note on E1: BERNARD Olivier: This column identifies the list to the associated operation codes. This list is defined through a name (Excel Formula name)

## B-Address Qty
FC / Class Name | BBPZ | BBAL | BBPR | ISST | BIST | CB | CB_OST | BSCP | 66KVIFPR | 33KVIFPR | 66KVBSPR | 33KVBSPR | 66KVHVPR | 33KVSTPR | 33KVOFPR | ESST | ESSM | 66KVIFBA | 33KVIFBA | 66KVHVBA | 33KVSTBA | 66KVBSBA | 33KVBSBA | 33KVOFBA | Gateway | GTW | 66KVLVAC | 66KVBATC | 66KVLVDC | 33KVLVDC | 66KVIFMV | 33KVIFMV | 66KVHVMV | 33KVSTMV | 66KVBSMV | 33KVBSMV | 33KVOFMV | 33KVVM | 66KVVM | VTIS | WTDG | AUXTF | POWTF | BCA
MODBUS:1:Read:Coils | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000
MODBUS:2:Read:Discrete Inputs | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000
MODBUS:3:Read:Holding Registers | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000
MODBUS:4:Read:Input Registers | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000
MODBUS:5:Write:Coil | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000
MODBUS:6:Write:Holding Register | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000
MODBUS:15:Write:Coils | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000
MODBUS:16:Write:Holding Registers | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000
IEC104:M_SP_NA_1 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000
IEC104:M_DP_NA_1 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000 | 20;4000
IEC104:M_ME_NA_1 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000 | 40;7000
IEC104:M_ME_NB_1 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000
IEC104:M_ME_NC_1 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000 | 20;13000
IEC104:M_IT_NA_1 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000 | 40;16000
IEC104:M_SP_TB_1 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000 | 40;17000
IEC104:M_DP_TB_1 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000 | 20;20000
IEC104:C_SC_NA_1 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000
IEC104:C_DC_NA_1 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000
IEC104:C_RC_NA_1 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000 | 20;27000
IEC104:C_SE_NA_1 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000 | 20;28000
IEC104:C_SE_NB_1 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000 | 20;29000
IEC104:C_SE_NC_1 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000 | 20;30000
IEC104:C_IC_NA_1 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000 | 20;31000
IEC104:C_CI_NA_1 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000 | 20;32000
IEC104:C_RD_NA_1 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000 | 20;33000
IEC104:C_SC_NA_RESULT_1 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000 | 20;23000
IEC104:C_DC_NA_RESULT_1 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000 | 20;25000