## Revision Register(变更记录)
Revision (版本) | Description of the modification(变更说明) | Company（公司） | By(修改者) | Date (日期)
1.0 | 根据厂家资料制定初版。 | SUPCON | 丁涛 | 2018-03-14
1.1 | 增加BAS CIP使用的标签列 AX | THALES | Xiaona | 2018-06-05
1.2 | 填写模拟量的单位。 | SUPCON | 丁涛 | 2018-06-29
1.3 | Update DB Info | THALES | Chao | 2018-07-21

## CLASS
row_no. | Version_Control |  |  | Equipment_Geographical_information |  | Equipment_Information |  |  |  |  | Attribute_Information(Internal_Variable,IV) |  |  |  | Digital_Type_Meanings-Alarm/Event[DI]/Control[DO] | [33 empty] | Register Address 寄存器地址 |  |  | Analogue_Type_Alarm/Event_Meanings[AI] | [8 empty] | Alarm_Behaviors |  |  |  |  | General_Control_Requirements |  |  |  | Control_Requirements[DO] | [31 empty] | Control_Requirements_[AO] |  |  |  | Control_Requirements_[SO] |  |  | SCADA_Functional_Requirement | [6 empty] | Drawing |  |  | SCADAsoft_Database | [9 empty] | SCADAsoft_DAC | [13 empty] | FEP_Addressing
# | IO_Version | A/M/D/I | ChkResult_Class-List | Station_Code 车站名称 | Equipment_Location 设备所在地 | System 系统 | (Sub)System 子系统 | Eqpt_Code 设备类码 | Eqpt_Description 设备描述 | Eqpt_Identifier 设备标签 | Attribute_Description 属性描述 | unit 单位 | DC_Data_Type IO 类型 | HMI_Order | v0_label(0) 值0标签 | v0_Severity 值0严重度 | v0_State 值0状态 | v0_Format 值0格式 | v1_label(1) 值1标签 | v1_Severity 值1严重度 | v1_State 值1状态 | v1_Format 值1格式 | v2_label(10) 值2标签 | v2_Severity 值2严重度 | v2_State 值2状态 | v2_Format 值2格式 | v3_label(11) 值3标签 | v3_Severity 值3严重度 | v3_State 值3状态 | v3_Format 值3格式 | v4_label(100) 值4标签 | v4_Severity 值4严重度 | v4_State 值4状态 | v4_Format 值4格式 | v5_label(101) 值5标签 | v5_Severity 值5严重度 | v5_State 值5状态 | v5_Format 值5格式 | v6_label(110) 值6标签 | v6_Severity 值6严重度 | v6_State 值6状态 | v6_Format 值6格式 | v7_label(111) 值7标签 | v7_Severity 值7严重度 | v7_State 值7状态 | v7_Format 值7格式 | Other_bits_meanings | Transition_Interval_(sec) 过度超时间隔 | ISCS/BAS用 PLC内存标签名称(BAS ONLY) | Register Address 寄存器地址 | Register Bit/ Bit number 寄存器比特/比特号 | Value_Out_of_Range_LOW(i) 报警下限 | Value_LOWER_Limit(ii) 报警下下限 | Value_UPPER_Limit(iii) 报警上上限 | Value_Out_of_Range_HIGH(iv) 报警上限 | Min_value_acquired 度量前模拟有效范围最低值 | Max_value_acquired 度量前模拟有效范围最高值 | 模拟度量 Scaling factor | Transformation_Function 模拟位移量 | 抖动量 Jittorfactor | Alarm_CE_Behaviour | valueAutomanton | ackAutomaton | hidden | theme | Initial_Condition(s)_before_Ctl 允许控制条件 | Return_Condition(s)_after_Ctl 反馈条件 | initCond_TO 允许控制超时时间 | ReturnCond_TO 反馈控制超时时间 | v0_dov_name | v0_CtlVal | v0_InitCond | v0_ReturnCond | v1_dov_name | v1_CtlVal | v1_InitCond | v1_ReturnCond | v2_dov_name | v2_CtlVal | v2_InitCond | v2_ReturnCond | v3_dov_name | v3_CtlVal | v3_InitCond | v3_ReturnCond | v4_dov_name | v4_CtlVal | v4_InitCond | v4_ReturnCond | v5_dov_name | v5_CtlVal | v5_InitCond | v5_ReturnCond | v6_dov_name | v6_CtlVal | v6_InitCond | v6_ReturnCond | v7_dov_name | v7_CtlVal | v7_InitCond | v7_ReturnCond | Init_Condition_CE AO允许控制条件 | Return_Condition_CE AO反馈条件 | Lower_limit 下限 | Upper_limit 上限 | Init_Condition_CE SO允许控制条件 | Return_Condition_CE | byte_reference | Archive_name | Handover_Right 控制权限 | Double_Ctl_CMD 双步命令 | (to_be_define) | (to_be_define) | (to_be_define) | (to_be_define) | Graphic Type (Active Symbol/Active Text/Sub-image/Active backdrop) | Schematic_Path_1 Symbol Path | Schematic_Path_2 Image Path | CFG_Equipment_Class | CFG_Element_Name | CFG_Data_Type | IV_Point_Name | CFG_EQPT_ID | CFG_EQPT_ALIAS | Combined_point_identifier_(w) | Individual_identifier_of_(w) | Combine_Type | DB_Comment | EV_Concentrator | EV_Group | EV_Type | EV_Name | DAC_Scaling_Factor | DAC_Offset_Factor | Transformation_Function | Jittor_Factor | SCADA_Address | varInvalid1 | varInvalid2 | varInvalid3 | CFG_EV_ID | DAC_Comment | swc_id | table_id | start_byte | start_bit | FEP_addr_size
[6 empty] | FG |  | FG__ | 防淹门 |  | 隧道水位 | cm | AI | 1 | [104 empty] | FG_FG__ | basicEquipment | AI | aciFG-WATTUNL
[6 empty] | FG |  | FG__ | 防淹门 |  | 隧道水位上升速度 | m/s | AI | 2 | [104 empty] | FG_FG__ | basicEquipment | AI | aciFG-TUNLRISPD
[6 empty] | FG |  | FG__ | 防淹门 |  | FG开过程状态 |  | DI1 | 3 | 正常 | 0 |  |  | 正在开门 | 0 | [98 empty] | FG_FG__ | basicEquipment | DI1 | dciFG-OPNSTA
[6 empty] | FG |  | FG__ | 防淹门 |  | FG关过程状态 |  | DI1 | 4 | 正常 | 0 |  |  | 正在关门 | 0 | [98 empty] | FG_FG__ | basicEquipment | DI1 | dciFG-CLOSTA
[6 empty] | FG |  | FG__ | 防淹门 |  | FG开到位状态 |  | DI1 | 5 | 正常 | 0 |  |  | 门开启 | 0 | [98 empty] | FG_FG__ | basicEquipment | DI1 | dciFG-OPNPSTA
[6 empty] | FG |  | FG__ | 防淹门 |  | FG关到位状态 |  | DI1 | 6 | 正常 | 0 |  |  | 门关闭 | 0 | [98 empty] | FG_FG__ | basicEquipment | DI1 | dciFG-CLOPSTA
[6 empty] | FG |  | FG__ | 防淹门 |  | 故障报警 |  | DI1 | 7 | 正常 | 0 |  |  | 故障 | 3 | [98 empty] | FG_FG__ | basicEquipment | DI1 | dciFG-FLTALM
[6 empty] | FG |  | FG__ | 防淹门 |  | 现地关门请求 |  | DI1 | 8 | 正常 | 0 |  |  | 请求 | 0 | [98 empty] | FG_FG__ | basicEquipment | DI1 | dciFG-CLOSREST
[6 empty] | FG |  | FG__ | 防淹门 |  | IBP盘关门请求 |  | DI1 | 9 | 正常 | 0 |  |  | 请求 | 0 | [98 empty] | FG_FG__ | basicEquipment | DI1 | dciFG-IBPCLOREST
[6 empty] | FG |  | FG__ | 防淹门 |  | 关门允许 |  | DI1 | 10 | 正常 | 0 |  |  | 允许 | 0 | [98 empty] | FG_FG__ | basicEquipment | DI1 | dciFG-CLOALLOW
[6 empty] | FG |  | FG__ | 防淹门 |  | 水位一级报警 |  | DI1 | 11 | 正常 | 0 |  |  | 报警 | 2 | [98 empty] | FG_FG__ | basicEquipment | DI1 | dciFG-ALMLVL1
[6 empty] | FG |  | FG__ | 防淹门 |  | 水位二级报警 |  | DI1 | 12 | 正常 | 0 |  |  | 报警 | 1 | [98 empty] | FG_FG__ | basicEquipment | DI1 | dciFG-ALMLVL2

## Note
Column Name | Column Description 描述 | Respond Party
Equipment Location 设备所在地 | Description of the location of equipment in layout 设备在布局图中的位置描述 | Column shoud be filled by Contractor 子系统合同商应填写的列
Equipment Type Code 设备类代码 | Equipment Code identifies the type equipment. Should be on 4 characters 代表设备类型的设备代码,应为4个字符.
HMI Equipment Label 装置标签描述 | Equipment lable display in HMI. The length of label should within 10 characters. 在人机界面中显示出来的设备装置标签.标签长度应小于10个字符.
Equipment Code 设备编码 | HMI显示的设备编码，同设计图纸上设备编码
Equipment Description 设备描述 | HMI显示的设备名称，同设计图纸上设备名称
Mode Command 模式指令 | The BAS mode triggered after received the FAS alarm. (Using for FAS IO only) 在接收到FAS报警后触发的BAS模式 (仅用于FAS IO)
Attribute Description 属性描述 （中文) | Any meaningful text describing the attribute of the equipment. 设备属性的文字描述
Digital Meaning Type 数字表示类型 | Input Digital Meaning Type. For the digital signal, it is the text associated if the value is at 0,1… i.e. 0 = Open, 1 Close. 输入数字表示类型. 对于数字信号, 当输入值为0,1…时对应的文字描述. 例如: 0 = 开, 1 = 关.
IO type Analog/Digital - Input/Output IO 类型 | Specify the type of point: DI, DO: Digital input/output AI, AO: Analog input/output SI, SO: Structure input/output for non-standard exchange (messages, Alarm Text…) 输入输出点的类型描述: DI, DO: 数字输入/输出 AI, AO: 模拟输入/输出 SI, SO: 结构输入/输出, 针对非标准的交换信息(信息,报警文本...)
Register Address 寄存器地址 | Register address shall be filled with according to the protocol design document. 应根据协议设计文档填写寄存器地址.
Register Bit / Bit number 寄存器比特 / 比特号 | Bit number for representing the equipment status/Alarm. 标识设备状态/报警的比特号.
Related AutoCAD Drawing name 对应的图纸名 | The drawing name that subsystem equipment location could be found 描述子系统设备位置的图纸名
Analog valid range Min before scale 度量前模拟有效范围最低值 | The minimum value send to ISCS before scalling 度量前发送给ISCS系统的最低值
Analog valid range Max before scale 度量前模拟有效范围最高值 | The maximum value send to ISCS before scalling 度量前发送给ISCS系统的最高值
Analog scale(a) = (Value+b)*a 模拟度量 | The scale used to calculate the figures for analog in ISCS. (Analog value displayed in HMI= Analog valid range * Analog scaling) 在ISCS中显示的模拟量的度量值. (人机界面中显示的模拟量值=模拟量有效值*模拟度量)
Jitter Factor 抖动量 | Jitter Factor is a numberical range for analog point that determinating whether the value updating in MMI and recorded in ISCS. Normally, it is should be defined as 0.2% of the maximun analog valid range after scaled. 抖动值是一个模拟点的数字范围,供以决定是否在人机界面中显示或在ISCS中记录其值的变化.一般来说,抖动值定义为度量后的最大有效值的0.2%.
Lower Alarm Limit 报警下限 | For analogue input point only: designed for alarm triggering when the value below the defults limits 仅针对模拟输入点: 当点值低于限制,触发报警.
Upper Alarm Limit 报警上限 | For analogue input point only: designed for alarm triggering when the value over the defults limits 仅针对模拟输入点: 当点值高于限制,触发报警.
Accuracy 精确度 | For analogue input point only: Designed for number of decemial place that display in HMI. (eg. X.XX) 仅针对模拟输入点: 指定在人机界面中显示的小数点后的位数.
Analog Unit 模拟单位 | Only need to input if IO Type is Analog (i.e. AI, AO) 只针对输入/输出点类型为模拟量的点(如AI, AO)。 Please input in English. 请用英文输入。 Analog unit is the unit used by Analog input/output. e.g. 模拟单位为模拟输入/输出使用的单位， 如 - No unit/无单位 - Voltage/伏特 - Amps /安培 - 1000 V/千伏
Severity 严重读 | 0：Equipment Failure Alarm设备故障告警，提示维护人员及时处理。 1：Emergency Alarm,only including fire alarm and PSCADA important keys (e.g. 10KV,750V,400V keys) shutting down 紧急报警，仅限于火灾报警、供电系统关键设备（例如10kV、750V、400V开关）发生跳闸事故。 2：Accident Alarm,operators must treat at once.For example, the key systerm or equipment failure which makes trains or lines not operate.事故报警，需要操作员立即干预，如关键系统或设备发生故障，影响到列车或地铁线的正常运行。 3：Normal Alarm,operators should treat in given time,such as unimportant equipment failure alarms and foreell alarms.普通报警，需要操作员在给定时间内干预，如非关键设备故障、预告报警。 4：No-critical Alarm,not need to do anything,just pay attention.非关键报警，不需人员干预的报警，但有必要引起操作员注意。
Addressing (FEP) | Internal information | Column shoud be filled by ISCS Contractor ISCS合同商应填写的列
Scadasoft Database | Internal information
MMI | Internal information
*Remarks:
If any discrepancy between IO class and IO list, all the software development, production and Testing should be reference IO class | 如果IO点表和类表有不一致,所有软件开发,生产及测试将以IO类表为准.
The contents now in the template are just examples, not all IO class. | 模板中所列仅为举例，不包括所有类点