## Revision Register(变更记录)
Revision (版本) | Description of the modification(变更说明) | Company（公司） | By(修改者) | Date (日期)
1.0 | 根据厂家资料制定初版（确认模拟量比例系数均由凯发处理，ISCS不再处理，接收值即为实际值）。 | SUPCON | 丁涛 | 2018-06-22
1.1 | 修改L列点属性的空格，修改个别数据类型，修改值0、1描述；删除不需要的报警严重度；合并YHKZ类相同属性；增加部分点报警严重度 | THALES | Xiaona | 2018-06-25

## CLASS
row_no. | Version_Control |  |  | Equipment_Geographical_information |  | Equipment_Information |  |  |  |  | Attribute_Information(Internal_Variable,IV) |  |  |  | Digital_Type_Meanings-Alarm/Event[DI]/Control[DO] | [33 empty] | Register Address 寄存器地址 |  |  | Analogue_Type_Alarm/Event_Meanings[AI] | [8 empty] | Alarm_Behaviors |  |  |  |  | General_Control_Requirements |  |  |  | Control_Requirements[DO] | [31 empty] | Control_Requirements_[AO] |  |  |  | Control_Requirements_[SO] |  |  | SCADA_Functional_Requirement | [6 empty] | Drawing |  |  | SCADAsoft_Database | [9 empty] | SCADAsoft_DAC | [13 empty] | FEP_Addressing
# | IO_Version | A/M/D/I | ChkResult_Class-List | Station_Code 车站名称 | Equipment_Location 设备所在地 | System 系统 | (Sub)System 子系统 | Eqpt_Code 设备类码 | Eqpt_Description 设备描述 | Eqpt_Identifier 设备标签 | Attribute_Description 属性描述 | unit 单位 | DC_Data_Type IO 类型 | HMI_Order | v0_label(0) 值0标签 | v0_Severity 值0严重度 | v0_State 值0状态 | v0_Format 值0格式 | v1_label(1) 值1标签 | v1_Severity 值1严重度 | v1_State 值1状态 | v1_Format 值1格式 | v2_label(10) 值2标签 | v2_Severity 值2严重度 | v2_State 值2状态 | v2_Format 值2格式 | v3_label(11) 值3标签 | v3_Severity 值3严重度 | v3_State 值3状态 | v3_Format 值3格式 | v4_label(100) 值4标签 | v4_Severity 值4严重度 | v4_State 值4状态 | v4_Format 值4格式 | v5_label(101) 值5标签 | v5_Severity 值5严重度 | v5_State 值5状态 | v5_Format 值5格式 | v6_label(110) 值6标签 | v6_Severity 值6严重度 | v6_State 值6状态 | v6_Format 值6格式 | v7_label(111) 值7标签 | v7_Severity 值7严重度 | v7_State 值7状态 | v7_Format 值7格式 | Other_bits_meanings | Transition_Interval_(sec) 过度超时间隔 | ISCS/BAS用 PLC内存标签名称(BAS ONLY) | Register Address 寄存器地址 | Register Bit/ Bit number 寄存器比特/比特号 | Value_Out_of_Range_LOW(i) 报警下限 | Value_LOWER_Limit(ii) 报警下下限 | Value_UPPER_Limit(iii) 报警上上限 | Value_Out_of_Range_HIGH(iv) 报警上限 | Min_value_acquired 度量前模拟有效范围最低值 | Max_value_acquired 度量前模拟有效范围最高值 | 模拟度量 Scaling factor | Transformation_Function 模拟位移量 | 抖动量 Jittorfactor | Alarm_CE_Behaviour | valueAutomanton | ackAutomaton | hidden | theme | Initial_Condition(s)_before_Ctl 允许控制条件 | Return_Condition(s)_after_Ctl 反馈条件 | initCond_TO 允许控制超时时间 | ReturnCond_TO 反馈控制超时时间 | v0_dov_name | v0_CtlVal | v0_InitCond | v0_ReturnCond | v1_dov_name | v1_CtlVal | v1_InitCond | v1_ReturnCond | v2_dov_name | v2_CtlVal | v2_InitCond | v2_ReturnCond | v3_dov_name | v3_CtlVal | v3_InitCond | v3_ReturnCond | v4_dov_name | v4_CtlVal | v4_InitCond | v4_ReturnCond | v5_dov_name | v5_CtlVal | v5_InitCond | v5_ReturnCond | v6_dov_name | v6_CtlVal | v6_InitCond | v6_ReturnCond | v7_dov_name | v7_CtlVal | v7_InitCond | v7_ReturnCond | Init_Condition_CE AO允许控制条件 | Return_Condition_CE AO反馈条件 | Lower_limit 下限 | Upper_limit 上限 | Init_Condition_CE SO允许控制条件 | Return_Condition_CE | byte_reference | Archive_name | Handover_Right 控制权限 | Double_Ctl_CMD 双步命令 | (to_be_define) | (to_be_define) | (to_be_define) | (to_be_define) | Graphic Type (Active Symbol/Active Text/Sub-image/Active backdrop) | Schematic_Path_1 Symbol Path | Schematic_Path_2 Image Path | CFG_Equipment_Class | CFG_Element_Name | CFG_Data_Type | IV_Point_Name | CFG_EQPT_ID | CFG_EQPT_ALIAS | Combined_point_identifier_(w) | Individual_identifier_of_(w) | Combine_Type | DB_Comment | EV_Concentrator | EV_Group | EV_Type | EV_Name | DAC_Scaling_Factor | DAC_Offset_Factor | Transformation_Function | Jittor_Factor | SCADA_Address | varInvalid1 | varInvalid2 | varInvalid3 | CFG_EV_ID | DAC_Comment | swc_id | table_id | start_byte | start_bit | FEP_addr_size
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | A相电流Ia | kA | AI | [105 empty] | PSCADA_AJXG | POWEquipment | AI | 1 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | AEIV | aeiAAAPSCADAAJXG0001-1
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | B相电流Ib | kA | AI | [105 empty] | PSCADA_AJXG | POWEquipment | AI | 2 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | AEIV | aeiAAAPSCADAAJXG0001-2
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | C相电流Ic | kA | AI | [105 empty] | PSCADA_AJXG | POWEquipment | AI | 3 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | AEIV | aeiAAAPSCADAAJXG0001-3
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 零序电流Io | kA | AI | [105 empty] | PSCADA_AJXG | POWEquipment | AI | 4 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | AEIV | aeiAAAPSCADAAJXG0001-4
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | AB线电压Uab | kV | AI | [105 empty] | PSCADA_AJXG | POWEquipment | AI | 5 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | AEIV | aeiAAAPSCADAAJXG0001-5
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | BC线电压Ubc | kV | AI | [105 empty] | PSCADA_AJXG | POWEquipment | AI | 6 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | AEIV | aeiAAAPSCADAAJXG0001-6
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | CA线电压Uca | kV | AI | [105 empty] | PSCADA_AJXG | POWEquipment | AI | 7 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | AEIV | aeiAAAPSCADAAJXG0001-7
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 有功功率 | MW | AI | [105 empty] | PSCADA_AJXG | POWEquipment | AI | 8 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | AEIV | aeiAAAPSCADAAJXG0001-8
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 无功功率 | MVA | AI | [105 empty] | PSCADA_AJXG | POWEquipment | AI | 9 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | AEIV | aeiAAAPSCADAAJXG0001-9
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 功率因数 |  | AI | [105 empty] | PSCADA_AJXG | POWEquipment | AI | 10 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | AEIV | aeiAAAPSCADAAJXG0001-10
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 断路器分位 |  | DI1/SOE |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 11 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-11
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 断路器合位 |  | DI1/SOE |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 12 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-12
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 定时限过流保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 13 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-13
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 定时限零流保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 14 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-14
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | PT回路断线报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 15 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-15
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 气体压力过低报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 16 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-16
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 跳闸回路异常报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 17 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-17
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 断路器操作方式 |  | DI1/SOE |  | 就地 |  |  |  | 远方 | 3 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 18 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-18
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 光纤对侧三工位接地位 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 19 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-19
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 弹簧未储能 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 20 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-20
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | PT-MCB位置状态 |  | DI1/SOE |  | 分位 |  |  |  | 合位 | 2 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 21 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-21
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 电缆电压状态 |  | DI1/SOE |  | 无压 |  |  |  | 有压 | 2 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 22 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-22
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 主保护事故总信号 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 23 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-23
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 合闸条件具备 |  | DI1/SOE |  | 消失 |  |  |  | 发出 | 2 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 24 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-24
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 差动装置异常后备保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 25 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-25
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 差动装置异常报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 26 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-26
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | MCB跳闸报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 27 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-27
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 本柜电压小母线位置状态 |  | DI1/SOE |  | 分位 |  |  |  | 合位 | 2 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 28 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-28
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 主保护装置通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 29 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-29
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 差动保护事故总信号 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 30 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-30
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 光纤纵差保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 31 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-31
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 差动光纤通讯异常 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 32 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-32
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 馈线后备保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 33 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-33
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 母线主保护动作跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 34 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-34
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 母线后备保护动作跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 35 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-35
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 进线失灵保护动作跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 36 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-36
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 光纤中断后备保护动作跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 37 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-37
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 差动保护装置通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_AJXG | POWEquipment | DI1/SOE | 38 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEIV | deiAAAPSCADAAJXG0001-38
|  |  |  | AAA |  | PSCADA | 35kV | AJXG | 35kV进线柜 断路器 |  | 断路器分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_AJXG | POWEquipment | DO2 | 39 | :R:A:AAA:PSCADA:AJXG0001 | <alias>AAAPSCADAAJXG0001 | [6 empty] | DEOV | deoAAAPSCADAAJXG0001-39
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | A相电流Ia | kA | AI | 0 | [104 empty] | PSCADA_ACXG | POWEquipment | AI | 40 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | AEIV | aeiAAAPSCADAACXG0001-40
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | B相电流Ib | kA | AI | 0 | [104 empty] | PSCADA_ACXG | POWEquipment | AI | 41 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | AEIV | aeiAAAPSCADAACXG0001-41
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | C相电流Ic | kA | AI | 0 | [104 empty] | PSCADA_ACXG | POWEquipment | AI | 42 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | AEIV | aeiAAAPSCADAACXG0001-42
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 零序电流Io | kA | AI | 0 | [104 empty] | PSCADA_ACXG | POWEquipment | AI | 43 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | AEIV | aeiAAAPSCADAACXG0001-43
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | AB线电压Uab | kV | AI | 0 | [104 empty] | PSCADA_ACXG | POWEquipment | AI | 44 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | AEIV | aeiAAAPSCADAACXG0001-44
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | BC线电压Ubc | kV | AI | 0 | [104 empty] | PSCADA_ACXG | POWEquipment | AI | 45 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | AEIV | aeiAAAPSCADAACXG0001-45
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | CA线电压Uca | kV | AI | 0 | [104 empty] | PSCADA_ACXG | POWEquipment | AI | 46 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | AEIV | aeiAAAPSCADAACXG0001-46
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 有功功率 | MW | AI | 0 | [104 empty] | PSCADA_ACXG | POWEquipment | AI | 47 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | AEIV | aeiAAAPSCADAACXG0001-47
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 无功功率 | MVA | AI | 0 | [104 empty] | PSCADA_ACXG | POWEquipment | AI | 48 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | AEIV | aeiAAAPSCADAACXG0001-48
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 功率因数 |  | AI | 0 | [104 empty] | PSCADA_ACXG | POWEquipment | AI | 49 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | AEIV | aeiAAAPSCADAACXG0001-49
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 断路器分位 |  | DI1/SOE |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 50 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-50
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 断路器合位 |  | DI1/SOE |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 51 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-51
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 定时限过流保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 52 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-52
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 定时限零流保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 53 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-53
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | PT回路断线报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 54 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-54
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 气体压力过低报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 55 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-55
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 跳闸回路异常报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 56 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-56
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 断路器操作方式 |  | DI1/SOE |  | 就地 |  |  |  | 远方 | 3 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 57 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-57
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 光纤对侧三工位接地位 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 58 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-58
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 弹簧未储能 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 59 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-59
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | PT-MCB位置状态 |  | DI1/SOE |  | 分位 |  |  |  | 合位 | 2 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 60 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-60
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 电缆电压状态 |  | DI1/SOE |  | 无压 |  |  |  | 有压 | 2 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 61 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-61
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 主保护事故总信号 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 62 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-62
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 合闸条件具备 |  | DI1/SOE |  | 消失 |  |  |  | 发出 | 2 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 63 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-63
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 差动装置异常后备保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 64 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-64
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 差动装置异常报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 65 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-65
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | MCB跳闸报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 66 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-66
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 本柜电压小母线位置状态 |  | DI1/SOE |  | 分位 |  |  |  | 合位 | 2 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 67 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-67
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 主保护装置通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 68 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-68
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 差动保护事故总信号 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 69 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-69
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 光纤纵差保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 70 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-70
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 差动光纤通讯异常 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 71 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-71
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 馈线后备保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 72 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-72
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 母线主保护动作跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 73 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-73
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 母线后备保护动作跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 74 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-74
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 出线失灵保护动作跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 75 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-75
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 光纤中断后备保护动作跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 76 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-76
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 差动保护装置通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_ACXG | POWEquipment | DI1/SOE | 77 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEIV | deiAAAPSCADAACXG0001-77
|  |  |  | AAA |  | PSCADA | 35kV | ACXG | 35kV出线柜 断路器 |  | 断路器分合闸指令 |  | DO2 | 0 |  |  |  |  | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_ACXG | POWEquipment | DO2 | 78 | :R:A:AAA:PSCADA:ACXG0001 | <alias>AAAPSCADAACXG0001 | [6 empty] | DEOV | deoAAAPSCADAACXG0001-78
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | A相电流Ia | kA | AI | [105 empty] | PSCADA_DTJX | POWEquipment | AI | 79 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | AEIV | aeiAAAPSCADADTJX0001-79
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | B相电流Ib | kA | AI | [105 empty] | PSCADA_DTJX | POWEquipment | AI | 80 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | AEIV | aeiAAAPSCADADTJX0001-80
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | C相电流Ic | kA | AI | [105 empty] | PSCADA_DTJX | POWEquipment | AI | 81 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | AEIV | aeiAAAPSCADADTJX0001-81
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 零序电流Io | kA | AI | [105 empty] | PSCADA_DTJX | POWEquipment | AI | 82 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | AEIV | aeiAAAPSCADADTJX0001-82
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | AB线电压Uab | kV | AI | [105 empty] | PSCADA_DTJX | POWEquipment | AI | 83 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | AEIV | aeiAAAPSCADADTJX0001-83
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | BC线电压Ubc | kV | AI | [105 empty] | PSCADA_DTJX | POWEquipment | AI | 84 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | AEIV | aeiAAAPSCADADTJX0001-84
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | CA线电压Uca | kV | AI | [105 empty] | PSCADA_DTJX | POWEquipment | AI | 85 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | AEIV | aeiAAAPSCADADTJX0001-85
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 有功功率 | MW | AI | [105 empty] | PSCADA_DTJX | POWEquipment | AI | 86 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | AEIV | aeiAAAPSCADADTJX0001-86
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 无功功率 | MVA | AI | [105 empty] | PSCADA_DTJX | POWEquipment | AI | 87 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | AEIV | aeiAAAPSCADADTJX0001-87
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 功率因数 |  | AI | [105 empty] | PSCADA_DTJX | POWEquipment | AI | 88 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | AEIV | aeiAAAPSCADADTJX0001-88
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 断路器分位 |  | DI1/SOE |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 89 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-89
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 断路器合位 |  | DI1/SOE |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 90 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-90
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 定时限过流保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 91 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-91
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 定时限零流保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 92 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-92
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 馈线后备保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 93 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-93
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 母线主保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 94 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-94
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 出线失灵保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 95 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-95
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 光纤中断后备保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 96 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-96
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | PT回路断线报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 97 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-97
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 气体压力过低报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 98 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-98
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 跳闸回路异常报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 99 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-99
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 断路器操作方式 |  | DI1/SOE |  | 就地 |  |  |  | 远方 | [99 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 100 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-100
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 弹簧未储能 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 101 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-101
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | PT-MCB位置状态 |  | DI1/SOE |  | 分位 |  |  |  | 合位 | 2 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 102 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-102
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 电缆有压 |  | DI1/SOE |  | 无压 |  |  |  | 有压 | 2 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 103 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-103
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 事故总信号 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 104 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-104
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 合闸条件具备 |  | DI1/SOE |  | 消失 |  |  |  | 发出 | 2 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 105 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-105
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 差动装置异常后备保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 106 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-106
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 差动装置异常报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 107 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-107
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | MCB跳闸报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 108 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-108
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 本柜电压小母线位置状态 |  | DI1/SOE |  | 分位 |  |  |  | 合位 | 2 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 109 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-109
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 主保护装置通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 110 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-110
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 差动保护比率制动段动作 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 111 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-111
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 差动保护速动段动作 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 112 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-112
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 差动保护无效 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 113 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-113
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 差动保护通信故障 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 114 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-114
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 重合闸进行中 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 115 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-115
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 后备保护动作 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 116 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-116
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 断路器失灵保护动作 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 117 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-117
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 故障滤波触发 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 118 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-118
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 回路监测告警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 119 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-119
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 开关量信号接收 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 120 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-120
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 开关量信号发出 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 121 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-121
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 差动启动 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 122 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-122
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 差动动作 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 123 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-123
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 差动保护装置通讯状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_DTJX | POWEquipment | DI1/SOE | 124 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEIV | deiAAAPSCADADTJX0001-124
|  |  |  | AAA |  | PSCADA | 35kV | DTJX | 35kV进线柜 断路器 |  | 断路器分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_DTJX | POWEquipment | DO2 | 125 | :R:A:AAA:PSCADA:DTJX0001 | <alias>AAAPSCADADTJX0001 | [6 empty] | DEOV | deoAAAPSCADADTJX0001-125
|  |  |  | AAA |  | PSCADA | 35kV | BHFG | 保护复归 |  | 保护复归 |  | DO2 | [9 empty] | 复归 | [95 empty] | PSCADA_BHFG | POWEquipment | DO2 | 126 | :R:A:AAA:PSCADA:BHFG0001 | <alias>AAAPSCADABHFG0001 | [6 empty] | DEOV | deoAAAPSCADABHFG0001-126
|  |  |  | AAA |  | PSCADA | 35kV | GLKG | 三工位隔离开关 |  | 隔离开关合位 |  | DI1/SOE |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_GLKG | POWEquipment | DI1/SOE | 127 | :R:A:AAA:PSCADA:GLKG0001 | <alias>AAAPSCADAGLKG0001 | [6 empty] | DEIV | deiAAAPSCADAGLKG0001-127
|  |  |  | AAA |  | PSCADA | 35kV | GLKG | 三工位隔离开关 |  | 隔离开关接地位 |  | DI1/SOE |  | 分位 |  |  |  | 合位 | [99 empty] | PSCADA_GLKG | POWEquipment | DI1/SOE | 128 | :R:A:AAA:PSCADA:GLKG0001 | <alias>AAAPSCADAGLKG0001 | [6 empty] | DEIV | deiAAAPSCADAGLKG0001-128
|  |  |  | AAA |  | PSCADA | 35kV | GLKG | 三工位隔离开关 |  | 隔离开关分位 |  | DI1/SOE |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_GLKG | POWEquipment | DI1/SOE | 129 | :R:A:AAA:PSCADA:GLKG0001 | <alias>AAAPSCADAGLKG0001 | [6 empty] | DEIV | deiAAAPSCADAGLKG0001-129
|  |  |  | AAA |  | PSCADA | 35kV | GLKG | 三工位隔离开关 |  | 隔离开关分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_GLKG | POWEquipment | DO2 | 130 | :R:A:AAA:PSCADA:GLKG0001 | <alias>AAAPSCADAGLKG0001 | [6 empty] | DEOV | deoAAAPSCADAGLKG0001-130
|  |  |  | AAA |  | PSCADA | 35kV | ABZT | 35kV母联备自投 |  | 备自投远方投入/退出 |  | DI1/SOE |  | 退出 |  |  |  | 投入 | 1 | [98 empty] | PSCADA_ABZT | POWEquipment | DI1/SOE | 131 | :R:A:AAA:PSCADA:ABZT0001 | <alias>AAAPSCADAABZT0001 | [6 empty] | DEIV | deiAAAPSCADAABZT0001-131
|  |  |  | AAA |  | PSCADA | 35kV | ABZT | 35kV母联备自投 |  | 备自投就地投入/退出 |  | DI1/SOE |  | 退出 |  |  |  | 投入 | 3 | [98 empty] | PSCADA_ABZT | POWEquipment | DI1/SOE | 132 | :R:A:AAA:PSCADA:ABZT0001 | <alias>AAAPSCADAABZT0001 | [6 empty] | DEIV | deiAAAPSCADAABZT0001-132
|  |  |  | AAA |  | PSCADA | 35kV | ABZT | 35kV母联备自投 |  | 备自投投入退出指令 |  | DO2 | [5 empty] | 退出 |  |  |  | 投入 | [95 empty] | PSCADA_ABZT | POWEquipment | DO2 | 133 | :R:A:AAA:PSCADA:ABZT0001 | <alias>AAAPSCADAABZT0001 | [6 empty] | DEOV | deoAAAPSCADAABZT0001-133
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | A相电流Ia | kA | AI | [105 empty] | PSCADA_AMLG | POWEquipment | AI | 134 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | AEIV | aeiAAAPSCADAAMLG0001-134
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | B相电流Ib | kA | AI | [105 empty] | PSCADA_AMLG | POWEquipment | AI | 135 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | AEIV | aeiAAAPSCADAAMLG0001-135
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | C相电流Ic | kA | AI | [105 empty] | PSCADA_AMLG | POWEquipment | AI | 136 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | AEIV | aeiAAAPSCADAAMLG0001-136
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 零序电流Io | kA | AI | [105 empty] | PSCADA_AMLG | POWEquipment | AI | 137 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | AEIV | aeiAAAPSCADAAMLG0001-137
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 有功功率 | MW | AI | [105 empty] | PSCADA_AMLG | POWEquipment | AI | 138 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | AEIV | aeiAAAPSCADAAMLG0001-138
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 无功功率 | MVA | AI | [105 empty] | PSCADA_AMLG | POWEquipment | AI | 139 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | AEIV | aeiAAAPSCADAAMLG0001-139
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 功率因数 |  | AI | [105 empty] | PSCADA_AMLG | POWEquipment | AI | 140 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | AEIV | aeiAAAPSCADAAMLG0001-140
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 断路器分位 |  | DI1/SOE |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 141 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-141
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 断路器合位 |  | DI1/SOE |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 142 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-142
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 过流一段保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 143 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-143
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 零序一段保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 144 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-144
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 跳闸回路异常报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 145 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-145
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 自投成功 |  | DI1/SOE |  | 无意义 |  |  |  | 成功 | 2 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 146 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-146
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 自投失败 |  | DI1/SOE |  | 无意义 |  |  |  | 失败 | 2 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 147 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-147
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 气体压力过低报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 148 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-148
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 断路器操作方式 |  | DI1/SOE |  | 就地 |  |  |  | 远方 | 3 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 149 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-149
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 弹簧未储能 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 150 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-150
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | I段母线有压 |  | DI1/SOE |  | 无意义 |  |  |  | 有压 | 3 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 151 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-151
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | I段母线失压 |  | DI1/SOE |  | 正常 |  |  |  | 失压 | 2 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 152 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-152
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | II段母线有压 |  | DI1/SOE |  | 无意义 |  |  |  | 有压 | 2 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 153 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-153
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | II段母线失压 |  | DI1/SOE |  | 正常 |  |  |  | 失压 | 2 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 154 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-154
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | I段进线启动自投 |  | DI1/SOE |  | 退出 |  |  |  | 投入 | 2 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 155 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-155
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | I段出线启动自投 |  | DI1/SOE |  | 退出 |  |  |  | 投入 | 3 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 156 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-156
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | II段进线启动自投 |  | DI1/SOE |  | 退出 |  |  |  | 投入 | 3 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 157 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-157
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | II段出线启动自投 |  | DI1/SOE |  | 退出 |  |  |  | 投入 | 3 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 158 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-158
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 事故总信号 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 3 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 159 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-159
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 合闸条件具备 |  | DI1/SOE |  | 消失 |  |  |  | 发出 | 1 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 160 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-160
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 定时限过流保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 2 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 161 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-161
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 定时限零流保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 162 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-162
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 馈线断路器失灵后备保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 163 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-163
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | MCB跳闸报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 3 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 164 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-164
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_AMLG | POWEquipment | DI1/SOE | 165 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEIV | deiAAAPSCADAAMLG0001-165
|  |  |  | AAA |  | PSCADA | 35kV | AMLG | 35kV母联柜 断路器 |  | 断路器分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_AMLG | POWEquipment | DO2 | 166 | :R:A:AAA:PSCADA:AMLG0001 | <alias>AAAPSCADAAMLG0001 | [6 empty] | DEOV | deoAAAPSCADAAMLG0001-166
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | 正向有功电度 | MWh | AI | [105 empty] | PSCADA_APDB | POWEquipment | AI | 167 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | AEIV | aeiAAAPSCADAAPDB0001-167
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | 断路器分位 |  | DI1/SOE |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_APDB | POWEquipment | DI1/SOE | 168 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | DEIV | deiAAAPSCADAAPDB0001-168
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | 断路器合位 |  | DI1/SOE |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_APDB | POWEquipment | DI1/SOE | 169 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | DEIV | deiAAAPSCADAAPDB0001-169
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | 电流速断保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_APDB | POWEquipment | DI1/SOE | 170 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | DEIV | deiAAAPSCADAAPDB0001-170
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | 过电流保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_APDB | POWEquipment | DI1/SOE | 171 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | DEIV | deiAAAPSCADAAPDB0001-171
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | 过负荷保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_APDB | POWEquipment | DI1/SOE | 172 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | DEIV | deiAAAPSCADAAPDB0001-172
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | 零序过流保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_APDB | POWEquipment | DI1/SOE | 173 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | DEIV | deiAAAPSCADAAPDB0001-173
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | 跳闸回路异常报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_APDB | POWEquipment | DI1/SOE | 174 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | DEIV | deiAAAPSCADAAPDB0001-174
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | 气体压力过低报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_APDB | POWEquipment | DI1/SOE | 175 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | DEIV | deiAAAPSCADAAPDB0001-175
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | 变压器超温跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_APDB | POWEquipment | DI1/SOE | 176 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | DEIV | deiAAAPSCADAAPDB0001-176
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | 断路器操作方式 |  | DI1/SOE |  | 就地 |  |  |  | 远方 | [99 empty] | PSCADA_APDB | POWEquipment | DI1/SOE | 177 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | DEIV | deiAAAPSCADAAPDB0001-177
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | 弹簧未储能 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_APDB | POWEquipment | DI1/SOE | 178 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | DEIV | deiAAAPSCADAAPDB0001-178
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | 对段保护装置故障报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_APDB | POWEquipment | DI1/SOE | 179 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | DEIV | deiAAAPSCADAAPDB0001-179
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | 事故总信号 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 3 | [98 empty] | PSCADA_APDB | POWEquipment | DI1/SOE | 180 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | DEIV | deiAAAPSCADAAPDB0001-180
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | 变压器开门报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_APDB | POWEquipment | DI1/SOE | 181 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | DEIV | deiAAAPSCADAAPDB0001-181
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | 合闸条件具备 |  | DI1/SOE |  | 消失 |  |  |  | 发出 | 2 | [98 empty] | PSCADA_APDB | POWEquipment | DI1/SOE | 182 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | DEIV | deiAAAPSCADAAPDB0001-182
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | MCB跳闸报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_APDB | POWEquipment | DI1/SOE | 183 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | DEIV | deiAAAPSCADAAPDB0001-183
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_APDB | POWEquipment | DI1/SOE | 184 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | DEIV | deiAAAPSCADAAPDB0001-184
|  |  |  | AAA |  | PSCADA | 35kV | APDB | 35kV配电变馈线柜 断路器 |  | 断路器分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_APDB | POWEquipment | DO2 | 185 | :R:A:AAA:PSCADA:APDB0001 | <alias>AAAPSCADAAPDB0001 | [6 empty] | DEOV | deoAAAPSCADAAPDB0001-185
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 正向有功电度 | MWh | AI | [105 empty] | PSCADA_AZLB | POWEquipment | AI | 186 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | AEIV | aeiAAAPSCADAAZLB0001-186
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 断路器分位 |  | DI1/SOE |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 187 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-187
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 断路器合位 |  | DI1/SOE |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 188 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-188
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 电流速断保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 189 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-189
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 过电流保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 190 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-190
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 过负荷保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 191 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-191
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 零序过流保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 192 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-192
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 跳闸回路异常报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 193 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-193
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 气体压力过低报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 194 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-194
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 整流变压器超温跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 195 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-195
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 整流器故障跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 196 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-196
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 框架泄漏保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 197 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-197
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 直流进线逆流联跳 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 198 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-198
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 断路器操作方式 |  | DI1/SOE |  | 就地 |  |  |  | 远方 | [99 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 199 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-199
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 联跳对侧整流机组 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 200 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-200
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 弹簧未储能 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 201 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-201
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 事故总信号 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 202 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-202
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 合闸条件具备 |  | DI1/SOE |  | 消失 |  |  |  | 发出 | 2 | [98 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 203 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-203
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | MCB跳闸报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 204 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-204
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 联跳对侧整流机组投入 |  | DI1/SOE |  | 退出 |  |  |  | 投入 | 2 | [98 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 205 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-205
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_AZLB | POWEquipment | DI1/SOE | 206 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEIV | deiAAAPSCADAAZLB0001-206
|  |  |  | AAA |  | PSCADA | 35kV | AZLB | 35kV整流变馈线柜 断路器 |  | 断路器分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_AZLB | POWEquipment | DO2 | 207 | :R:A:AAA:PSCADA:AZLB0001 | <alias>AAAPSCADAAZLB0001 | [6 empty] | DEOV | deoAAAPSCADAAZLB0001-207
|  |  |  | AAA |  | PSCADA | 35kV | AGPB | 35kV跟随所配电变馈线柜 断路器 |  | 正向有功电度 | MWh | AI | [105 empty] | PSCADA_AGPB | POWEquipment | AI | 208 | :R:A:AAA:PSCADA:AGPB0001 | <alias>AAAPSCADAAGPB0001 | [6 empty] | AEIV | aeiAAAPSCADAAGPB0001-208
|  |  |  | AAA |  | PSCADA | 35kV | AGPB | 35kV跟随所配电变馈线柜 断路器 |  | 断路器分位 |  | DI1/SOE |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_AGPB | POWEquipment | DI1/SOE | 209 | :R:A:AAA:PSCADA:AGPB0001 | <alias>AAAPSCADAAGPB0001 | [6 empty] | DEIV | deiAAAPSCADAAGPB0001-209
|  |  |  | AAA |  | PSCADA | 35kV | AGPB | 35kV跟随所配电变馈线柜 断路器 |  | 断路器合位 |  | DI1/SOE |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_AGPB | POWEquipment | DI1/SOE | 210 | :R:A:AAA:PSCADA:AGPB0001 | <alias>AAAPSCADAAGPB0001 | [6 empty] | DEIV | deiAAAPSCADAAGPB0001-210
|  |  |  | AAA |  | PSCADA | 35kV | AGPB | 35kV跟随所配电变馈线柜 断路器 |  | 电流速断保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AGPB | POWEquipment | DI1/SOE | 211 | :R:A:AAA:PSCADA:AGPB0001 | <alias>AAAPSCADAAGPB0001 | [6 empty] | DEIV | deiAAAPSCADAAGPB0001-211
|  |  |  | AAA |  | PSCADA | 35kV | AGPB | 35kV跟随所配电变馈线柜 断路器 |  | 过电流保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AGPB | POWEquipment | DI1/SOE | 212 | :R:A:AAA:PSCADA:AGPB0001 | <alias>AAAPSCADAAGPB0001 | [6 empty] | DEIV | deiAAAPSCADAAGPB0001-212
|  |  |  | AAA |  | PSCADA | 35kV | AGPB | 35kV跟随所配电变馈线柜 断路器 |  | 过负荷保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AGPB | POWEquipment | DI1/SOE | 213 | :R:A:AAA:PSCADA:AGPB0001 | <alias>AAAPSCADAAGPB0001 | [6 empty] | DEIV | deiAAAPSCADAAGPB0001-213
|  |  |  | AAA |  | PSCADA | 35kV | AGPB | 35kV跟随所配电变馈线柜 断路器 |  | 零序过流保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AGPB | POWEquipment | DI1/SOE | 214 | :R:A:AAA:PSCADA:AGPB0001 | <alias>AAAPSCADAAGPB0001 | [6 empty] | DEIV | deiAAAPSCADAAGPB0001-214
|  |  |  | AAA |  | PSCADA | 35kV | AGPB | 35kV跟随所配电变馈线柜 断路器 |  | 跳闸回路异常报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AGPB | POWEquipment | DI1/SOE | 215 | :R:A:AAA:PSCADA:AGPB0001 | <alias>AAAPSCADAAGPB0001 | [6 empty] | DEIV | deiAAAPSCADAAGPB0001-215
|  |  |  | AAA |  | PSCADA | 35kV | AGPB | 35kV跟随所配电变馈线柜 断路器 |  | 变压器开门报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AGPB | POWEquipment | DI1/SOE | 216 | :R:A:AAA:PSCADA:AGPB0001 | <alias>AAAPSCADAAGPB0001 | [6 empty] | DEIV | deiAAAPSCADAAGPB0001-216
|  |  |  | AAA |  | PSCADA | 35kV | AGPB | 35kV跟随所配电变馈线柜 断路器 |  | 气体压力过低报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AGPB | POWEquipment | DI1/SOE | 217 | :R:A:AAA:PSCADA:AGPB0001 | <alias>AAAPSCADAAGPB0001 | [6 empty] | DEIV | deiAAAPSCADAAGPB0001-217
|  |  |  | AAA |  | PSCADA | 35kV | AGPB | 35kV跟随所配电变馈线柜 断路器 |  | 变压器超温跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AGPB | POWEquipment | DI1/SOE | 218 | :R:A:AAA:PSCADA:AGPB0001 | <alias>AAAPSCADAAGPB0001 | [6 empty] | DEIV | deiAAAPSCADAAGPB0001-218
|  |  |  | AAA |  | PSCADA | 35kV | AGPB | 35kV跟随所配电变馈线柜 断路器 |  | 断路器操作方式 |  | DI1/SOE |  | 就地 |  |  |  | 远方 | [99 empty] | PSCADA_AGPB | POWEquipment | DI1/SOE | 219 | :R:A:AAA:PSCADA:AGPB0001 | <alias>AAAPSCADAAGPB0001 | [6 empty] | DEIV | deiAAAPSCADAAGPB0001-219
|  |  |  | AAA |  | PSCADA | 35kV | AGPB | 35kV跟随所配电变馈线柜 断路器 |  | 弹簧未储能 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AGPB | POWEquipment | DI1/SOE | 220 | :R:A:AAA:PSCADA:AGPB0001 | <alias>AAAPSCADAAGPB0001 | [6 empty] | DEIV | deiAAAPSCADAAGPB0001-220
|  |  |  | AAA |  | PSCADA | 35kV | AGPB | 35kV跟随所配电变馈线柜 断路器 |  | 事故总信号 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_AGPB | POWEquipment | DI1/SOE | 221 | :R:A:AAA:PSCADA:AGPB0001 | <alias>AAAPSCADAAGPB0001 | [6 empty] | DEIV | deiAAAPSCADAAGPB0001-221
|  |  |  | AAA |  | PSCADA | 35kV | AGPB | 35kV跟随所配电变馈线柜 断路器 |  | 合闸条件具备 |  | DI1/SOE |  | 消失 |  |  |  | 发出 | 2 | [98 empty] | PSCADA_AGPB | POWEquipment | DI1/SOE | 222 | :R:A:AAA:PSCADA:AGPB0001 | <alias>AAAPSCADAAGPB0001 | [6 empty] | DEIV | deiAAAPSCADAAGPB0001-222
|  |  |  | AAA |  | PSCADA | 35kV | AGPB | 35kV跟随所配电变馈线柜 断路器 |  | MCB跳闸报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AGPB | POWEquipment | DI1/SOE | 223 | :R:A:AAA:PSCADA:AGPB0001 | <alias>AAAPSCADAAGPB0001 | [6 empty] | DEIV | deiAAAPSCADAAGPB0001-223
|  |  |  | AAA |  | PSCADA | 35kV | AGPB | 35kV跟随所配电变馈线柜 断路器 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_AGPB | POWEquipment | DI1/SOE | 224 | :R:A:AAA:PSCADA:AGPB0001 | <alias>AAAPSCADAAGPB0001 | [6 empty] | DEIV | deiAAAPSCADAAGPB0001-224
|  |  |  | AAA |  | PSCADA | 35kV | AGPB | 35kV跟随所配电变馈线柜 断路器 |  | 断路器分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_AGPB | POWEquipment | DO2 | 225 | :R:A:AAA:PSCADA:AGPB0001 | <alias>AAAPSCADAAGPB0001 | [6 empty] | DEOV | deoAAAPSCADAAGPB0001-225
|  |  |  | AAA |  | PSCADA | 35kV | AGJX | 35kV跟随所进线柜 隔离开关 |  | A相电流Ia | kA | AI | [105 empty] | PSCADA_AGJX | POWEquipment | AI | 226 | :R:A:AAA:PSCADA:AGJX0001 | <alias>AAAPSCADAAGJX0001 | [6 empty] | AEIV | aeiAAAPSCADAAGJX0001-226
|  |  |  | AAA |  | PSCADA | 35kV | AGJX | 35kV跟随所进线柜 隔离开关 |  | B相电流Ib | kA | AI | [105 empty] | PSCADA_AGJX | POWEquipment | AI | 227 | :R:A:AAA:PSCADA:AGJX0001 | <alias>AAAPSCADAAGJX0001 | [6 empty] | AEIV | aeiAAAPSCADAAGJX0001-227
|  |  |  | AAA |  | PSCADA | 35kV | AGJX | 35kV跟随所进线柜 隔离开关 |  | C相电流Ic | kA | AI | [105 empty] | PSCADA_AGJX | POWEquipment | AI | 228 | :R:A:AAA:PSCADA:AGJX0001 | <alias>AAAPSCADAAGJX0001 | [6 empty] | AEIV | aeiAAAPSCADAAGJX0001-228
|  |  |  | AAA |  | PSCADA | 35kV | AGJX | 35kV跟随所进线柜 隔离开关 |  | 零序电流Io | kA | AI | [105 empty] | PSCADA_AGJX | POWEquipment | AI | 229 | :R:A:AAA:PSCADA:AGJX0001 | <alias>AAAPSCADAAGJX0001 | [6 empty] | AEIV | aeiAAAPSCADAAGJX0001-229
|  |  |  | AAA |  | PSCADA | 35kV | AGJX | 35kV跟随所进线柜 隔离开关 |  | 隔离开关合位 |  | DI1/SOE |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_AGJX | POWEquipment | DI1/SOE | 230 | :R:A:AAA:PSCADA:AGJX0001 | <alias>AAAPSCADAAGJX0001 | [6 empty] | DEIV | deiAAAPSCADAAGJX0001-230
|  |  |  | AAA |  | PSCADA | 35kV | AGJX | 35kV跟随所进线柜 隔离开关 |  | 隔离开关接地位 |  | DI1/SOE |  | 分位 |  |  |  | 合位 | [99 empty] | PSCADA_AGJX | POWEquipment | DI1/SOE | 231 | :R:A:AAA:PSCADA:AGJX0001 | <alias>AAAPSCADAAGJX0001 | [6 empty] | DEIV | deiAAAPSCADAAGJX0001-231
|  |  |  | AAA |  | PSCADA | 35kV | AGJX | 35kV跟随所进线柜 隔离开关 |  | 隔离开关分位 |  | DI1/SOE |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_AGJX | POWEquipment | DI1/SOE | 232 | :R:A:AAA:PSCADA:AGJX0001 | <alias>AAAPSCADAAGJX0001 | [6 empty] | DEIV | deiAAAPSCADAAGJX0001-232
|  |  |  | AAA |  | PSCADA | 35kV | AGJX | 35kV跟随所进线柜 隔离开关 |  | 气体压力过低报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AGJX | POWEquipment | DI1/SOE | 233 | :R:A:AAA:PSCADA:AGJX0001 | <alias>AAAPSCADAAGJX0001 | [6 empty] | DEIV | deiAAAPSCADAAGJX0001-233
|  |  |  | AAA |  | PSCADA | 35kV | AGJX | 35kV跟随所进线柜 隔离开关 |  | 开关操作方式 |  | DI1/SOE |  | 就地 |  |  |  | 远方 | [99 empty] | PSCADA_AGJX | POWEquipment | DI1/SOE | 234 | :R:A:AAA:PSCADA:AGJX0001 | <alias>AAAPSCADAAGJX0001 | [6 empty] | DEIV | deiAAAPSCADAAGJX0001-234
|  |  |  | AAA |  | PSCADA | 35kV | AGJX | 35kV跟随所进线柜 隔离开关 |  | MCB跳闸报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_AGJX | POWEquipment | DI1/SOE | 235 | :R:A:AAA:PSCADA:AGJX0001 | <alias>AAAPSCADAAGJX0001 | [6 empty] | DEIV | deiAAAPSCADAAGJX0001-235
|  |  |  | AAA |  | PSCADA | 35kV | AGJX | 35kV跟随所进线柜 隔离开关 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_AGJX | POWEquipment | DI1/SOE | 236 | :R:A:AAA:PSCADA:AGJX0001 | <alias>AAAPSCADAAGJX0001 | [6 empty] | DEIV | deiAAAPSCADAAGJX0001-236
|  |  |  | AAA |  | PSCADA | 35kV | AGJX | 35kV跟随所进线柜 隔离开关 |  | 开关分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_AGJX | POWEquipment | DO2 | 237 | :R:A:AAA:PSCADA:AGJX0001 | <alias>AAAPSCADAAGJX0001 | [6 empty] | DEOV | deoAAAPSCADAAGJX0001-237
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | A相电流Ia | kA | AI | [105 empty] | PSCADA_NKBG | POWEquipment | AI | 238 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | AEIV | aeiAAAPSCADANKBG0001-238
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | B相电流Ib | kA | AI | [105 empty] | PSCADA_NKBG | POWEquipment | AI | 239 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | AEIV | aeiAAAPSCADANKBG0001-239
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | C相电流Ic | kA | AI | [105 empty] | PSCADA_NKBG | POWEquipment | AI | 240 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | AEIV | aeiAAAPSCADANKBG0001-240
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 零序电流Io | kA | AI | [105 empty] | PSCADA_NKBG | POWEquipment | AI | 241 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | AEIV | aeiAAAPSCADANKBG0001-241
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | AB线电压Uab | kV | AI | [105 empty] | PSCADA_NKBG | POWEquipment | AI | 242 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | AEIV | aeiAAAPSCADANKBG0001-242
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | BC线电压Ubc | kV | AI | [105 empty] | PSCADA_NKBG | POWEquipment | AI | 243 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | AEIV | aeiAAAPSCADANKBG0001-243
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | CA线电压Uca | kV | AI | [105 empty] | PSCADA_NKBG | POWEquipment | AI | 244 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | AEIV | aeiAAAPSCADANKBG0001-244
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 有功功率 | MW | AI | [105 empty] | PSCADA_NKBG | POWEquipment | AI | 245 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | AEIV | aeiAAAPSCADANKBG0001-245
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 无功功率 | MVA | AI | [105 empty] | PSCADA_NKBG | POWEquipment | AI | 246 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | AEIV | aeiAAAPSCADANKBG0001-246
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 功率因数 |  | AI | [105 empty] | PSCADA_NKBG | POWEquipment | AI | 247 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | AEIV | aeiAAAPSCADANKBG0001-247
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 正向有功电度 | MWh | AI | [105 empty] | PSCADA_NKBG | POWEquipment | AI | 248 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | AEIV | aeiAAAPSCADANKBG0001-248
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 正向无功电度 | MVarh | AI | [105 empty] | PSCADA_NKBG | POWEquipment | AI | 249 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | AEIV | aeiAAAPSCADANKBG0001-249
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 断路器分位 |  | DI1/SOE |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_NKBG | POWEquipment | DI1/SOE | 250 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | DEIV | deiAAAPSCADANKBG0001-250
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 断路器合位 |  | DI1/SOE |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_NKBG | POWEquipment | DI1/SOE | 251 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | DEIV | deiAAAPSCADANKBG0001-251
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 电流速断保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NKBG | POWEquipment | DI1/SOE | 252 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | DEIV | deiAAAPSCADANKBG0001-252
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 过电流保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NKBG | POWEquipment | DI1/SOE | 253 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | DEIV | deiAAAPSCADANKBG0001-253
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 过负荷保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NKBG | POWEquipment | DI1/SOE | 254 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | DEIV | deiAAAPSCADANKBG0001-254
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 零序过流保护跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NKBG | POWEquipment | DI1/SOE | 255 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | DEIV | deiAAAPSCADANKBG0001-255
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 跳闸回路异常报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_NKBG | POWEquipment | DI1/SOE | 256 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | DEIV | deiAAAPSCADANKBG0001-256
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 气体压力过低报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_NKBG | POWEquipment | DI1/SOE | 257 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | DEIV | deiAAAPSCADANKBG0001-257
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 能馈系统故障跳闸 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NKBG | POWEquipment | DI1/SOE | 258 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | DEIV | deiAAAPSCADANKBG0001-258
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 能馈系统合闸允许 |  | DI1/SOE |  | 无意义 |  |  |  | 允许 | 2 | [98 empty] | PSCADA_NKBG | POWEquipment | DI1/SOE | 259 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | DEIV | deiAAAPSCADANKBG0001-259
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 断路器操作方式 |  | DI1/SOE |  | 就地 |  |  |  | 远方 | [99 empty] | PSCADA_NKBG | POWEquipment | DI1/SOE | 260 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | DEIV | deiAAAPSCADANKBG0001-260
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 弹簧未储能 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_NKBG | POWEquipment | DI1/SOE | 261 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | DEIV | deiAAAPSCADANKBG0001-261
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 事故总信号 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NKBG | POWEquipment | DI1/SOE | 262 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | DEIV | deiAAAPSCADANKBG0001-262
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 合闸条件具备 |  | DI1/SOE |  | 消失 |  |  |  | 发出 | 2 | [98 empty] | PSCADA_NKBG | POWEquipment | DI1/SOE | 263 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | DEIV | deiAAAPSCADANKBG0001-263
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | MCB跳闸报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_NKBG | POWEquipment | DI1/SOE | 264 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | DEIV | deiAAAPSCADANKBG0001-264
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 装置通讯状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_NKBG | POWEquipment | DI1/SOE | 265 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | DEIV | deiAAAPSCADANKBG0001-265
|  |  |  | AAA |  | PSCADA | 35kV | NKBG | 35kV能馈变柜 断路器 |  | 断路器分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_NKBG | POWEquipment | DO2 | 266 | :R:A:AAA:PSCADA:NKBG0001 | <alias>AAAPSCADANKBG0001 | [6 empty] | DEOV | deoAAAPSCADANKBG0001-266
|  |  |  | AAA |  | PSCADA | 35kV | ZNBJ | 馈线智能表计 |  | AB线电压Uab | kV | AI | [105 empty] | PSCADA_ZNBJ | POWEquipment | AI | 267 | :R:A:AAA:PSCADA:ZNBJ0001 | <alias>AAAPSCADAZNBJ0001 | [6 empty] | AEIV | aeiAAAPSCADAZNBJ0001-267
|  |  |  | AAA |  | PSCADA | 35kV | ZNBJ | 馈线智能表计 |  | BC线电压Ubc | kV | AI | [105 empty] | PSCADA_ZNBJ | POWEquipment | AI | 268 | :R:A:AAA:PSCADA:ZNBJ0001 | <alias>AAAPSCADAZNBJ0001 | [6 empty] | AEIV | aeiAAAPSCADAZNBJ0001-268
|  |  |  | AAA |  | PSCADA | 35kV | ZNBJ | 馈线智能表计 |  | CA线电压Uca | kV | AI | [105 empty] | PSCADA_ZNBJ | POWEquipment | AI | 269 | :R:A:AAA:PSCADA:ZNBJ0001 | <alias>AAAPSCADAZNBJ0001 | [6 empty] | AEIV | aeiAAAPSCADAZNBJ0001-269
|  |  |  | AAA |  | PSCADA | 35kV | ZNBJ | 馈线智能表计 |  | A相电流Ia | A | AI | [105 empty] | PSCADA_ZNBJ | POWEquipment | AI | 270 | :R:A:AAA:PSCADA:ZNBJ0001 | <alias>AAAPSCADAZNBJ0001 | [6 empty] | AEIV | aeiAAAPSCADAZNBJ0001-270
|  |  |  | AAA |  | PSCADA | 35kV | ZNBJ | 馈线智能表计 |  | B相电流Ib | A | AI | [105 empty] | PSCADA_ZNBJ | POWEquipment | AI | 271 | :R:A:AAA:PSCADA:ZNBJ0001 | <alias>AAAPSCADAZNBJ0001 | [6 empty] | AEIV | aeiAAAPSCADAZNBJ0001-271
|  |  |  | AAA |  | PSCADA | 35kV | ZNBJ | 馈线智能表计 |  | C相电流Ic | A | AI | [105 empty] | PSCADA_ZNBJ | POWEquipment | AI | 272 | :R:A:AAA:PSCADA:ZNBJ0001 | <alias>AAAPSCADAZNBJ0001 | [6 empty] | AEIV | aeiAAAPSCADAZNBJ0001-272
|  |  |  | AAA |  | PSCADA | 35kV | ZNBJ | 馈线智能表计 |  | 有功功率 | kW | AI | [105 empty] | PSCADA_ZNBJ | POWEquipment | AI | 273 | :R:A:AAA:PSCADA:ZNBJ0001 | <alias>AAAPSCADAZNBJ0001 | [6 empty] | AEIV | aeiAAAPSCADAZNBJ0001-273
|  |  |  | AAA |  | PSCADA | 35kV | ZNBJ | 馈线智能表计 |  | 无功功率 | kVA | AI | [105 empty] | PSCADA_ZNBJ | POWEquipment | AI | 274 | :R:A:AAA:PSCADA:ZNBJ0001 | <alias>AAAPSCADAZNBJ0001 | [6 empty] | AEIV | aeiAAAPSCADAZNBJ0001-274
|  |  |  | AAA |  | PSCADA | 35kV | ZNBJ | 馈线智能表计 |  | 正向有功电度 | kWh | AI | [105 empty] | PSCADA_ZNBJ | POWEquipment | AI | 275 | :R:A:AAA:PSCADA:ZNBJ0001 | <alias>AAAPSCADAZNBJ0001 | [6 empty] | AEIV | aeiAAAPSCADAZNBJ0001-275
|  |  |  | AAA |  | PSCADA | 35kV | ZNBJ | 馈线智能表计 |  | 正向无功电度 | kVarh | AI | [105 empty] | PSCADA_ZNBJ | POWEquipment | AI | 276 | :R:A:AAA:PSCADA:ZNBJ0001 | <alias>AAAPSCADAZNBJ0001 | [6 empty] | AEIV | aeiAAAPSCADAZNBJ0001-276
|  |  |  | AAA |  | PSCADA | 35kV | ZNBJ | 馈线智能表计 |  | 反向有功电度 | kWh | AI | [105 empty] | PSCADA_ZNBJ | POWEquipment | AI | 277 | :R:A:AAA:PSCADA:ZNBJ0001 | <alias>AAAPSCADAZNBJ0001 | [6 empty] | AEIV | aeiAAAPSCADAZNBJ0001-277
|  |  |  | AAA |  | PSCADA | 35kV | ZNBJ | 馈线智能表计 |  | 反向无功电度 | kVarh | AI | [105 empty] | PSCADA_ZNBJ | POWEquipment | AI | 278 | :R:A:AAA:PSCADA:ZNBJ0001 | <alias>AAAPSCADAZNBJ0001 | [6 empty] | AEIV | aeiAAAPSCADAZNBJ0001-278
|  |  |  | AAA |  | PSCADA | 35kV | ZNBJ | 馈线智能表计 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_ZNBJ | POWEquipment | DI1/SOE | 279 | :R:A:AAA:PSCADA:ZNBJ0001 | <alias>AAAPSCADAZNBJ0001 | [6 empty] | DEIV | deiAAAPSCADAZNBJ0001-279
|  |  |  | AAA |  | PSCADA | 1500V | DCSC | DC1500V手车 |  | 手车工作位置 |  | DI1 |  | 无意义 |  |  |  | 工作位 | 3 | [98 empty] | PSCADA_DCSC | POWEquipment | DI1 | 280 | :R:A:AAA:PSCADA:DCSC0001 | <alias>AAAPSCADADCSC0001 | [6 empty] | DEIV | deiAAAPSCADADCSC0001-280
|  |  |  | AAA |  | PSCADA | 1500V | DCSC | DC1500V手车 |  | 手车试验位置 |  | DI1 |  | 无意义 |  |  |  | 实验位 | 3 | [98 empty] | PSCADA_DCSC | POWEquipment | DI1 | 281 | :R:A:AAA:PSCADA:DCSC0001 | <alias>AAAPSCADADCSC0001 | [6 empty] | DEIV | deiAAAPSCADADCSC0001-281
|  |  |  | AAA |  | PSCADA | 1500V | DJXG | 1500V直流进线柜 断路器 |  | 进线电流 | A | AI | [105 empty] | PSCADA_DJXG | POWEquipment | AI | 282 | :R:A:AAA:PSCADA:DJXG0001 | <alias>AAAPSCADADJXG0001 | [6 empty] | AEIV | aeiAAAPSCADADJXG0001-282
|  |  |  | AAA |  | PSCADA | 1500V | DJXG | 1500V直流进线柜 断路器 |  | 母线电压 | V | AI | [105 empty] | PSCADA_DJXG | POWEquipment | AI | 283 | :R:A:AAA:PSCADA:DJXG0001 | <alias>AAAPSCADADJXG0001 | [6 empty] | AEIV | aeiAAAPSCADADJXG0001-283
|  |  |  | AAA |  | PSCADA | 1500V | DJXG | 1500V直流进线柜 断路器 |  | 断路器合位 |  | DI1/SOE |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_DJXG | POWEquipment | DI1/SOE | 284 | :R:A:AAA:PSCADA:DJXG0001 | <alias>AAAPSCADADJXG0001 | [6 empty] | DEIV | deiAAAPSCADADJXG0001-284
|  |  |  | AAA |  | PSCADA | 1500V | DJXG | 1500V直流进线柜 断路器 |  | 断路器分位 |  | DI1/SOE |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_DJXG | POWEquipment | DI1/SOE | 285 | :R:A:AAA:PSCADA:DJXG0001 | <alias>AAAPSCADADJXG0001 | [6 empty] | DEIV | deiAAAPSCADADJXG0001-285
|  |  |  | AAA |  | PSCADA | 1500V | DJXG | 1500V直流进线柜 断路器 |  | 远方位置 |  | DI1 |  | 无意义 |  |  |  | 远方 | [99 empty] | PSCADA_DJXG | POWEquipment | DI1 | 286 | :R:A:AAA:PSCADA:DJXG0001 | <alias>AAAPSCADADJXG0001 | [6 empty] | DEIV | deiAAAPSCADADJXG0001-286
|  |  |  | AAA |  | PSCADA | 1500V | DJXG | 1500V直流进线柜 断路器 |  | 就地位置 |  | DI1 |  | 无意义 |  |  |  | 就地 | [99 empty] | PSCADA_DJXG | POWEquipment | DI1 | 287 | :R:A:AAA:PSCADA:DJXG0001 | <alias>AAAPSCADADJXG0001 | [6 empty] | DEIV | deiAAAPSCADADJXG0001-287
|  |  |  | AAA |  | PSCADA | 1500V | DJXG | 1500V直流进线柜 断路器 |  | 大电流脱扣动作 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DJXG | POWEquipment | DI1/SOE | 288 | :R:A:AAA:PSCADA:DJXG0001 | <alias>AAAPSCADADJXG0001 | [6 empty] | DEIV | deiAAAPSCADADJXG0001-288
|  |  |  | AAA |  | PSCADA | 1500V | DJXG | 1500V直流进线柜 断路器 |  | 逆流保护动作 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DJXG | POWEquipment | DI1/SOE | 289 | :R:A:AAA:PSCADA:DJXG0001 | <alias>AAAPSCADADJXG0001 | [6 empty] | DEIV | deiAAAPSCADADJXG0001-289
|  |  |  | AAA |  | PSCADA | 1500V | DJXG | 1500V直流进线柜 断路器 |  | 断路器位置错误 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DJXG | POWEquipment | DI1 | 290 | :R:A:AAA:PSCADA:DJXG0001 | <alias>AAAPSCADADJXG0001 | [6 empty] | DEIV | deiAAAPSCADADJXG0001-290
|  |  |  | AAA |  | PSCADA | 1500V | DJXG | 1500V直流进线柜 断路器 |  | 中压柜联跳断路器 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DJXG | POWEquipment | DI1 | 291 | :R:A:AAA:PSCADA:DJXG0001 | <alias>AAAPSCADADJXG0001 | [6 empty] | DEIV | deiAAAPSCADADJXG0001-291
|  |  |  | AAA |  | PSCADA | 1500V | DJXG | 1500V直流进线柜 断路器 |  | MCB跳闸信号 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DJXG | POWEquipment | DI1 | 292 | :R:A:AAA:PSCADA:DJXG0001 | <alias>AAAPSCADADJXG0001 | [6 empty] | DEIV | deiAAAPSCADADJXG0001-292
|  |  |  | AAA |  | PSCADA | 1500V | DJXG | 1500V直流进线柜 断路器 |  | 机械紧急分闸 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DJXG | POWEquipment | DI1 | 293 | :R:A:AAA:PSCADA:DJXG0001 | <alias>AAAPSCADADJXG0001 | [6 empty] | DEIV | deiAAAPSCADADJXG0001-293
|  |  |  | AAA |  | PSCADA | 1500V | DJXG | 1500V直流进线柜 断路器 |  | 断路器失灵 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DJXG | POWEquipment | DI1 | 294 | :R:A:AAA:PSCADA:DJXG0001 | <alias>AAAPSCADADJXG0001 | [6 empty] | DEIV | deiAAAPSCADADJXG0001-294
|  |  |  | AAA |  | PSCADA | 1500V | DJXG | 1500V直流进线柜 断路器 |  | 后门打开报警 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DJXG | POWEquipment | DI1 | 295 | :R:A:AAA:PSCADA:DJXG0001 | <alias>AAAPSCADADJXG0001 | [6 empty] | DEIV | deiAAAPSCADADJXG0001-295
|  |  |  | AAA |  | PSCADA | 1500V | DJXG | 1500V直流进线柜 断路器 |  | 装置故障报警 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DJXG | POWEquipment | DI1 | 296 | :R:A:AAA:PSCADA:DJXG0001 | <alias>AAAPSCADADJXG0001 | [6 empty] | DEIV | deiAAAPSCADADJXG0001-296
|  |  |  | AAA |  | PSCADA | 1500V | DJXG | 1500V直流进线柜 断路器 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_DJXG | POWEquipment | DI1/SOE | 297 | :R:A:AAA:PSCADA:DJXG0001 | <alias>AAAPSCADADJXG0001 | [6 empty] | DEIV | deiAAAPSCADADJXG0001-297
|  |  |  | AAA |  | PSCADA | 35kV | DJXG | 1500V直流进线柜 断路器 |  | 断路器分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_DJXG | POWEquipment | DO2 | 298 | :R:A:AAA:PSCADA:DJXG0001 | <alias>AAAPSCADADJXG0001 | [6 empty] | DEOV | deoAAAPSCADADJXG0001-298
|  |  |  | AAA |  | PSCADA | 1500V | DCFG | 直流进线柜复归 |  | 逆流保护复归 |  | DO2 | [9 empty] | 复归 | [95 empty] | PSCADA_DCFG | POWEquipment | DO2 | 299 | :R:A:AAA:PSCADA:DCFG0001 | <alias>AAAPSCADADCFG0001 | [6 empty] | DEOV | deoAAAPSCADADCFG0001-299
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 馈线电流 | A | AI | [105 empty] | PSCADA_DKXG | POWEquipment | AI | 300 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | AEIV | aeiAAAPSCADADKXG0001-300
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 馈线电压 | V | AI | [105 empty] | PSCADA_DKXG | POWEquipment | AI | 301 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | AEIV | aeiAAAPSCADADKXG0001-301
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 断路器合位 |  | DI1/SOE |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_DKXG | POWEquipment | DI1/SOE | 302 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-302
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 断路器分位 |  | DI1/SOE |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_DKXG | POWEquipment | DI1/SOE | 303 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-303
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 远方位置 |  | DI1 |  | 无意义 |  |  |  | 远方 | [99 empty] | PSCADA_DKXG | POWEquipment | DI1 | 304 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-304
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 就地位置 |  | DI1 |  | 无意义 |  |  |  | 就地 | [99 empty] | PSCADA_DKXG | POWEquipment | DI1 | 305 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-305
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 馈线有压 |  | DI1 |  | 无意义 |  |  |  | 有压 | 2 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1 | 306 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-306
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 馈线无压 |  | DI1 |  | 无意义 |  |  |  | 无压 | 2 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1 | 307 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-307
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 电流测量回路故障 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1 | 308 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-308
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 断路器位置错误 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1 | 309 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-309
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 速断保护（IOP）动作 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1/SOE | 310 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-310
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 过流保护（OCP）动作 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1/SOE | 311 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-311
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 热过负荷保护（TIP）动作 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1/SOE | 312 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-312
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | di/dt+△I保护（ROR）近端动作 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1/SOE | 313 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-313
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | di/dt+△I保护（ROR）远端动作 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1/SOE | 314 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-314
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 邻站非框架保护联跳断路器 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1 | 315 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-315
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 邻站框架保护联跳断路器 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1 | 316 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-316
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 断路器失灵 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1 | 317 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-317
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 机械紧急分闸 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1 | 318 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-318
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 大电流脱扣动作 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1 | 319 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-319
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | MCB跳闸信号 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1 | 320 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-320
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 热过负荷保护（TIP）报警 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1 | 321 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-321
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 线路测试闭锁 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1 | 322 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-322
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 线路测试熔丝故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1 | 323 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-323
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 后门打开报警 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1 | 324 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-324
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 装置故障报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1/SOE | 325 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-325
|  |  |  | AAA |  | PSCADA | 1500V | DKXG | 1500V直流馈线柜 断路器 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_DKXG | POWEquipment | DI1/SOE | 326 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEIV | deiAAAPSCADADKXG0001-326
|  |  |  | AAA |  | PSCADA | 35kV | DKXG | 1500V直流馈线柜 断路器 |  | 断路器分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_DKXG | POWEquipment | DO2 | 327 | :R:A:AAA:PSCADA:DKXG0001 | <alias>AAAPSCADADKXG0001 | [6 empty] | DEOV | deoAAAPSCADADKXG0001-327
|  |  |  | AAA |  | PSCADA | 1500V | XLFG | 直流馈线复归 |  | 线路测试闭锁复归 |  | DO2 | [9 empty] | 复归 | [95 empty] | PSCADA_XLFG | POWEquipment | DO2 | 328 | :R:A:AAA:PSCADA:XLFG0001 | <alias>AAAPSCADAXLFG0001 | [6 empty] | DEOV | deoAAAPSCADAXLFG0001-328
|  |  |  | AAA |  | PSCADA | 1500V | DGLK | 负极柜隔离开关 |  | 隔离开关分位 |  | DI1/SOE |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_DGLK | POWEquipment | DI1/SOE | 329 | :R:A:AAA:PSCADA:DGLK0001 | <alias>AAAPSCADADGLK0001 | [6 empty] | DEIV | deiAAAPSCADADGLK0001-329
|  |  |  | AAA |  | PSCADA | 1500V | DGLK | 负极柜隔离开关 |  | 隔离开关合位 |  | DI1/SOE |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_DGLK | POWEquipment | DI1/SOE | 330 | :R:A:AAA:PSCADA:DGLK0001 | <alias>AAAPSCADADGLK0001 | [6 empty] | DEIV | deiAAAPSCADADGLK0001-330
|  |  |  | AAA |  | PSCADA | 1500V | FJNL | 直流柜侧负极柜 |  | 框架泄漏电流 | A | AI | [105 empty] | PSCADA_FJNL | POWEquipment | AI | 331 | :R:A:AAA:PSCADA:FJNL0001 | <alias>AAAPSCADAFJNL0001 | [6 empty] | AEIV | aeiAAAPSCADAFJNL0001-331
|  |  |  | AAA |  | PSCADA | 1500V | FJNL | 直流柜侧负极柜 |  | 框架泄漏电压 | V | AI | [105 empty] | PSCADA_FJNL | POWEquipment | AI | 332 | :R:A:AAA:PSCADA:FJNL0001 | <alias>AAAPSCADAFJNL0001 | [6 empty] | AEIV | aeiAAAPSCADAFJNL0001-332
|  |  |  | AAA |  | PSCADA | 1500V | FJNL | 直流柜侧负极柜 |  | 负极总回流 | A | AI | [105 empty] | PSCADA_FJNL | POWEquipment | AI | 333 | :R:A:AAA:PSCADA:FJNL0001 | <alias>AAAPSCADAFJNL0001 | [6 empty] | AEIV | aeiAAAPSCADAFJNL0001-333
|  |  |  | AAA |  | PSCADA | 1500V | FJNL | 直流柜侧负极柜 |  | 框架泄漏保护电流型动作 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_FJNL | POWEquipment | DI1/SOE | 334 | :R:A:AAA:PSCADA:FJNL0001 | <alias>AAAPSCADAFJNL0001 | [6 empty] | DEIV | deiAAAPSCADAFJNL0001-334
|  |  |  | AAA |  | PSCADA | 1500V | FJNL | 直流柜侧负极柜 |  | 框架泄漏保护电压型动作 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_FJNL | POWEquipment | DI1/SOE | 335 | :R:A:AAA:PSCADA:FJNL0001 | <alias>AAAPSCADAFJNL0001 | [6 empty] | DEIV | deiAAAPSCADAFJNL0001-335
|  |  |  | AAA |  | PSCADA | 1500V | FJNL | 直流柜侧负极柜 |  | 框架泄漏保护电压型报警 |  | DI1 |  | 恢复 |  |  |  | 报警 | 1 | [98 empty] | PSCADA_FJNL | POWEquipment | DI1 | 336 | :R:A:AAA:PSCADA:FJNL0001 | <alias>AAAPSCADAFJNL0001 | [6 empty] | DEIV | deiAAAPSCADAFJNL0001-336
|  |  |  | AAA |  | PSCADA | 1500V | FJNL | 直流柜侧负极柜 |  | MCB跳闸信号 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_FJNL | POWEquipment | DI1 | 337 | :R:A:AAA:PSCADA:FJNL0001 | <alias>AAAPSCADAFJNL0001 | [6 empty] | DEIV | deiAAAPSCADAFJNL0001-337
|  |  |  | AAA |  | PSCADA | 1500V | FJNL | 直流柜侧负极柜 |  | 框架泄漏电压监视回路故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 3 | [98 empty] | PSCADA_FJNL | POWEquipment | DI1 | 338 | :R:A:AAA:PSCADA:FJNL0001 | <alias>AAAPSCADAFJNL0001 | [6 empty] | DEIV | deiAAAPSCADAFJNL0001-338
|  |  |  | AAA |  | PSCADA | 1500V | FJNL | 直流柜侧负极柜 |  | 框架泄漏电流测量回路故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 3 | [98 empty] | PSCADA_FJNL | POWEquipment | DI1 | 339 | :R:A:AAA:PSCADA:FJNL0001 | <alias>AAAPSCADAFJNL0001 | [6 empty] | DEIV | deiAAAPSCADAFJNL0001-339
|  |  |  | AAA |  | PSCADA | 1500V | FJNL | 直流柜侧负极柜 |  | 后门打开报警 |  | DI1 |  | 恢复 |  |  |  | 报警 | 3 | [98 empty] | PSCADA_FJNL | POWEquipment | DI1 | 340 | :R:A:AAA:PSCADA:FJNL0001 | <alias>AAAPSCADAFJNL0001 | [6 empty] | DEIV | deiAAAPSCADAFJNL0001-340
|  |  |  | AAA |  | PSCADA | 1500V | FJNL | 直流柜侧负极柜 |  | 装置故障报警 |  | DI1 |  | 恢复 |  |  |  | 报警 | [99 empty] | PSCADA_FJNL | POWEquipment | DI1 | 341 | :R:A:AAA:PSCADA:FJNL0001 | <alias>AAAPSCADAFJNL0001 | [6 empty] | DEIV | deiAAAPSCADAFJNL0001-341
|  |  |  | AAA |  | PSCADA | 1500V | FJNL | 直流柜侧负极柜 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_FJNL | POWEquipment | DI1/SOE | 342 | :R:A:AAA:PSCADA:FJNL0001 | <alias>AAAPSCADAFJNL0001 | [6 empty] | DEIV | deiAAAPSCADAFJNL0001-342
|  |  |  | AAA |  | PSCADA | 1500V | FJNR | 整流器侧负极柜 |  | 框架泄漏电流 | A | AI | [105 empty] | PSCADA_FJNR | POWEquipment | AI | 343 | :R:A:AAA:PSCADA:FJNR0001 | <alias>AAAPSCADAFJNR0001 | [6 empty] | AEIV | aeiAAAPSCADAFJNR0001-343
|  |  |  | AAA |  | PSCADA | 1500V | FJNR | 整流器侧负极柜 |  | 框架泄漏电压 | V | AI | [105 empty] | PSCADA_FJNR | POWEquipment | AI | 344 | :R:A:AAA:PSCADA:FJNR0001 | <alias>AAAPSCADAFJNR0001 | [6 empty] | AEIV | aeiAAAPSCADAFJNR0001-344
|  |  |  | AAA |  | PSCADA | 1500V | FJNR | 整流器侧负极柜 |  | 框架泄漏保护电流型动作 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_FJNR | POWEquipment | DI1/SOE | 345 | :R:A:AAA:PSCADA:FJNR0001 | <alias>AAAPSCADAFJNR0001 | [6 empty] | DEIV | deiAAAPSCADAFJNR0001-345
|  |  |  | AAA |  | PSCADA | 1500V | FJNR | 整流器侧负极柜 |  | 框架泄漏保护电压型动作 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_FJNR | POWEquipment | DI1/SOE | 346 | :R:A:AAA:PSCADA:FJNR0001 | <alias>AAAPSCADAFJNR0001 | [6 empty] | DEIV | deiAAAPSCADAFJNR0001-346
|  |  |  | AAA |  | PSCADA | 1500V | FJNR | 整流器侧负极柜 |  | 框架泄漏保护电压型报警 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_FJNR | POWEquipment | DI1 | 347 | :R:A:AAA:PSCADA:FJNR0001 | <alias>AAAPSCADAFJNR0001 | [6 empty] | DEIV | deiAAAPSCADAFJNR0001-347
|  |  |  | AAA |  | PSCADA | 1500V | FJNR | 整流器侧负极柜 |  | 框架泄漏电压监视回路故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 3 | [98 empty] | PSCADA_FJNR | POWEquipment | DI1 | 348 | :R:A:AAA:PSCADA:FJNR0001 | <alias>AAAPSCADAFJNR0001 | [6 empty] | DEIV | deiAAAPSCADAFJNR0001-348
|  |  |  | AAA |  | PSCADA | 1500V | FJNR | 整流器侧负极柜 |  | 框架泄漏电流测量回路故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 3 | [98 empty] | PSCADA_FJNR | POWEquipment | DI1 | 349 | :R:A:AAA:PSCADA:FJNR0001 | <alias>AAAPSCADAFJNR0001 | [6 empty] | DEIV | deiAAAPSCADAFJNR0001-349
|  |  |  | AAA |  | PSCADA | 1500V | FJNR | 整流器侧负极柜 |  | 装置故障报警 |  | DI1 |  | 恢复 |  |  |  | 报警 | [99 empty] | PSCADA_FJNR | POWEquipment | DI1 | 350 | :R:A:AAA:PSCADA:FJNR0001 | <alias>AAAPSCADAFJNR0001 | [6 empty] | DEIV | deiAAAPSCADAFJNR0001-350
|  |  |  | AAA |  | PSCADA | 1500V | FJNR | 整流器侧负极柜 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_FJNR | POWEquipment | DI1/SOE | 351 | :R:A:AAA:PSCADA:FJNR0001 | <alias>AAAPSCADAFJNR0001 | [6 empty] | DEIV | deiAAAPSCADAFJNR0001-351
|  |  |  | AAA |  | PSCADA | 1500V | FJFG | 整流器侧负极柜复归 |  | 框架泄漏保护电压型复归 |  | DO2 | [9 empty] | 复归 | [95 empty] | PSCADA_FJFG | POWEquipment | DO2 | 352 | :R:A:AAA:PSCADA:FJFG0001 | <alias>AAAPSCADAFJFG0001 | [6 empty] | DEOV | deoAAAPSCADAFJFG0001-352
|  |  |  | AAA |  | PSCADA | 1500V | DNKG | 1500V能源再生馈线柜 断路器 |  | 馈线电流 | A | AI | [105 empty] | PSCADA_DNKG | POWEquipment | AI | 353 | :R:A:AAA:PSCADA:DNKG0001 | <alias>AAAPSCADADNKG0001 | [6 empty] | AEIV | aeiAAAPSCADADNKG0001-353
|  |  |  | AAA |  | PSCADA | 1500V | DNKG | 1500V能源再生馈线柜 断路器 |  | 断路器合位 |  | DI1/SOE |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_DNKG | POWEquipment | DI1/SOE | 354 | :R:A:AAA:PSCADA:DNKG0001 | <alias>AAAPSCADADNKG0001 | [6 empty] | DEIV | deiAAAPSCADADNKG0001-354
|  |  |  | AAA |  | PSCADA | 1500V | DNKG | 1500V能源再生馈线柜 断路器 |  | 断路器分位 |  | DI1/SOE |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_DNKG | POWEquipment | DI1/SOE | 355 | :R:A:AAA:PSCADA:DNKG0001 | <alias>AAAPSCADADNKG0001 | [6 empty] | DEIV | deiAAAPSCADADNKG0001-355
|  |  |  | AAA |  | PSCADA | 1500V | DNKG | 1500V能源再生馈线柜 断路器 |  | 远方位置 |  | DI1 |  | 无意义 |  |  |  | 远方 | [99 empty] | PSCADA_DNKG | POWEquipment | DI1 | 356 | :R:A:AAA:PSCADA:DNKG0001 | <alias>AAAPSCADADNKG0001 | [6 empty] | DEIV | deiAAAPSCADADNKG0001-356
|  |  |  | AAA |  | PSCADA | 1500V | DNKG | 1500V能源再生馈线柜 断路器 |  | 就地位置 |  | DI1 |  | 无意义 |  |  |  | 就地 | [99 empty] | PSCADA_DNKG | POWEquipment | DI1 | 357 | :R:A:AAA:PSCADA:DNKG0001 | <alias>AAAPSCADADNKG0001 | [6 empty] | DEIV | deiAAAPSCADADNKG0001-357
|  |  |  | AAA |  | PSCADA | 1500V | DNKG | 1500V能源再生馈线柜 断路器 |  | 电流测量回路故障 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DNKG | POWEquipment | DI1 | 358 | :R:A:AAA:PSCADA:DNKG0001 | <alias>AAAPSCADADNKG0001 | [6 empty] | DEIV | deiAAAPSCADADNKG0001-358
|  |  |  | AAA |  | PSCADA | 1500V | DNKG | 1500V能源再生馈线柜 断路器 |  | 断路器位置错误 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DNKG | POWEquipment | DI1 | 359 | :R:A:AAA:PSCADA:DNKG0001 | <alias>AAAPSCADADNKG0001 | [6 empty] | DEIV | deiAAAPSCADADNKG0001-359
|  |  |  | AAA |  | PSCADA | 1500V | DNKG | 1500V能源再生馈线柜 断路器 |  | 速断保护（IOP）动作 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DNKG | POWEquipment | DI1/SOE | 360 | :R:A:AAA:PSCADA:DNKG0001 | <alias>AAAPSCADADNKG0001 | [6 empty] | DEIV | deiAAAPSCADADNKG0001-360
|  |  |  | AAA |  | PSCADA | 1500V | DNKG | 1500V能源再生馈线柜 断路器 |  | 过流保护（OCP）动作 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DNKG | POWEquipment | DI1/SOE | 361 | :R:A:AAA:PSCADA:DNKG0001 | <alias>AAAPSCADADNKG0001 | [6 empty] | DEIV | deiAAAPSCADADNKG0001-361
|  |  |  | AAA |  | PSCADA | 1500V | DNKG | 1500V能源再生馈线柜 断路器 |  | 再生制动能量回馈装置联跳断路器 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DNKG | POWEquipment | DI1 | 362 | :R:A:AAA:PSCADA:DNKG0001 | <alias>AAAPSCADADNKG0001 | [6 empty] | DEIV | deiAAAPSCADADNKG0001-362
|  |  |  | AAA |  | PSCADA | 1500V | DNKG | 1500V能源再生馈线柜 断路器 |  | 断路器失灵 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DNKG | POWEquipment | DI1 | 363 | :R:A:AAA:PSCADA:DNKG0001 | <alias>AAAPSCADADNKG0001 | [6 empty] | DEIV | deiAAAPSCADADNKG0001-363
|  |  |  | AAA |  | PSCADA | 1500V | DNKG | 1500V能源再生馈线柜 断路器 |  | 机械紧急分位 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DNKG | POWEquipment | DI1 | 364 | :R:A:AAA:PSCADA:DNKG0001 | <alias>AAAPSCADADNKG0001 | [6 empty] | DEIV | deiAAAPSCADADNKG0001-364
|  |  |  | AAA |  | PSCADA | 1500V | DNKG | 1500V能源再生馈线柜 断路器 |  | 大电流脱扣动作 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DNKG | POWEquipment | DI1 | 365 | :R:A:AAA:PSCADA:DNKG0001 | <alias>AAAPSCADADNKG0001 | [6 empty] | DEIV | deiAAAPSCADADNKG0001-365
|  |  |  | AAA |  | PSCADA | 1500V | DNKG | 1500V能源再生馈线柜 断路器 |  | MCB跳闸信号 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DNKG | POWEquipment | DI1 | 366 | :R:A:AAA:PSCADA:DNKG0001 | <alias>AAAPSCADADNKG0001 | [6 empty] | DEIV | deiAAAPSCADADNKG0001-366
|  |  |  | AAA |  | PSCADA | 1500V | DNKG | 1500V能源再生馈线柜 断路器 |  | 后门打开报警 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DNKG | POWEquipment | DI1 | 367 | :R:A:AAA:PSCADA:DNKG0001 | <alias>AAAPSCADADNKG0001 | [6 empty] | DEIV | deiAAAPSCADADNKG0001-367
|  |  |  | AAA |  | PSCADA | 1500V | DNKG | 1500V能源再生馈线柜 断路器 |  | 装置故障报警 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DNKG | POWEquipment | DI1 | 368 | :R:A:AAA:PSCADA:DNKG0001 | <alias>AAAPSCADADNKG0001 | [6 empty] | DEIV | deiAAAPSCADADNKG0001-368
|  |  |  | AAA |  | PSCADA | 1500V | DNKG | 1500V能源再生馈线柜 断路器 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_DNKG | POWEquipment | DI1/SOE | 369 | :R:A:AAA:PSCADA:DNKG0001 | <alias>AAAPSCADADNKG0001 | [6 empty] | DEIV | deiAAAPSCADADNKG0001-369
|  |  |  | AAA |  | PSCADA | 1500V | DNKG | 1500V能源再生馈线柜 断路器 |  | 断路器分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_DNKG | POWEquipment | DO2 | 370 | :R:A:AAA:PSCADA:DNKG0001 | <alias>AAAPSCADADNKG0001 | [6 empty] | DEOV | deoAAAPSCADADNKG0001-370
|  |  |  | AAA |  | PSCADA | 1500V | DWDG | 1500V电动隔离开关 |  | 电机失电 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DWDG | POWEquipment | DI1 | 371 | :R:A:AAA:PSCADA:DWDG0001 | <alias>AAAPSCADADWDG0001 | [6 empty] | DEIV | deiAAAPSCADADWDG0001-371
|  |  |  | AAA |  | PSCADA | 1500V | DWDG | 1500V电动隔离开关 |  | 控制回路故障 |  | DI1 |  | 复归 |  |  |  | 动作 | 2 | [98 empty] | PSCADA_DWDG | POWEquipment | DI1 | 372 | :R:A:AAA:PSCADA:DWDG0001 | <alias>AAAPSCADADWDG0001 | [6 empty] | DEIV | deiAAAPSCADADWDG0001-372
|  |  |  | AAA |  | PSCADA | 1500V | DWDG | 1500V电动隔离开关 |  | 隔开操作方式 |  | DI1 |  | 就地 |  |  |  | 远方 | [99 empty] | PSCADA_DWDG | POWEquipment | DI1 | 373 | :R:A:AAA:PSCADA:DWDG0001 | <alias>AAAPSCADADWDG0001 | [6 empty] | DEIV | deiAAAPSCADADWDG0001-373
|  |  |  | AAA |  | PSCADA | 1500V | DWDG | 1500V电动隔离开关 |  | 隔开分位 |  | DI1 |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_DWDG | POWEquipment | DI1 | 374 | :R:A:AAA:PSCADA:DWDG0001 | <alias>AAAPSCADADWDG0001 | [6 empty] | DEIV | deiAAAPSCADADWDG0001-374
|  |  |  | AAA |  | PSCADA | 1500V | DWDG | 1500V电动隔离开关 |  | 隔开合位 |  | DI1 |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_DWDG | POWEquipment | DI1 | 375 | :R:A:AAA:PSCADA:DWDG0001 | <alias>AAAPSCADADWDG0001 | [6 empty] | DEIV | deiAAAPSCADADWDG0001-375
|  |  |  | AAA |  | PSCADA | 1500V | DWDG | 1500V电动隔离开关 |  | 隔开分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_DWDG | POWEquipment | DO2 | 376 | :R:A:AAA:PSCADA:DWDG0001 | <alias>AAAPSCADADWDG0001 | [6 empty] | DEOV | deoAAAPSCADADWDG0001-376
|  |  |  | AAA |  | PSCADA | 1500V | CZGK | 1500V隔开控制柜 |  | MCB跳闸信号 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CZGK | POWEquipment | DI1 | 377 | :R:A:AAA:PSCADA:CZGK0001 | <alias>AAAPSCADACZGK0001 | [6 empty] | DEIV | deiAAAPSCADACZGK0001-377
|  |  |  | AAA |  | PSCADA | 1500V | CZGK | 1500V隔开控制柜 |  | DC24V系统正常 |  | DI1 |  | 故障 |  |  |  | 正常 | 2 | [98 empty] | PSCADA_CZGK | POWEquipment | DI1 | 378 | :R:A:AAA:PSCADA:CZGK0001 | <alias>AAAPSCADACZGK0001 | [6 empty] | DEIV | deiAAAPSCADACZGK0001-378
|  |  |  | AAA |  | PSCADA | 1500V | CZGK | 1500V隔开控制柜 |  | 装置故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CZGK | POWEquipment | DI1 | 379 | :R:A:AAA:PSCADA:CZGK0001 | <alias>AAAPSCADACZGK0001 | [6 empty] | DEIV | deiAAAPSCADACZGK0001-379
|  |  |  | AAA |  | PSCADA | 1500V | CZGK | 1500V隔开控制柜 |  | 直流柜DC24V接地故障 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CZGK | POWEquipment | DI1 | 380 | :R:A:AAA:PSCADA:CZGK0001 | <alias>AAAPSCADACZGK0001 | [6 empty] | DEIV | deiAAAPSCADACZGK0001-380
|  |  |  | AAA |  | PSCADA | 1500V | CZGK | 1500V隔开控制柜 |  | 下行隔离开关远方位置 |  | DI1 |  | 无意义 |  |  |  | 远方 | 2 | [98 empty] | PSCADA_CZGK | POWEquipment | DI1 | 381 | :R:A:AAA:PSCADA:CZGK0001 | <alias>AAAPSCADACZGK0001 | [6 empty] | DEIV | deiAAAPSCADACZGK0001-381
|  |  |  | AAA |  | PSCADA | 1500V | CZGK | 1500V隔开控制柜 |  | 下行隔离开关就地位置 |  | DI1 |  | 无意义 |  |  |  | 就地 | 3 | [98 empty] | PSCADA_CZGK | POWEquipment | DI1 | 382 | :R:A:AAA:PSCADA:CZGK0001 | <alias>AAAPSCADACZGK0001 | [6 empty] | DEIV | deiAAAPSCADACZGK0001-382
|  |  |  | AAA |  | PSCADA | 1500V | CZGK | 1500V隔开控制柜 |  | 上行隔离开关远方位置 |  | DI1 |  | 无意义 |  |  |  | 远方 | 3 | [98 empty] | PSCADA_CZGK | POWEquipment | DI1 | 383 | :R:A:AAA:PSCADA:CZGK0001 | <alias>AAAPSCADACZGK0001 | [6 empty] | DEIV | deiAAAPSCADACZGK0001-383
|  |  |  | AAA |  | PSCADA | 1500V | CZGK | 1500V隔开控制柜 |  | 上行隔离开关就地位置 |  | DI1 |  | 无意义 |  |  |  | 就地 | 3 | [98 empty] | PSCADA_CZGK | POWEquipment | DI1 | 384 | :R:A:AAA:PSCADA:CZGK0001 | <alias>AAAPSCADACZGK0001 | [6 empty] | DEIV | deiAAAPSCADACZGK0001-384
|  |  |  | AAA |  | PSCADA | 1500V | CZGK | 1500V隔开控制柜 |  | 馈线211联跳投入 |  | DI1 |  | 退出 |  |  |  | 投入 | 3 | [98 empty] | PSCADA_CZGK | POWEquipment | DI1 | 385 | :R:A:AAA:PSCADA:CZGK0001 | <alias>AAAPSCADACZGK0001 | [6 empty] | DEIV | deiAAAPSCADACZGK0001-385
|  |  |  | AAA |  | PSCADA | 1500V | CZGK | 1500V隔开控制柜 |  | 馈线212联跳投入 |  | DI1 |  | 退出 |  |  |  | 投入 | 3 | [98 empty] | PSCADA_CZGK | POWEquipment | DI1 | 386 | :R:A:AAA:PSCADA:CZGK0001 | <alias>AAAPSCADACZGK0001 | [6 empty] | DEIV | deiAAAPSCADACZGK0001-386
|  |  |  | AAA |  | PSCADA | 1500V | CZGK | 1500V隔开控制柜 |  | 馈线213联跳投入 |  | DI1 |  | 退出 |  |  |  | 投入 | 3 | [98 empty] | PSCADA_CZGK | POWEquipment | DI1 | 387 | :R:A:AAA:PSCADA:CZGK0001 | <alias>AAAPSCADACZGK0001 | [6 empty] | DEIV | deiAAAPSCADACZGK0001-387
|  |  |  | AAA |  | PSCADA | 1500V | CZGK | 1500V隔开控制柜 |  | 馈线214联跳投入 |  | DI1 |  | 退出 |  |  |  | 投入 | 3 | [98 empty] | PSCADA_CZGK | POWEquipment | DI1 | 388 | :R:A:AAA:PSCADA:CZGK0001 | <alias>AAAPSCADACZGK0001 | [6 empty] | DEIV | deiAAAPSCADACZGK0001-388
|  |  |  | AAA |  | PSCADA | 1500V | CZGK | 1500V隔开控制柜 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_CZGK | POWEquipment | DI1/SOE | 389 | :R:A:AAA:PSCADA:CZGK0001 | <alias>AAAPSCADACZGK0001 | [6 empty] | DEIV | deiAAAPSCADACZGK0001-389
|  |  |  | AAA |  | PSCADA | 1500V | SNGK | 1500V隔开控制柜 |  | MCB跳闸信号 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_SNGK | POWEquipment | DI1 | 390 | :R:A:AAA:PSCADA:SNGK0001 | <alias>AAAPSCADASNGK0001 | [6 empty] | DEIV | deiAAAPSCADASNGK0001-390
|  |  |  | AAA |  | PSCADA | 1500V | SNGK | 1500V隔开控制柜 |  | DC24V系统正常 |  | DI1 |  | 故障 |  |  |  | 正常 | 2 | [98 empty] | PSCADA_SNGK | POWEquipment | DI1 | 391 | :R:A:AAA:PSCADA:SNGK0001 | <alias>AAAPSCADASNGK0001 | [6 empty] | DEIV | deiAAAPSCADASNGK0001-391
|  |  |  | AAA |  | PSCADA | 1500V | SNGK | 1500V隔开控制柜 |  | 装置故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_SNGK | POWEquipment | DI1 | 392 | :R:A:AAA:PSCADA:SNGK0001 | <alias>AAAPSCADASNGK0001 | [6 empty] | DEIV | deiAAAPSCADASNGK0001-392
|  |  |  | AAA |  | PSCADA | 1500V | SNGK | 1500V隔开控制柜 |  | 直流柜DC24V接地故障 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_SNGK | POWEquipment | DI1 | 393 | :R:A:AAA:PSCADA:SNGK0001 | <alias>AAAPSCADASNGK0001 | [6 empty] | DEIV | deiAAAPSCADASNGK0001-393
|  |  |  | AAA |  | PSCADA | 1500V | SNGK | 1500V隔开控制柜 |  | 远方位置 |  | DI1 |  | 无意义 |  |  |  | 远方 | 2 | [98 empty] | PSCADA_SNGK | POWEquipment | DI1 | 394 | :R:A:AAA:PSCADA:SNGK0001 | <alias>AAAPSCADASNGK0001 | [6 empty] | DEIV | deiAAAPSCADASNGK0001-394
|  |  |  | AAA |  | PSCADA | 1500V | SNGK | 1500V隔开控制柜 |  | 就地位置 |  | DI1 |  | 无意义 |  |  |  | 就地 | 3 | [98 empty] | PSCADA_SNGK | POWEquipment | DI1 | 395 | :R:A:AAA:PSCADA:SNGK0001 | <alias>AAAPSCADASNGK0001 | [6 empty] | DEIV | deiAAAPSCADASNGK0001-395
|  |  |  | AAA |  | PSCADA | 1500V | SNGK | 1500V隔开控制柜 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_SNGK | POWEquipment | DI1/SOE | 396 | :R:A:AAA:PSCADA:SNGK0001 | <alias>AAAPSCADASNGK0001 | [6 empty] | DEIV | deiAAAPSCADASNGK0001-396
|  |  |  | AAA |  | PSCADA | 1500V | WDWG | 轨电位柜 |  | 轨电位电压 | V | AI | [105 empty] | PSCADA_WDWG | POWEquipment | AI | 397 | :R:A:AAA:PSCADA:WDWG0001 | <alias>AAAPSCADAWDWG0001 | [6 empty] | AEIV | aeiAAAPSCADAWDWG0001-397
|  |  |  | AAA |  | PSCADA | 1500V | WDWG | 轨电位柜 |  | 轨电位电流 | A | AI | [105 empty] | PSCADA_WDWG | POWEquipment | AI | 398 | :R:A:AAA:PSCADA:WDWG0001 | <alias>AAAPSCADAWDWG0001 | [6 empty] | AEIV | aeiAAAPSCADAWDWG0001-398
|  |  |  | AAA |  | PSCADA | 1500V | WDWG | 轨电位柜 |  | 接触器分位 |  | DI1 |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_WDWG | POWEquipment | DI1 | 399 | :R:A:AAA:PSCADA:WDWG0001 | <alias>AAAPSCADAWDWG0001 | [6 empty] | DEIV | deiAAAPSCADAWDWG0001-399
|  |  |  | AAA |  | PSCADA | 1500V | WDWG | 轨电位柜 |  | 接触器合位 |  | DI1 |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_WDWG | POWEquipment | DI1 | 400 | :R:A:AAA:PSCADA:WDWG0001 | <alias>AAAPSCADAWDWG0001 | [6 empty] | DEIV | deiAAAPSCADAWDWG0001-400
|  |  |  | AAA |  | PSCADA | 1500V | WDWG | 轨电位柜 |  | 接触器开合次数超限 |  | DI1/SOE |  | 复归 |  |  |  | 动作 | 3 | [98 empty] | PSCADA_WDWG | POWEquipment | DI1/SOE | 401 | :R:A:AAA:PSCADA:WDWG0001 | <alias>AAAPSCADAWDWG0001 | [6 empty] | DEIV | deiAAAPSCADAWDWG0001-401
|  |  |  | AAA |  | PSCADA | 1500V | WDWG | 轨电位柜 |  | 接触器回路异常 |  | DI1 |  | 恢复 |  |  |  | 报警 | 3 | [98 empty] | PSCADA_WDWG | POWEquipment | DI1 | 402 | :R:A:AAA:PSCADA:WDWG0001 | <alias>AAAPSCADAWDWG0001 | [6 empty] | DEIV | deiAAAPSCADAWDWG0001-402
|  |  |  | AAA |  | PSCADA | 1500V | WDWG | 轨电位柜 |  | 轨电位闭锁 |  | DI1 |  | 恢复 |  |  |  | 报警 | 3 | [98 empty] | PSCADA_WDWG | POWEquipment | DI1 | 403 | :R:A:AAA:PSCADA:WDWG0001 | <alias>AAAPSCADAWDWG0001 | [6 empty] | DEIV | deiAAAPSCADAWDWG0001-403
|  |  |  | AAA |  | PSCADA | 1500V | WDWG | 轨电位柜 |  | 晶闸管故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 3 | [98 empty] | PSCADA_WDWG | POWEquipment | DI1 | 404 | :R:A:AAA:PSCADA:WDWG0001 | <alias>AAAPSCADAWDWG0001 | [6 empty] | DEIV | deiAAAPSCADAWDWG0001-404
|  |  |  | AAA |  | PSCADA | 1500V | WDWG | 轨电位柜 |  | I>>>动作 |  | DI1 |  | 恢复 |  |  |  | 报警 | 3 | [98 empty] | PSCADA_WDWG | POWEquipment | DI1 | 405 | :R:A:AAA:PSCADA:WDWG0001 | <alias>AAAPSCADAWDWG0001 | [6 empty] | DEIV | deiAAAPSCADAWDWG0001-405
|  |  |  | AAA |  | PSCADA | 1500V | WDWG | 轨电位柜 |  | 远程闭锁合闸 |  | DI1 |  | 恢复 |  |  |  | 报警 | 3 | [98 empty] | PSCADA_WDWG | POWEquipment | DI1 | 406 | :R:A:AAA:PSCADA:WDWG0001 | <alias>AAAPSCADAWDWG0001 | [6 empty] | DEIV | deiAAAPSCADAWDWG0001-406
|  |  |  | AAA |  | PSCADA | 1500V | WDWG | 轨电位柜 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_WDWG | POWEquipment | DI1/SOE | 407 | :R:A:AAA:PSCADA:WDWG0001 | <alias>AAAPSCADAWDWG0001 | [6 empty] | DEIV | deiAAAPSCADAWDWG0001-407
|  |  |  | AAA |  | PSCADA | 1500V | WDWG | 轨电位柜 |  | 远程闭锁合闸指令 |  | DO2 | [9 empty] | 闭锁 | [95 empty] | PSCADA_WDWG | POWEquipment | DO2 | 408 | :R:A:AAA:PSCADA:WDWG0001 | <alias>AAAPSCADAWDWG0001 | [6 empty] | DEOV | deoAAAPSCADAWDWG0001-408
|  |  |  | AAA |  | PSCADA | 1500V | GDFG | 轨电位复归 |  | 轨电位复归 |  | DO2 | [9 empty] | 复归 | [95 empty] | PSCADA_GDFG | POWEquipment | DO2 | 409 | :R:A:AAA:PSCADA:GDFG0001 | <alias>AAAPSCADAGDFG0001 | [6 empty] | DEOV | deoAAAPSCADAGDFG0001-409
|  |  |  | AAA |  | PSCADA | 温控器 | BWKQ | 变压器温控器 |  | A相绕组温度 | ℃ | AI | [105 empty] | PSCADA_BWKQ | POWEquipment | AI | 410 | :R:A:AAA:PSCADA:BWKQ0001 | <alias>AAAPSCADABWKQ0001 | [6 empty] | AEIV | aeiAAAPSCADABWKQ0001-410
|  |  |  | AAA |  | PSCADA | 温控器 | BWKQ | 变压器温控器 |  | B相绕组温度 | ℃ | AI | [105 empty] | PSCADA_BWKQ | POWEquipment | AI | 411 | :R:A:AAA:PSCADA:BWKQ0001 | <alias>AAAPSCADABWKQ0001 | [6 empty] | AEIV | aeiAAAPSCADABWKQ0001-411
|  |  |  | AAA |  | PSCADA | 温控器 | BWKQ | 变压器温控器 |  | C相绕组温度 | ℃ | AI | [105 empty] | PSCADA_BWKQ | POWEquipment | AI | 412 | :R:A:AAA:PSCADA:BWKQ0001 | <alias>AAAPSCADABWKQ0001 | [6 empty] | AEIV | aeiAAAPSCADABWKQ0001-412
|  |  |  | AAA |  | PSCADA | 温控器 | BWKQ | 变压器温控器 |  | 铁芯温度 | ℃ | AI | [105 empty] | PSCADA_BWKQ | POWEquipment | AI | 413 | :R:A:AAA:PSCADA:BWKQ0001 | <alias>AAAPSCADABWKQ0001 | [6 empty] | AEIV | aeiAAAPSCADABWKQ0001-413
|  |  |  | AAA |  | PSCADA | 温控器 | BWKQ | 变压器温控器 |  | 绕组超温报警 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_BWKQ | POWEquipment | DI1 | 414 | :R:A:AAA:PSCADA:BWKQ0001 | <alias>AAAPSCADABWKQ0001 | [6 empty] | DEIV | deiAAAPSCADABWKQ0001-414
|  |  |  | AAA |  | PSCADA | 温控器 | BWKQ | 变压器温控器 |  | 绕组超温跳闸 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKQ | POWEquipment | DI1 | 415 | :R:A:AAA:PSCADA:BWKQ0001 | <alias>AAAPSCADABWKQ0001 | [6 empty] | DEIV | deiAAAPSCADABWKQ0001-415
|  |  |  | AAA |  | PSCADA | 温控器 | BWKQ | 变压器温控器 |  | 铁芯超温报警 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_BWKQ | POWEquipment | DI1 | 416 | :R:A:AAA:PSCADA:BWKQ0001 | <alias>AAAPSCADABWKQ0001 | [6 empty] | DEIV | deiAAAPSCADABWKQ0001-416
|  |  |  | AAA |  | PSCADA | 温控器 | BWKQ | 变压器温控器 |  | 温控装置故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_BWKQ | POWEquipment | DI1 | 417 | :R:A:AAA:PSCADA:BWKQ0001 | <alias>AAAPSCADABWKQ0001 | [6 empty] | DEIV | deiAAAPSCADABWKQ0001-417
|  |  |  | AAA |  | PSCADA | 温控器 | BWKQ | 变压器温控器 |  | 配电变外壳门状态 |  | DI1 |  | 关门 |  |  |  | 开门 | 2 | [98 empty] | PSCADA_BWKQ | POWEquipment | DI1 | 418 | :R:A:AAA:PSCADA:BWKQ0001 | <alias>AAAPSCADABWKQ0001 | [6 empty] | DEIV | deiAAAPSCADABWKQ0001-418
|  |  |  | AAA |  | PSCADA | 温控器 | BWKQ | 变压器温控器 |  | 装置通讯状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_BWKQ | POWEquipment | DI1/SOE | 419 | :R:A:AAA:PSCADA:BWKQ0001 | <alias>AAAPSCADABWKQ0001 | [6 empty] | DEIV | deiAAAPSCADABWKQ0001-419
|  |  |  | AAA |  | PSCADA | 整流器 | DZLQ | 整流器 |  | 桥臂熔断报警 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DZLQ | POWEquipment | DI1 | 420 | :R:A:AAA:PSCADA:DZLQ0001 | <alias>AAAPSCADADZLQ0001 | [6 empty] | DEIV | deiAAAPSCADADZLQ0001-420
|  |  |  | AAA |  | PSCADA | 整流器 | DZLQ | 整流器 |  | 桥臂熔断跳闸 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DZLQ | POWEquipment | DI1 | 421 | :R:A:AAA:PSCADA:DZLQ0001 | <alias>AAAPSCADADZLQ0001 | [6 empty] | DEIV | deiAAAPSCADADZLQ0001-421
|  |  |  | AAA |  | PSCADA | 整流器 | DZLQ | 整流器 |  | 超温报警 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DZLQ | POWEquipment | DI1 | 422 | :R:A:AAA:PSCADA:DZLQ0001 | <alias>AAAPSCADADZLQ0001 | [6 empty] | DEIV | deiAAAPSCADADZLQ0001-422
|  |  |  | AAA |  | PSCADA | 整流器 | DZLQ | 整流器 |  | 超温跳闸 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DZLQ | POWEquipment | DI1 | 423 | :R:A:AAA:PSCADA:DZLQ0001 | <alias>AAAPSCADADZLQ0001 | [6 empty] | DEIV | deiAAAPSCADADZLQ0001-423
|  |  |  | AAA |  | PSCADA | 整流器 | DZLQ | 整流器 |  | 开门信号 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DZLQ | POWEquipment | DI1 | 424 | :R:A:AAA:PSCADA:DZLQ0001 | <alias>AAAPSCADADZLQ0001 | [6 empty] | DEIV | deiAAAPSCADADZLQ0001-424
|  |  |  | AAA |  | PSCADA | 整流器 | DZLQ | 整流器 |  | 压敏快熔故障信号 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DZLQ | POWEquipment | DI1 | 425 | :R:A:AAA:PSCADA:DZLQ0001 | <alias>AAAPSCADADZLQ0001 | [6 empty] | DEIV | deiAAAPSCADADZLQ0001-425
|  |  |  | AAA |  | PSCADA | 整流器 | DZLQ | 整流器 |  | 装置通讯状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_DZLQ | POWEquipment | DI1/SOE | 426 | :R:A:AAA:PSCADA:DZLQ0001 | <alias>AAAPSCADADZLQ0001 | [6 empty] | DEIV | deiAAAPSCADADZLQ0001-426
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 蓄电池电压 | V | AI | [105 empty] | PSCADA_DZLP | POWEquipment | AI | 427 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | AEIV | aeiAAAPSCADADZLP0001-427
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 蓄电池电流 | A | AI | [105 empty] | PSCADA_DZLP | POWEquipment | AI | 428 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | AEIV | aeiAAAPSCADADZLP0001-428
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 蓄电池温度 | ℃ | AI | [105 empty] | PSCADA_DZLP | POWEquipment | AI | 429 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | AEIV | aeiAAAPSCADADZLP0001-429
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 直流母线电压 | V | AI | [105 empty] | PSCADA_DZLP | POWEquipment | AI | 430 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | AEIV | aeiAAAPSCADADZLP0001-430
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 直流母线电流 | A | AI | [105 empty] | PSCADA_DZLP | POWEquipment | AI | 431 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | AEIV | aeiAAAPSCADADZLP0001-431
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 绝缘监测母线正对地电压 | V | AI | [105 empty] | PSCADA_DZLP | POWEquipment | AI | 432 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | AEIV | aeiAAAPSCADADZLP0001-432
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 绝缘监测母线负对地电压 | V | AI | [105 empty] | PSCADA_DZLP | POWEquipment | AI | 433 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | AEIV | aeiAAAPSCADADZLP0001-433
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 绝缘监测母线正对地电阻 | kΩ | AI | [105 empty] | PSCADA_DZLP | POWEquipment | AI | 434 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | AEIV | aeiAAAPSCADADZLP0001-434
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 绝缘监测母线负对地电阻 | kΩ | AI | [105 empty] | PSCADA_DZLP | POWEquipment | AI | 435 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | AEIV | aeiAAAPSCADADZLP0001-435
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 高频开关电源智能充电模块异常 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DZLP | POWEquipment | DI1 | 436 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | DEIV | deiAAAPSCADADZLP0001-436
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 蓄电池组过压 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DZLP | POWEquipment | DI1 | 437 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | DEIV | deiAAAPSCADADZLP0001-437
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 蓄电池组欠压 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DZLP | POWEquipment | DI1 | 438 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | DEIV | deiAAAPSCADADZLP0001-438
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 蓄电池充放电状态 |  | DI1 |  | 充电 |  |  |  | 放电 | 2 | [98 empty] | PSCADA_DZLP | POWEquipment | DI1 | 439 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | DEIV | deiAAAPSCADADZLP0001-439
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 母线过压 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DZLP | POWEquipment | DI1 | 440 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | DEIV | deiAAAPSCADADZLP0001-440
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 母线欠压 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DZLP | POWEquipment | DI1 | 441 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | DEIV | deiAAAPSCADADZLP0001-441
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 电池巡检仪故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DZLP | POWEquipment | DI1 | 442 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | DEIV | deiAAAPSCADADZLP0001-442
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 交流进线开关1JK状态 |  | DI1 |  | 分位 |  |  |  | 合位 | 2 | [98 empty] | PSCADA_DZLP | POWEquipment | DI1 | 443 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | DEIV | deiAAAPSCADADZLP0001-443
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 充电机输出开关1ZK状态 |  | DI1 |  | 分位 |  |  |  | 合位 | 2 | [98 empty] | PSCADA_DZLP | POWEquipment | DI1 | 444 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | DEIV | deiAAAPSCADADZLP0001-444
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 蓄电池输出开关2ZK状态 |  | DI1 |  | 分位 |  |  |  | 合位 | 2 | [98 empty] | PSCADA_DZLP | POWEquipment | DI1 | 445 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | DEIV | deiAAAPSCADADZLP0001-445
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 输入交流故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DZLP | POWEquipment | DI1 | 446 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | DEIV | deiAAAPSCADADZLP0001-446
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 主开关故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DZLP | POWEquipment | DI1 | 447 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | DEIV | deiAAAPSCADADZLP0001-447
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 输出开关跳闸总信号 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DZLP | POWEquipment | DI1 | 448 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | DEIV | deiAAAPSCADADZLP0001-448
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 绝缘故障 |  | DI1 |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_DZLP | POWEquipment | DI1 | 449 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | DEIV | deiAAAPSCADADZLP0001-449
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 硅链故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DZLP | POWEquipment | DI1 | 450 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | DEIV | deiAAAPSCADADZLP0001-450
|  |  |  | AAA |  | PSCADA | 交直流屏 | DZLP | 直流屏 |  | 直流屏避雷器故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DZLP | POWEquipment | DI1 | 451 | :R:A:AAA:PSCADA:DZLP0001 | <alias>AAAPSCADADZLP0001 | [6 empty] | DEIV | deiAAAPSCADADZLP0001-451
|  |  |  | AAA |  | PSCADA | 交直流屏 | DJLP | 交流屏 |  | 交流进线I段A相电压 | V | AI | [105 empty] | PSCADA_DJLP | POWEquipment | AI | 452 | :R:A:AAA:PSCADA:DJLP0001 | <alias>AAAPSCADADJLP0001 | [6 empty] | AEIV | aeiAAAPSCADADJLP0001-452
|  |  |  | AAA |  | PSCADA | 交直流屏 | DJLP | 交流屏 |  | 交流进线I段B相电压 | V | AI | [105 empty] | PSCADA_DJLP | POWEquipment | AI | 453 | :R:A:AAA:PSCADA:DJLP0001 | <alias>AAAPSCADADJLP0001 | [6 empty] | AEIV | aeiAAAPSCADADJLP0001-453
|  |  |  | AAA |  | PSCADA | 交直流屏 | DJLP | 交流屏 |  | 交流进线I段C相电压 | V | AI | [105 empty] | PSCADA_DJLP | POWEquipment | AI | 454 | :R:A:AAA:PSCADA:DJLP0001 | <alias>AAAPSCADADJLP0001 | [6 empty] | AEIV | aeiAAAPSCADADJLP0001-454
|  |  |  | AAA |  | PSCADA | 交直流屏 | DJLP | 交流屏 |  | 交流进线II段A相电压 | V | AI | [105 empty] | PSCADA_DJLP | POWEquipment | AI | 455 | :R:A:AAA:PSCADA:DJLP0001 | <alias>AAAPSCADADJLP0001 | [6 empty] | AEIV | aeiAAAPSCADADJLP0001-455
|  |  |  | AAA |  | PSCADA | 交直流屏 | DJLP | 交流屏 |  | 交流进线II段B相电压 | V | AI | [105 empty] | PSCADA_DJLP | POWEquipment | AI | 456 | :R:A:AAA:PSCADA:DJLP0001 | <alias>AAAPSCADADJLP0001 | [6 empty] | AEIV | aeiAAAPSCADADJLP0001-456
|  |  |  | AAA |  | PSCADA | 交直流屏 | DJLP | 交流屏 |  | 交流进线II段C相电压 | V | AI | [105 empty] | PSCADA_DJLP | POWEquipment | AI | 457 | :R:A:AAA:PSCADA:DJLP0001 | <alias>AAAPSCADADJLP0001 | [6 empty] | AEIV | aeiAAAPSCADADJLP0001-457
|  |  |  | AAA |  | PSCADA | 交直流屏 | DJLP | 交流屏 |  | ATS-I位开关状态 |  | DI1 |  | 分位 |  |  |  | 合位 | 2 | [98 empty] | PSCADA_DJLP | POWEquipment | DI1 | 458 | :R:A:AAA:PSCADA:DJLP0001 | <alias>AAAPSCADADJLP0001 | [6 empty] | DEIV | deiAAAPSCADADJLP0001-458
|  |  |  | AAA |  | PSCADA | 交直流屏 | DJLP | 交流屏 |  | ATS-II位开关状态 |  | DI1 |  | 分位 |  |  |  | 合位 | 2 | [98 empty] | PSCADA_DJLP | POWEquipment | DI1 | 459 | :R:A:AAA:PSCADA:DJLP0001 | <alias>AAAPSCADADJLP0001 | [6 empty] | DEIV | deiAAAPSCADADJLP0001-459
|  |  |  | AAA |  | PSCADA | 交直流屏 | DJLP | 交流屏 |  | 交流屏避雷器故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DJLP | POWEquipment | DI1 | 460 | :R:A:AAA:PSCADA:DJLP0001 | <alias>AAAPSCADADJLP0001 | [6 empty] | DEIV | deiAAAPSCADADJLP0001-460
|  |  |  | AAA |  | PSCADA | 交直流屏 | DJLP | 交流屏 |  | 交流屏交流电异常 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DJLP | POWEquipment | DI1 | 461 | :R:A:AAA:PSCADA:DJLP0001 | <alias>AAAPSCADADJLP0001 | [6 empty] | DEIV | deiAAAPSCADADJLP0001-461
|  |  |  | AAA |  | PSCADA | 交直流屏 | DJLP | 交流屏 |  | 交流屏输出开关跳闸（总信号） |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DJLP | POWEquipment | DI1 | 462 | :R:A:AAA:PSCADA:DJLP0001 | <alias>AAAPSCADADJLP0001 | [6 empty] | DEIV | deiAAAPSCADADJLP0001-462
|  |  |  | AAA |  | PSCADA | 交直流屏 | DJLP | 交流屏 |  | ATS装置故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_DJLP | POWEquipment | DI1 | 463 | :R:A:AAA:PSCADA:DJLP0001 | <alias>AAAPSCADADJLP0001 | [6 empty] | DEIV | deiAAAPSCADADJLP0001-463
|  |  |  | AAA |  | PSCADA | PSCADA | TXZT | 通信状态 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_TXZT | POWEquipment | DI1/SOE | 464 | :R:A:AAA:PSCADA:TXZT0001 | <alias>AAAPSCADATXZT0001 | [6 empty] | DEIV | deiAAAPSCADATXZT0001-464
|  |  |  | AAA |  | PSCADA | 控制信号盘 | KZQX | 控制信号盘 |  | 调度操作 |  | DI1/SOE |  | 无意义 |  |  |  | 调度 | 2 | [98 empty] | PSCADA_KZQX | POWEquipment | DI1/SOE | 465 | :R:A:AAA:PSCADA:KZQX0001 | <alias>AAAPSCADAKZQX0001 | [6 empty] | DEIV | deiAAAPSCADAKZQX0001-465
|  |  |  | AAA |  | PSCADA | 控制信号盘 | KZQX | 控制信号盘 |  | 所内操作 |  | DI1/SOE |  | 无意义 |  |  |  | 所内 | 2 | [98 empty] | PSCADA_KZQX | POWEquipment | DI1/SOE | 466 | :R:A:AAA:PSCADA:KZQX0001 | <alias>AAAPSCADAKZQX0001 | [6 empty] | DEIV | deiAAAPSCADAKZQX0001-466
|  |  |  | AAA |  | PSCADA | 控制信号盘 | CPHU | 控制信号盘 |  | 音响复归信号 |  | DI1/SOE |  | 消失 |  |  |  | 发出 | 2 | [98 empty] | PSCADA_CPHU | POWEquipment | DI1/SOE | 467 | :R:A:AAA:PSCADA:CPHU0001 | <alias>AAAPSCADACPHU0001 | [6 empty] | DEIV | deiAAAPSCADACPHU0001-467
|  |  |  | AAA |  | PSCADA | 控制信号盘 | CPHU | 控制信号盘 |  | 音响投入/退出 |  | DI1/SOE |  | 退出 |  |  |  | 投入 | 2 | [98 empty] | PSCADA_CPHU | POWEquipment | DI1/SOE | 468 | :R:A:AAA:PSCADA:CPHU0001 | <alias>AAAPSCADACPHU0001 | [6 empty] | DEIV | deiAAAPSCADACPHU0001-468
|  |  |  | AAA |  | PSCADA | 控制信号盘 | CPHU | 控制信号盘 |  | 遥控测试开关位置 |  | DI1/SOE |  | 分位 |  |  |  | 合位 | [99 empty] | PSCADA_CPHU | POWEquipment | DI1/SOE | 469 | :R:A:AAA:PSCADA:CPHU0001 | <alias>AAAPSCADACPHU0001 | [6 empty] | DEIV | deiAAAPSCADACPHU0001-469
|  |  |  | AAA |  | PSCADA | 控制信号盘 | CPHU | 控制信号盘 |  | 交直流电源装置故障 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CPHU | POWEquipment | DI1/SOE | 470 | :R:A:AAA:PSCADA:CPHU0001 | <alias>AAAPSCADACPHU0001 | [6 empty] | DEIV | deiAAAPSCADACPHU0001-470
|  |  |  | AAA |  | PSCADA | 控制信号盘 | CPHU | 控制信号盘 |  | 35kV保护装置故障 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CPHU | POWEquipment | DI1/SOE | 471 | :R:A:AAA:PSCADA:CPHU0001 | <alias>AAAPSCADACPHU0001 | [6 empty] | DEIV | deiAAAPSCADACPHU0001-471
|  |  |  | AAA |  | PSCADA | 控制信号盘 | CPHU | 控制信号盘 |  | 1500V保护装置故障 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CPHU | POWEquipment | DI1/SOE | 472 | :R:A:AAA:PSCADA:CPHU0001 | <alias>AAAPSCADACPHU0001 | [6 empty] | DEIV | deiAAAPSCADACPHU0001-472
|  |  |  | AAA |  | PSCADA | 控制信号盘 | CPHU | 控制信号盘 |  | 再生制动能馈装置系统故障 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CPHU | POWEquipment | DI1/SOE | 473 | :R:A:AAA:PSCADA:CPHU0001 | <alias>AAAPSCADACPHU0001 | [6 empty] | DEIV | deiAAAPSCADACPHU0001-473
|  |  |  | AAA |  | PSCADA | 控制信号盘 | CPHU | 控制信号盘 |  | 能馈装置24V控制电源报警 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CPHU | POWEquipment | DI1/SOE | 474 | :R:A:AAA:PSCADA:CPHU0001 | <alias>AAAPSCADACPHU0001 | [6 empty] | DEIV | deiAAAPSCADACPHU0001-474
|  |  |  | AAA |  | PSCADA | 控制信号盘 | CPHU | 控制信号盘 |  | 跟随所交直流电源装置故障 |  | DI1/SOE |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CPHU | POWEquipment | DI1/SOE | 475 | :R:A:AAA:PSCADA:CPHU0001 | <alias>AAAPSCADACPHU0001 | [6 empty] | DEIV | deiAAAPSCADACPHU0001-475
|  |  |  | AAA |  | PSCADA | 控制信号盘 | CPHU | 控制信号盘 |  | 本体装置通讯中断报警 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_CPHU | POWEquipment | DI1/SOE | 476 | :R:A:AAA:PSCADA:CPHU0001 | <alias>AAAPSCADACPHU0001 | [6 empty] | DEIV | deiAAAPSCADACPHU0001-476
|  |  |  | AAA |  | PSCADA | 控制信号盘 | CPHU | 控制信号盘 |  | 测试开关分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_CPHU | POWEquipment | DO2 | 477 | :R:A:AAA:PSCADA:CPHU0001 | <alias>AAAPSCADACPHU0001 | [6 empty] | DEOV | deoAAAPSCADACPHU0001-477
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 1#电流测量值 | A | AI | [105 empty] | PSCADA_SNDD | POWEquipment | AI | 478 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | AEIV | aeiAAAPSCADASNDD0001-478
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 2#电流测量值 | A | AI | [105 empty] | PSCADA_SNDD | POWEquipment | AI | 479 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | AEIV | aeiAAAPSCADASNDD0001-479
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 3#电流测量值 | A | AI | [105 empty] | PSCADA_SNDD | POWEquipment | AI | 480 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | AEIV | aeiAAAPSCADASNDD0001-480
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 4#电流测量值 | A | AI | [105 empty] | PSCADA_SNDD | POWEquipment | AI | 481 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | AEIV | aeiAAAPSCADASNDD0001-481
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 5#电流测量值 | A | AI | [105 empty] | PSCADA_SNDD | POWEquipment | AI | 482 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | AEIV | aeiAAAPSCADASNDD0001-482
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 6#电流测量值 | A | AI | [105 empty] | PSCADA_SNDD | POWEquipment | AI | 483 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | AEIV | aeiAAAPSCADASNDD0001-483
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 7#电流测量值 | A | AI | [105 empty] | PSCADA_SNDD | POWEquipment | AI | 484 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | AEIV | aeiAAAPSCADASNDD0001-484
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 8#电流测量值 | A | AI | [105 empty] | PSCADA_SNDD | POWEquipment | AI | 485 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | AEIV | aeiAAAPSCADASNDD0001-485
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 超声波测得有车距离 | m | AI | [105 empty] | PSCADA_SNDD | POWEquipment | AI | 486 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | AEIV | aeiAAAPSCADASNDD0001-486
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 轨道电压值 | V | AI | [105 empty] | PSCADA_SNDD | POWEquipment | AI | 487 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | AEIV | aeiAAAPSCADASNDD0001-487
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 来车次数总计数 |  | AI | [105 empty] | PSCADA_SNDD | POWEquipment | AI | 488 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | AEIV | aeiAAAPSCADASNDD0001-488
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 1#熔断器故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 489 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-489
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 2#熔断器故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 490 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-490
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 3#熔断器故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 491 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-491
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 4#熔断器故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 492 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-492
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 控制器空开 |  | DI1 |  | 分位 |  |  |  | 合位 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 493 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-493
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 交流空开 |  | DI1 |  | 分位 |  |  |  | 合位 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 494 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-494
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 电操空开 |  | DI1 |  | 分位 |  |  |  | 合位 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 495 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-495
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 隔离开关合位 |  | DI1 |  | 无意义 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 496 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-496
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 隔离开关分位 |  | DI1 |  | 无意义 |  |  |  | 分位 | 3 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 497 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-497
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 远方操作方式 |  | DI1 |  | 无意义 |  |  |  | 远方 | 3 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 498 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-498
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 就地操作方式 |  | DI1 |  | 无意义 |  |  |  | 就地 | 3 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 499 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-499
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 门状态信号 |  | DI1 |  | 关闭 |  |  |  | 打开 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 500 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-500
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 1#逆流状态 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 501 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-501
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 2#逆流状态 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 502 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-502
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 3#逆流状态 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 503 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-503
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 4#逆流状态 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 504 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-504
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 5#逆流状态 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 505 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-505
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 6#逆流状态 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 506 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-506
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 7#逆流状态 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 507 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-507
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 8#逆流状态 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 508 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-508
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 有无车信号 |  | DI1 |  | 无车 |  |  |  | 有车 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 509 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-509
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 晶闸管导通信号 |  | DI1 |  | 关闭 |  |  |  | 导通 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1 | 510 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-510
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_SNDD | POWEquipment | DI1/SOE | 511 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEIV | deiAAAPSCADASNDD0001-511
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 单导隔离开关分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_SNDD | POWEquipment | DO2 | 512 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEOV | deoAAAPSCADASNDD0001-512
|  |  |  | AAA |  | PSCADA | 单导装置 | SNDD | 单导装置 |  | 单导清除逆流指令 |  | DO2 | [9 empty] | 清除 | [95 empty] | PSCADA_SNDD | POWEquipment | DO2 | 513 | :R:A:AAA:PSCADA:SNDD0001 | <alias>AAAPSCADASNDD0001 | [6 empty] | DEOV | deoAAAPSCADASNDD0001-513
|  |  |  | AAA |  | PSCADA | 400V | LVSC | 0.4kV手车 |  | 进线开关抽出位置 |  | DI1/SOE |  | 非抽出位 |  |  |  | 抽出位 | [99 empty] | PSCADA_LVSC | POWEquipment | DI1/SOE | 514 | :R:A:AAA:PSCADA:LVSC0001 | <alias>AAAPSCADALVSC0001 | [6 empty] | DEIV | deiAAAPSCADALVSC0001-514
|  |  |  | AAA |  | PSCADA | 400V | LVSC | 0.4kV手车 |  | 进线开关试验位置 |  | DI1/SOE |  | 非试验位 |  |  |  | 试验位 | [99 empty] | PSCADA_LVSC | POWEquipment | DI1/SOE | 515 | :R:A:AAA:PSCADA:LVSC0001 | <alias>AAAPSCADALVSC0001 | [6 empty] | DEIV | deiAAAPSCADALVSC0001-515
|  |  |  | AAA |  | PSCADA | 400V | LVSC | 0.4kV手车 |  | 进线开关工作位置 |  | DI1/SOE |  | 非工作位 |  |  |  | 工作位 | [99 empty] | PSCADA_LVSC | POWEquipment | DI1/SOE | 516 | :R:A:AAA:PSCADA:LVSC0001 | <alias>AAAPSCADALVSC0001 | [6 empty] | DEIV | deiAAAPSCADALVSC0001-516
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 进线电压(UA) | V | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 517 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-517
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 进线电压(UB) | V | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 518 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-518
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 进线电压(UC) | V | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 519 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-519
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 进线电压(Uab) | V | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 520 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-520
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 进线电压(Ubc) | V | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 521 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-521
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 进线电压(Uca) | V | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 522 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-522
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 进线电流A | A | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 523 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-523
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 进线电流B | A | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 524 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-524
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 进线电流C | A | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 525 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-525
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 有功功率A | W | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 526 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-526
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 有功功率B | W | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 527 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-527
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 有功功率C | W | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 528 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-528
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 总有功功率 | W | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 529 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-529
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 无功功率A | Var | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 530 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-530
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 无功功率B | Var | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 531 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-531
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 无功功率C | Var | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 532 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-532
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 总无功功率 | Var | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 533 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-533
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 功率因数A |  | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 534 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-534
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 功率因数B |  | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 535 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-535
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 功率因数C |  | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 536 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-536
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 总功率因数 |  | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 537 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-537
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 频率 | Hz | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 538 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-538
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 总有功电度 | Wh | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 539 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-539
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 总无功电度 | Varh | AI | [105 empty] | PSCADA_LVIA | POWEquipment | AI | 540 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | AEIV | aeiAAAPSCADALVIA0001-540
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 进线开关分位状态 |  | DI1 |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_LVIA | POWEquipment | DI1 | 541 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | DEIV | deiAAAPSCADALVIA0001-541
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 进线开关合位状态 |  | DI1 |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_LVIA | POWEquipment | DI1 | 542 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | DEIV | deiAAAPSCADALVIA0001-542
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 进线开关故障状态 |  | DI1 |  | 正常 |  |  |  | 故障 | [99 empty] | PSCADA_LVIA | POWEquipment | DI1 | 543 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | DEIV | deiAAAPSCADALVIA0001-543
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 进线开关准备就绪 |  | DI1 |  | 无意义 |  |  |  | 就绪 | [99 empty] | PSCADA_LVIA | POWEquipment | DI1 | 544 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | DEIV | deiAAAPSCADALVIA0001-544
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 进线电源 |  | DI1 |  | 失压 |  |  |  | 有压 | [99 empty] | PSCADA_LVIA | POWEquipment | DI1 | 545 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | DEIV | deiAAAPSCADALVIA0001-545
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_LVIA | POWEquipment | DI1/SOE | 546 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | DEIV | deiAAAPSCADALVIA0001-546
|  |  |  | AAA |  | PSCADA | 400V | LVIA | 0.4kV进线断路器 |  | 断路器分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_LVIA | POWEquipment | DO2 | 547 | :R:A:AAA:PSCADA:LVIA0001 | <alias>AAAPSCADALVIA0001 | [6 empty] | DEOV | deoAAAPSCADALVIA0001-547
|  |  |  | AAA |  | PSCADA | 400V | LVCA | 0.4kV母联断路器 |  | 母联开关分位状态 |  | DI1 |  | 无意义 |  |  |  | 分位 | 1 | [98 empty] | PSCADA_LVCA | POWEquipment | DI1 | 548 | :R:A:AAA:PSCADA:LVCA0001 | <alias>AAAPSCADALVCA0001 | [6 empty] | DEIV | deiAAAPSCADALVCA0001-548
|  |  |  | AAA |  | PSCADA | 400V | LVCA | 0.4kV母联断路器 |  | 母联开关合位状态 |  | DI1 |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_LVCA | POWEquipment | DI1 | 549 | :R:A:AAA:PSCADA:LVCA0001 | <alias>AAAPSCADALVCA0001 | [6 empty] | DEIV | deiAAAPSCADALVCA0001-549
|  |  |  | AAA |  | PSCADA | 400V | LVCA | 0.4kV母联断路器 |  | 母联开关故障状态 |  | DI1 |  | 正常 |  |  |  | 故障 | [99 empty] | PSCADA_LVCA | POWEquipment | DI1 | 550 | :R:A:AAA:PSCADA:LVCA0001 | <alias>AAAPSCADALVCA0001 | [6 empty] | DEIV | deiAAAPSCADALVCA0001-550
|  |  |  | AAA |  | PSCADA | 400V | LVCA | 0.4kV母联断路器 |  | 母联开关准备就绪 |  | DI1 |  | 无意义 |  |  |  | 就绪 | [99 empty] | PSCADA_LVCA | POWEquipment | DI1 | 551 | :R:A:AAA:PSCADA:LVCA0001 | <alias>AAAPSCADALVCA0001 | [6 empty] | DEIV | deiAAAPSCADALVCA0001-551
|  |  |  | AAA |  | PSCADA | 400V | LVCA | 0.4kV母联断路器 |  | 就地操作方式 |  | DI1 |  | 无意义 |  |  |  | 就地 | [99 empty] | PSCADA_LVCA | POWEquipment | DI1 | 552 | :R:A:AAA:PSCADA:LVCA0001 | <alias>AAAPSCADALVCA0001 | [6 empty] | DEIV | deiAAAPSCADALVCA0001-552
|  |  |  | AAA |  | PSCADA | 400V | LVCA | 0.4kV母联断路器 |  | 远方操作方式 |  | DI1 |  | 无意义 |  |  |  | 远方 | 2 | [98 empty] | PSCADA_LVCA | POWEquipment | DI1 | 553 | :R:A:AAA:PSCADA:LVCA0001 | <alias>AAAPSCADALVCA0001 | [6 empty] | DEIV | deiAAAPSCADALVCA0001-553
|  |  |  | AAA |  | PSCADA | 400V | LVCA | 0.4kV母联断路器 |  | 自投自复-投入 |  | DI1 |  | 无意义 |  |  |  | 投入 | 2 | [98 empty] | PSCADA_LVCA | POWEquipment | DI1 | 554 | :R:A:AAA:PSCADA:LVCA0001 | <alias>AAAPSCADALVCA0001 | [6 empty] | DEIV | deiAAAPSCADALVCA0001-554
|  |  |  | AAA |  | PSCADA | 400V | LVCA | 0.4kV母联断路器 |  | 自投自复-退出 |  | DI1 |  | 无意义 |  |  |  | 退出 | [99 empty] | PSCADA_LVCA | POWEquipment | DI1 | 555 | :R:A:AAA:PSCADA:LVCA0001 | <alias>AAAPSCADALVCA0001 | [6 empty] | DEIV | deiAAAPSCADALVCA0001-555
|  |  |  | AAA |  | PSCADA | 400V | LVCA | 0.4kV母联断路器 |  | 三级负荷联动反馈 |  | DI1 |  | 无意义 |  |  |  | 联动 | 2 | [98 empty] | PSCADA_LVCA | POWEquipment | DI1 | 556 | :R:A:AAA:PSCADA:LVCA0001 | <alias>AAAPSCADALVCA0001 | [6 empty] | DEIV | deiAAAPSCADALVCA0001-556
|  |  |  | AAA |  | PSCADA | 400V | LVCA | 0.4kV母联断路器 |  | 三级负荷不联动反馈 |  | DI1 |  | 无意义 |  |  |  | 不联动 | 2 | [98 empty] | PSCADA_LVCA | POWEquipment | DI1 | 557 | :R:A:AAA:PSCADA:LVCA0001 | <alias>AAAPSCADALVCA0001 | [6 empty] | DEIV | deiAAAPSCADALVCA0001-557
|  |  |  | AAA |  | PSCADA | 400V | LVCA | 0.4kV母联断路器 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_LVCA | POWEquipment | DI1/SOE | 558 | :R:A:AAA:PSCADA:LVCA0001 | <alias>AAAPSCADALVCA0001 | [6 empty] | DEIV | deiAAAPSCADALVCA0001-558
|  |  |  | AAA |  | PSCADA | 400V | LVCA | 0.4kV母联断路器 |  | 母联断路器分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_LVCA | POWEquipment | DO2 | 559 | :R:A:AAA:PSCADA:LVCA0001 | <alias>AAAPSCADALVCA0001 | [6 empty] | DEOV | deoAAAPSCADALVCA0001-559
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | A相电压Ua | V | AI | [105 empty] | PSCADA_LVIB | POWEquipment | AI | 560 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | AEIV | aeiAAAPSCADALVIB0001-560
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | B相电压Ub | V | AI | [105 empty] | PSCADA_LVIB | POWEquipment | AI | 561 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | AEIV | aeiAAAPSCADALVIB0001-561
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | C相电压Uc | V | AI | [105 empty] | PSCADA_LVIB | POWEquipment | AI | 562 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | AEIV | aeiAAAPSCADALVIB0001-562
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | AB线电压Uab | V | AI | [105 empty] | PSCADA_LVIB | POWEquipment | AI | 563 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | AEIV | aeiAAAPSCADALVIB0001-563
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | BC线电压Ubc | V | AI | [105 empty] | PSCADA_LVIB | POWEquipment | AI | 564 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | AEIV | aeiAAAPSCADALVIB0001-564
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | CA线电压Uca | V | AI | [105 empty] | PSCADA_LVIB | POWEquipment | AI | 565 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | AEIV | aeiAAAPSCADALVIB0001-565
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | A相电流Ia | A | AI | [105 empty] | PSCADA_LVIB | POWEquipment | AI | 566 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | AEIV | aeiAAAPSCADALVIB0001-566
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | B相电流Ib | A | AI | [105 empty] | PSCADA_LVIB | POWEquipment | AI | 567 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | AEIV | aeiAAAPSCADALVIB0001-567
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | C相电流Ic | A | AI | [105 empty] | PSCADA_LVIB | POWEquipment | AI | 568 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | AEIV | aeiAAAPSCADALVIB0001-568
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | N相电流In | A | AI | [105 empty] | PSCADA_LVIB | POWEquipment | AI | 569 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | AEIV | aeiAAAPSCADALVIB0001-569
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | 有功功率P | W | AI | [105 empty] | PSCADA_LVIB | POWEquipment | AI | 570 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | AEIV | aeiAAAPSCADALVIB0001-570
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | 无功功率Q | Var | AI | [105 empty] | PSCADA_LVIB | POWEquipment | AI | 571 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | AEIV | aeiAAAPSCADALVIB0001-571
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | 功率因数 |  | AI | [105 empty] | PSCADA_LVIB | POWEquipment | AI | 572 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | AEIV | aeiAAAPSCADALVIB0001-572
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | 有功电度KWh | kWh | AI | [105 empty] | PSCADA_LVIB | POWEquipment | AI | 573 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | AEIV | aeiAAAPSCADALVIB0001-573
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | 无功电度Kvarh | kVarh | AI | [105 empty] | PSCADA_LVIB | POWEquipment | AI | 574 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | AEIV | aeiAAAPSCADALVIB0001-574
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | 进线开关电压信号 |  | DI1 |  | 有压 |  |  |  | 无压 | [99 empty] | PSCADA_LVIB | POWEquipment | DI1 | 575 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | DEIV | deiAAAPSCADALVIB0001-575
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | 进线开关故障跳闸 |  | DI1 |  | 复归 |  |  |  | 动作 | [99 empty] | PSCADA_LVIB | POWEquipment | DI1 | 576 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | DEIV | deiAAAPSCADALVIB0001-576
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | 进线开关分位 |  | DI1 |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_LVIB | POWEquipment | DI1 | 577 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | DEIV | deiAAAPSCADALVIB0001-577
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | 进线开关合位 |  | DI1 |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_LVIB | POWEquipment | DI1 | 578 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | DEIV | deiAAAPSCADALVIB0001-578
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | 进线开关合闸准备就绪 |  | DI1 |  | 无意义 |  |  |  | 就绪 | [99 empty] | PSCADA_LVIB | POWEquipment | DI1 | 579 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | DEIV | deiAAAPSCADALVIB0001-579
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | 进线开关抽出位置 |  | DI1 |  | 非抽出位 |  |  |  | 抽出位 | [99 empty] | PSCADA_LVIB | POWEquipment | DI1 | 580 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | DEIV | deiAAAPSCADALVIB0001-580
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | 进线开关试验位置 |  | DI1 |  | 非试验位 |  |  |  | 试验位 | [99 empty] | PSCADA_LVIB | POWEquipment | DI1 | 581 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | DEIV | deiAAAPSCADALVIB0001-581
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | 进线开关工作位置 |  | DI1 |  | 非工作位 |  |  |  | 工作位 | [99 empty] | PSCADA_LVIB | POWEquipment | DI1 | 582 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | DEIV | deiAAAPSCADALVIB0001-582
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | 就地/远方操作方式 |  | DI1 |  | 远方 |  |  |  | 就地 | [99 empty] | PSCADA_LVIB | POWEquipment | DI1 | 583 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | DEIV | deiAAAPSCADALVIB0001-583
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | 自投自复投入/退出模式 |  | DI1 |  | 退出 |  |  |  | 投入 | [99 empty] | PSCADA_LVIB | POWEquipment | DI1 | 584 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | DEIV | deiAAAPSCADALVIB0001-584
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | 对侧断路器110V控制电源故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | [99 empty] | PSCADA_LVIB | POWEquipment | DI1 | 585 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | DEIV | deiAAAPSCADALVIB0001-585
|  |  |  | AAA |  | PSCADA | 400V | LVIB | 0.4kV进线断路器 |  | 断路器分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_LVIB | POWEquipment | DO2 | 586 | :R:A:AAA:PSCADA:LVIB0001 | <alias>AAAPSCADALVIB0001 | [6 empty] | DEOV | deoAAAPSCADALVIB0001-586
|  |  |  | AAA |  | PSCADA | 400V | LVCB | 0.4kV母联断路器 |  | 母联开关分位状态 |  | DI1 |  | 无意义 |  |  |  | 分位 | [99 empty] | PSCADA_LVCB | POWEquipment | DI1 | 587 | :R:A:AAA:PSCADA:LVCB0001 | <alias>AAAPSCADALVCB0001 | [6 empty] | DEIV | deiAAAPSCADALVCB0001-587
|  |  |  | AAA |  | PSCADA | 400V | LVCB | 0.4kV母联断路器 |  | 母联开关合位状态 |  | DI1 |  | 无意义 |  |  |  | 合位 | [99 empty] | PSCADA_LVCB | POWEquipment | DI1 | 588 | :R:A:AAA:PSCADA:LVCB0001 | <alias>AAAPSCADALVCB0001 | [6 empty] | DEIV | deiAAAPSCADALVCB0001-588
|  |  |  | AAA |  | PSCADA | 400V | LVCB | 0.4kV母联断路器 |  | 母联开关故障跳闸 |  | DI1 |  | 复归 |  |  |  | 动作 | [99 empty] | PSCADA_LVCB | POWEquipment | DI1 | 589 | :R:A:AAA:PSCADA:LVCB0001 | <alias>AAAPSCADALVCB0001 | [6 empty] | DEIV | deiAAAPSCADALVCB0001-589
|  |  |  | AAA |  | PSCADA | 400V | LVCB | 0.4kV母联断路器 |  | 母联开关合闸准备就绪 |  | DI1 |  | 无意义 |  |  |  | 就绪 | [99 empty] | PSCADA_LVCB | POWEquipment | DI1 | 590 | :R:A:AAA:PSCADA:LVCB0001 | <alias>AAAPSCADALVCB0001 | [6 empty] | DEIV | deiAAAPSCADALVCB0001-590
|  |  |  | AAA |  | PSCADA | 400V | LVCB | 0.4kV母联断路器 |  | 母联开关工作位置 |  | DI1 |  | 非工作位 |  |  |  | 工作位 | [99 empty] | PSCADA_LVCB | POWEquipment | DI1 | 591 | :R:A:AAA:PSCADA:LVCB0001 | <alias>AAAPSCADALVCB0001 | [6 empty] | DEIV | deiAAAPSCADALVCB0001-591
|  |  |  | AAA |  | PSCADA | 400V | LVCB | 0.4kV母联断路器 |  | 母联开关抽出位置 |  | DI1 |  | 非抽出位 |  |  |  | 抽出位 | [99 empty] | PSCADA_LVCB | POWEquipment | DI1 | 592 | :R:A:AAA:PSCADA:LVCB0001 | <alias>AAAPSCADALVCB0001 | [6 empty] | DEIV | deiAAAPSCADALVCB0001-592
|  |  |  | AAA |  | PSCADA | 400V | LVCB | 0.4kV母联断路器 |  | 母联开关试验位置 |  | DI1 |  | 非试验位 |  |  |  | 试验位 | [99 empty] | PSCADA_LVCB | POWEquipment | DI1 | 593 | :R:A:AAA:PSCADA:LVCB0001 | <alias>AAAPSCADALVCB0001 | [6 empty] | DEIV | deiAAAPSCADALVCB0001-593
|  |  |  | AAA |  | PSCADA | 400V | LVCB | 0.4kV母联断路器 |  | 就地/远方操作方式 |  | DI1 |  | 远方 |  |  |  | 就地 | [99 empty] | PSCADA_LVCB | POWEquipment | DI1 | 594 | :R:A:AAA:PSCADA:LVCB0001 | <alias>AAAPSCADALVCB0001 | [6 empty] | DEIV | deiAAAPSCADALVCB0001-594
|  |  |  | AAA |  | PSCADA | 400V | LVCB | 0.4kV母联断路器 |  | 母联断路器分合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_LVCB | POWEquipment | DO2 | 595 | :R:A:AAA:PSCADA:LVCB0001 | <alias>AAAPSCADALVCB0001 | [6 empty] | DEOV | deoAAAPSCADALVCB0001-595
|  |  |  | AAA |  | PSCADA | 400V | FHZT | 三级负荷总开关 |  | 三级负荷开关分/合闸指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_FHZT | POWEquipment | DO2 | 596 | :R:A:AAA:PSCADA:FHZT0001 | <alias>AAAPSCADAFHZT0001 | [6 empty] | DEOV | deoAAAPSCADAFHZT0001-596
|  |  |  | AAA |  | PSCADA | 400V | FHRY | 三级负荷软压板 |  | 三级负荷软压板状态反馈信号 |  | DI1 |  | 退出 |  |  |  | 投入 | [99 empty] | PSCADA_FHRY | POWEquipment | DI1 | 597 | :R:A:AAA:PSCADA:FHRY0001 | <alias>AAAPSCADAFHRY0001 | [6 empty] | DEIV | deiAAAPSCADAFHRY0001-597
|  |  |  | AAA |  | PSCADA | 400V | FHRY | 三级负荷软压板 |  | 三级负荷点动软压板切换 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_FHRY | POWEquipment | DO2 | 598 | :R:A:AAA:PSCADA:FHRY0001 | <alias>AAAPSCADAFHRY0001 | [6 empty] | DEOV | deoAAAPSCADAFHRY0001-598
|  |  |  | AAA |  | PSCADA | 400V | XKG1 | 0.4kV开关 |  | 开关状态 |  | DI1 |  | 分位 |  |  |  | 合位 | [99 empty] | PSCADA_XKG1 | POWEquipment | DI1 | 599 | :R:A:AAA:PSCADA:XKG10001 | <alias>AAAPSCADAXKG10001 | [6 empty] | DEIV | deiAAAPSCADAXKG10001-599
|  |  |  | AAA |  | PSCADA | 400V | XKG1 | 0.4kV开关 |  | 开关故障状态 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_XKG1 | POWEquipment | DI1 | 600 | :R:A:AAA:PSCADA:XKG10001 | <alias>AAAPSCADAXKG10001 | [6 empty] | DEIV | deiAAAPSCADAXKG10001-600
|  |  |  | AAA |  | PSCADA | 400V | XKG2 | 0.4kV开关 |  | 进线电压(UA) | V | AI | [105 empty] | PSCADA_XKG2 | POWEquipment | AI | 601 | :R:A:AAA:PSCADA:XKG20001 | <alias>AAAPSCADAXKG20001 | [6 empty] | AEIV | aeiAAAPSCADAXKG20001-601
|  |  |  | AAA |  | PSCADA | 400V | XKG2 | 0.4kV开关 |  | 进线电压(UB) | V | AI | [105 empty] | PSCADA_XKG2 | POWEquipment | AI | 602 | :R:A:AAA:PSCADA:XKG20001 | <alias>AAAPSCADAXKG20001 | [6 empty] | AEIV | aeiAAAPSCADAXKG20001-602
|  |  |  | AAA |  | PSCADA | 400V | XKG2 | 0.4kV开关 |  | 进线电压(UC) | V | AI | [105 empty] | PSCADA_XKG2 | POWEquipment | AI | 603 | :R:A:AAA:PSCADA:XKG20001 | <alias>AAAPSCADAXKG20001 | [6 empty] | AEIV | aeiAAAPSCADAXKG20001-603
|  |  |  | AAA |  | PSCADA | 400V | XKG2 | 0.4kV开关 |  | 进线电流A | A | AI | [105 empty] | PSCADA_XKG2 | POWEquipment | AI | 604 | :R:A:AAA:PSCADA:XKG20001 | <alias>AAAPSCADAXKG20001 | [6 empty] | AEIV | aeiAAAPSCADAXKG20001-604
|  |  |  | AAA |  | PSCADA | 400V | XKG2 | 0.4kV开关 |  | 进线电流B | A | AI | [105 empty] | PSCADA_XKG2 | POWEquipment | AI | 605 | :R:A:AAA:PSCADA:XKG20001 | <alias>AAAPSCADAXKG20001 | [6 empty] | AEIV | aeiAAAPSCADAXKG20001-605
|  |  |  | AAA |  | PSCADA | 400V | XKG2 | 0.4kV开关 |  | 进线电流C | A | AI | [105 empty] | PSCADA_XKG2 | POWEquipment | AI | 606 | :R:A:AAA:PSCADA:XKG20001 | <alias>AAAPSCADAXKG20001 | [6 empty] | AEIV | aeiAAAPSCADAXKG20001-606
|  |  |  | AAA |  | PSCADA | 400V | XKG2 | 0.4kV开关 |  | 有功功率A | W | AI | [105 empty] | PSCADA_XKG2 | POWEquipment | AI | 607 | :R:A:AAA:PSCADA:XKG20001 | <alias>AAAPSCADAXKG20001 | [6 empty] | AEIV | aeiAAAPSCADAXKG20001-607
|  |  |  | AAA |  | PSCADA | 400V | XKG2 | 0.4kV开关 |  | 有功功率B | W | AI | [105 empty] | PSCADA_XKG2 | POWEquipment | AI | 608 | :R:A:AAA:PSCADA:XKG20001 | <alias>AAAPSCADAXKG20001 | [6 empty] | AEIV | aeiAAAPSCADAXKG20001-608
|  |  |  | AAA |  | PSCADA | 400V | XKG2 | 0.4kV开关 |  | 有功功率C | W | AI | [105 empty] | PSCADA_XKG2 | POWEquipment | AI | 609 | :R:A:AAA:PSCADA:XKG20001 | <alias>AAAPSCADAXKG20001 | [6 empty] | AEIV | aeiAAAPSCADAXKG20001-609
|  |  |  | AAA |  | PSCADA | 400V | XKG2 | 0.4kV开关 |  | 总有功功率 | W | AI | [105 empty] | PSCADA_XKG2 | POWEquipment | AI | 610 | :R:A:AAA:PSCADA:XKG20001 | <alias>AAAPSCADAXKG20001 | [6 empty] | AEIV | aeiAAAPSCADAXKG20001-610
|  |  |  | AAA |  | PSCADA | 400V | XKG2 | 0.4kV开关 |  | 总有功电度 | Wh | AI | [105 empty] | PSCADA_XKG2 | POWEquipment | AI | 611 | :R:A:AAA:PSCADA:XKG20001 | <alias>AAAPSCADAXKG20001 | [6 empty] | AEIV | aeiAAAPSCADAXKG20001-611
|  |  |  | AAA |  | PSCADA | 400V | XKG2 | 0.4kV开关 |  | 开关状态 |  | DI1 |  | 分位 |  |  |  | 合位 | [99 empty] | PSCADA_XKG2 | POWEquipment | DI1 | 612 | :R:A:AAA:PSCADA:XKG20001 | <alias>AAAPSCADAXKG20001 | [6 empty] | DEIV | deiAAAPSCADAXKG20001-612
|  |  |  | AAA |  | PSCADA | 400V | XKG2 | 0.4kV开关 |  | 开关故障状态 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_XKG2 | POWEquipment | DI1 | 613 | :R:A:AAA:PSCADA:XKG20001 | <alias>AAAPSCADAXKG20001 | [6 empty] | DEIV | deiAAAPSCADAXKG20001-613
|  |  |  | AAA |  | PSCADA | 400V | XKG2 | 0.4kV开关 |  | 开关就地/远方 |  | DI1 |  | 就地 |  |  |  | 远方 | [99 empty] | PSCADA_XKG2 | POWEquipment | DI1 | 614 | :R:A:AAA:PSCADA:XKG20001 | <alias>AAAPSCADAXKG20001 | [6 empty] | DEIV | deiAAAPSCADAXKG20001-614
|  |  |  | AAA |  | PSCADA | 400V | XKG3 | 0.4kV开关 |  | 开关电流Ia | A | AI | [105 empty] | PSCADA_XKG3 | POWEquipment | AI | 615 | :R:A:AAA:PSCADA:XKG30001 | <alias>AAAPSCADAXKG30001 | [6 empty] | AEIV | aeiAAAPSCADAXKG30001-615
|  |  |  | AAA |  | PSCADA | 400V | XKG3 | 0.4kV开关 |  | 开关电流Ib | A | AI | [105 empty] | PSCADA_XKG3 | POWEquipment | AI | 616 | :R:A:AAA:PSCADA:XKG30001 | <alias>AAAPSCADAXKG30001 | [6 empty] | AEIV | aeiAAAPSCADAXKG30001-616
|  |  |  | AAA |  | PSCADA | 400V | XKG3 | 0.4kV开关 |  | 开关电流Ic | A | AI | [105 empty] | PSCADA_XKG3 | POWEquipment | AI | 617 | :R:A:AAA:PSCADA:XKG30001 | <alias>AAAPSCADAXKG30001 | [6 empty] | AEIV | aeiAAAPSCADAXKG30001-617
|  |  |  | AAA |  | PSCADA | 400V | XKG3 | 0.4kV开关 |  | 开关有功电度 | kVarh | AI | [105 empty] | PSCADA_XKG3 | POWEquipment | AI | 618 | :R:A:AAA:PSCADA:XKG30001 | <alias>AAAPSCADAXKG30001 | [6 empty] | AEIV | aeiAAAPSCADAXKG30001-618
|  |  |  | AAA |  | PSCADA | 400V | XKG3 | 0.4kV开关 |  | 开关状态 |  | DI1 |  | 分位 |  |  |  | 合位 | [99 empty] | PSCADA_XKG3 | POWEquipment | DI1 | 619 | :R:A:AAA:PSCADA:XKG30001 | <alias>AAAPSCADAXKG30001 | [6 empty] | DEIV | deiAAAPSCADAXKG30001-619
|  |  |  | AAA |  | PSCADA | 400V | XKG3 | 0.4kV开关 |  | 开关故障状态 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_XKG3 | POWEquipment | DI1 | 620 | :R:A:AAA:PSCADA:XKG30001 | <alias>AAAPSCADAXKG30001 | [6 empty] | DEIV | deiAAAPSCADAXKG30001-620
|  |  |  | AAA |  | PSCADA | 400V | XKG3 | 0.4kV开关 |  | 开关就地/远方 |  | DI1 |  | 远方 |  |  |  | 就地 | [99 empty] | PSCADA_XKG3 | POWEquipment | DI1 | 621 | :R:A:AAA:PSCADA:XKG30001 | <alias>AAAPSCADAXKG30001 | [6 empty] | DEIV | deiAAAPSCADAXKG30001-621
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 运行状态 |  | DI1 |  | 无意义 |  |  |  | 分位 | 1 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 622 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-622
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 系统故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 623 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-623
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 电网过压(RS) |  | DI1 |  | 正常 |  |  |  | 过压 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 624 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-624
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 电网过压(ST) |  | DI1 |  | 正常 |  |  |  | 过压 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 625 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-625
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 电网过压(TR) |  | DI1 |  | 正常 |  |  |  | 过压 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 626 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-626
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 电网欠压(RS) |  | DI1 |  | 正常 |  |  |  | 过压 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 627 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-627
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 电网欠压(ST) |  | DI1 |  | 正常 |  |  |  | 过压 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 628 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-628
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 电网欠压(TR) |  | DI1 |  | 正常 |  |  |  | 过压 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 629 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-629
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 电网缺相/掉电(RS) |  | DI1 |  | 无意义 |  |  |  | 掉电 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 630 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-630
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 电网缺相/掉电(ST) |  | DI1 |  | 无意义 |  |  |  | 掉电 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 631 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-631
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 电网缺相/掉电(TR) |  | DI1 |  | 无意义 |  |  |  | 掉电 | [99 empty] | PSCADA_YYLB | POWEquipment | DI1 | 632 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-632
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 电网电压不平衡 |  | DI1 |  | 无意义 |  |  |  | 故障 | 1 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 633 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-633
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 电网电压THD故障 |  | DI1 |  | 无意义 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 634 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-634
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 电网过频 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 635 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-635
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 电网欠频 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 636 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-636
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 电网相序故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 637 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-637
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 电网缺相故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 638 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-638
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 电网峰值过压 |  | DI1 |  | 正常 |  |  |  | 过压 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 639 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-639
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 直流母线硬件过压 |  | DI1 |  | 正常 |  |  |  | 过压 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 640 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-640
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 直流母线(+)过压 |  | DI1 |  | 正常 |  |  |  | 过压 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 641 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-641
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 直流母线(-)过压 |  | DI1 |  | 正常 |  |  |  | 过压 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 642 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-642
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 直流母线(+)欠压 |  | DI1 |  | 正常 |  |  |  | 欠压 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 643 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-643
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 直流母线(-)欠压 |  | DI1 |  | 正常 |  |  |  | 欠压 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 644 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-644
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 直流母线不平衡故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 645 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-645
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 直流母线预充电故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 646 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-646
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 直流母线软启故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 647 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-647
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 直流母线短路故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 648 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-648
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 模块变流器：输出电流有效值过流 |  | DI1 |  | 正常 |  |  |  | 过流 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 649 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-649
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 模块变流器：硬件峰值过流 |  | DI1 |  | 正常 |  |  |  | 过流 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 650 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-650
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 模块变流器：锁相故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 651 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-651
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 模块变流器：中线电流过流 |  | DI1 |  | 正常 |  |  |  | 过流 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 652 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-652
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 模块变流器：电流检测故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 653 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-653
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 模块变流器：IGBT故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 654 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-654
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 模块变流器：峰值过流 |  | DI1 |  | 正常 |  |  |  | 过流 | 1 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 655 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-655
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 模块变流器：IGBT硬件短路 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 656 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-656
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 模块变流器：(预留) |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 657 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-657
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 环境过温 |  | DI1 |  | 正常 |  |  |  | 抽出位 | [99 empty] | PSCADA_YYLB | POWEquipment | DI1 | 658 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-658
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 环境低温 |  | DI1 |  | 正常 |  |  |  | 试验位 | [99 empty] | PSCADA_YYLB | POWEquipment | DI1 | 659 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-659
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 控制板过温 |  | DI1 |  | 正常 |  |  |  | 过温 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 660 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-660
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 右散热器过温 |  | DI1 |  | 正常 |  |  |  | 过温 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 661 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-661
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 左散热器过温 |  | DI1 |  | 正常 |  |  |  | 过温 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 662 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-662
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | IGBT硬件过温 |  | DI1 |  | 正常 |  |  |  | 过温 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 663 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-663
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | RS485通讯故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 664 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-664
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | CAN通讯故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 665 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-665
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | SPI通讯故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 666 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-666
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | (预留1) |  | DI1 |  | 无意义 |  |  |  | 分位 | 1 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 667 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-667
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 软件版本不匹配 |  | DI1 |  | 正常 |  |  |  | 不匹配 | 3 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 668 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-668
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | Offset初始化故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 3 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 669 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-669
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 电容板过温 |  | DI1 |  | 正常 |  |  |  | 过温 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 670 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-670
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | NTC硬件故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 671 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-671
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | (预留2) |  | DI1 |  | 非工作位 |  |  |  | 工作位 | [99 empty] | PSCADA_YYLB | POWEquipment | DI1 | 672 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-672
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 模式不匹配 |  | DI1 |  | 正常 |  |  |  | 不匹配 | 3 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 673 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-673
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | ADC校准失败 |  | DI1 |  | 正常 |  |  |  | 失败 | 3 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 674 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-674
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | RAM自检失败 |  | DI1 |  | 正常 |  |  |  | 失败 | 3 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 675 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-675
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | (预留内部用，禁止写操作) |  | DI1 |  | 无意义 |  |  |  | 投入 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 676 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-676
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 急停故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 2 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 677 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-677
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 辅助电源故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 1 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 678 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-678
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 风扇故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 3 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 679 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-679
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 保险丝故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 3 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 680 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-680
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 防雷器故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 3 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 681 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-681
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | EEPROM故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 3 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 682 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-682
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 同步信号丢失 |  | DI1 |  | 正常 |  |  |  | 故障 | 3 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 683 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-683
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 机械锁未锁 |  | DI1 |  | 正常 |  |  |  | 故障 | 3 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 684 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-684
|  |  |  | AAA |  | PSCADA | 400V | YYLB | 有源滤波 |  | 霍尔电源故障 |  | DI1 |  | 正常 |  |  |  | 故障 | 3 | [98 empty] | PSCADA_YYLB | POWEquipment | DI1 | 685 | :R:A:AAA:PSCADA:YYLB0001 | <alias>AAAPSCADAYYLB0001 | [6 empty] | DEIV | deiAAAPSCADAYYLB0001-685
|  |  |  | AAA |  | PSCADA | 400V | ZMZJ | 照明总计量 |  | 照明总计量回路电压U | V | AI | [105 empty] | PSCADA_ZMZJ | POWEquipment | AI | 686 | :R:A:AAA:PSCADA:ZMZJ0001 | <alias>AAAPSCADAZMZJ0001 | [6 empty] | AEIV | aeiAAAPSCADAZMZJ0001-686
|  |  |  | AAA |  | PSCADA | 400V | ZMZJ | 照明总计量 |  | 照明总计量回路电流Ia | A | AI | [105 empty] | PSCADA_ZMZJ | POWEquipment | AI | 687 | :R:A:AAA:PSCADA:ZMZJ0001 | <alias>AAAPSCADAZMZJ0001 | [6 empty] | AEIV | aeiAAAPSCADAZMZJ0001-687
|  |  |  | AAA |  | PSCADA | 400V | ZMZJ | 照明总计量 |  | 照明总计量回路电流Ib | A | AI | [105 empty] | PSCADA_ZMZJ | POWEquipment | AI | 688 | :R:A:AAA:PSCADA:ZMZJ0001 | <alias>AAAPSCADAZMZJ0001 | [6 empty] | AEIV | aeiAAAPSCADAZMZJ0001-688
|  |  |  | AAA |  | PSCADA | 400V | ZMZJ | 照明总计量 |  | 照明总计量回路电流Ic | A | AI | [105 empty] | PSCADA_ZMZJ | POWEquipment | AI | 689 | :R:A:AAA:PSCADA:ZMZJ0001 | <alias>AAAPSCADAZMZJ0001 | [6 empty] | AEIV | aeiAAAPSCADAZMZJ0001-689
|  |  |  | AAA |  | PSCADA | 400V | ZMZJ | 照明总计量 |  | 照明总计量回路有功电度 | kWh | AI | [105 empty] | PSCADA_ZMZJ | POWEquipment | AI | 690 | :R:A:AAA:PSCADA:ZMZJ0001 | <alias>AAAPSCADAZMZJ0001 | [6 empty] | AEIV | aeiAAAPSCADAZMZJ0001-690
|  |  |  | AAA |  | PSCADA | 1500V | ZSCD | 杂散电流监测点 |  | 本体电位 | mV | AI | [105 empty] | PSCADA_ZSCD | POWEquipment | AI | 691 | :R:A:AAA:PSCADA:ZSCD0001 | <alias>AAAPSCADAZSCD0001 | [6 empty] | AEIV | aeiAAAPSCADAZSCD0001-691
|  |  |  | AAA |  | PSCADA | 1500V | ZSCD | 杂散电流监测点 |  | 极化瞬时值 | mV | AI | [105 empty] | PSCADA_ZSCD | POWEquipment | AI | 692 | :R:A:AAA:PSCADA:ZSCD0001 | <alias>AAAPSCADAZSCD0001 | [6 empty] | AEIV | aeiAAAPSCADAZSCD0001-692
|  |  |  | AAA |  | PSCADA | 1500V | ZSCD | 杂散电流监测点 |  | 正向极化平均值 | mV | AI | [105 empty] | PSCADA_ZSCD | POWEquipment | AI | 693 | :R:A:AAA:PSCADA:ZSCD0001 | <alias>AAAPSCADAZSCD0001 | [6 empty] | AEIV | aeiAAAPSCADAZSCD0001-693
|  |  |  | AAA |  | PSCADA | 1500V | ZSCD | 杂散电流监测点 |  | 负向极化平均值 | mV | AI | [105 empty] | PSCADA_ZSCD | POWEquipment | AI | 694 | :R:A:AAA:PSCADA:ZSCD0001 | <alias>AAAPSCADAZSCD0001 | [6 empty] | AEIV | aeiAAAPSCADAZSCD0001-694
|  |  |  | AAA |  | PSCADA | 1500V | ZSCD | 杂散电流监测点 |  | 正向极化最大值 | mV | AI | [105 empty] | PSCADA_ZSCD | POWEquipment | AI | 695 | :R:A:AAA:PSCADA:ZSCD0001 | <alias>AAAPSCADAZSCD0001 | [6 empty] | AEIV | aeiAAAPSCADAZSCD0001-695
|  |  |  | AAA |  | PSCADA | 1500V | ZSCD | 杂散电流监测点 |  | 负向极化最大值 | mV | AI | [105 empty] | PSCADA_ZSCD | POWEquipment | AI | 696 | :R:A:AAA:PSCADA:ZSCD0001 | <alias>AAAPSCADAZSCD0001 | [6 empty] | AEIV | aeiAAAPSCADAZSCD0001-696
|  |  |  | AAA |  | PSCADA | 1500V | ZSCD | 杂散电流监测点 |  | 正向极化最小值 | mV | AI | [105 empty] | PSCADA_ZSCD | POWEquipment | AI | 697 | :R:A:AAA:PSCADA:ZSCD0001 | <alias>AAAPSCADAZSCD0001 | [6 empty] | AEIV | aeiAAAPSCADAZSCD0001-697
|  |  |  | AAA |  | PSCADA | 1500V | ZSCD | 杂散电流监测点 |  | 负向极化最小值 | mV | AI | [105 empty] | PSCADA_ZSCD | POWEquipment | AI | 698 | :R:A:AAA:PSCADA:ZSCD0001 | <alias>AAAPSCADAZSCD0001 | [6 empty] | AEIV | aeiAAAPSCADAZSCD0001-698
|  |  |  | AAA |  | PSCADA | 1500V | ZSCD | 杂散电流监测点 |  | 钢轨电位瞬时值 | mV | AI | [105 empty] | PSCADA_ZSCD | POWEquipment | AI | 699 | :R:A:AAA:PSCADA:ZSCD0001 | <alias>AAAPSCADAZSCD0001 | [6 empty] | AEIV | aeiAAAPSCADAZSCD0001-699
|  |  |  | AAA |  | PSCADA | 1500V | ZSCD | 杂散电流监测点 |  | 钢轨正向最大值 | mV | AI | [105 empty] | PSCADA_ZSCD | POWEquipment | AI | 700 | :R:A:AAA:PSCADA:ZSCD0001 | <alias>AAAPSCADAZSCD0001 | [6 empty] | AEIV | aeiAAAPSCADAZSCD0001-700
|  |  |  | AAA |  | PSCADA | 1500V | ZSCD | 杂散电流监测点 |  | 钢轨负向最大值 | mV | AI | [105 empty] | PSCADA_ZSCD | POWEquipment | AI | 701 | :R:A:AAA:PSCADA:ZSCD0001 | <alias>AAAPSCADAZSCD0001 | [6 empty] | AEIV | aeiAAAPSCADAZSCD0001-701
|  |  |  | AAA |  | PSCADA | 1500V | ZSCD | 杂散电流监测点 |  | 传感器通信状态 |  | DI1 |  | 正常 |  |  |  | 中断 | 1 | [98 empty] | PSCADA_ZSCD | POWEquipment | DI1 | 702 | :R:A:AAA:PSCADA:ZSCD0001 | <alias>AAAPSCADAZSCD0001 | [6 empty] | DEIV | deiAAAPSCADAZSCD0001-702
|  |  |  | AAA |  | PSCADA | 1500V | NFCD | 杂散电流监测点 |  | 极化电压30分钟正向平均值 | mV | AI | [105 empty] | PSCADA_NFCD | POWEquipment | AI | 703 | :R:A:AAA:PSCADA:NFCD0001 | <alias>AAAPSCADANFCD0001 | [6 empty] | AEIV | aeiAAAPSCADANFCD0001-703
|  |  |  | AAA |  | PSCADA | 1500V | NFCD | 杂散电流监测点 |  | 极化电压超限报警 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_NFCD | POWEquipment | DI1 | 704 | :R:A:AAA:PSCADA:NFCD0001 | <alias>AAAPSCADANFCD0001 | [6 empty] | DEIV | deiAAAPSCADANFCD0001-704
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 上行道床排流电流值 | A | AI | [105 empty] | PSCADA_NFZS | POWEquipment | AI | 705 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | AEIV | aeiAAAPSCADANFZS0001-705
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 上行侧壁排流电流值 | A | AI | [105 empty] | PSCADA_NFZS | POWEquipment | AI | 706 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | AEIV | aeiAAAPSCADANFZS0001-706
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 地排流电流值 | A | AI | [105 empty] | PSCADA_NFZS | POWEquipment | AI | 707 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | AEIV | aeiAAAPSCADANFZS0001-707
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 下行道床排流电流值 | A | AI | [105 empty] | PSCADA_NFZS | POWEquipment | AI | 708 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | AEIV | aeiAAAPSCADANFZS0001-708
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 下行侧壁排流电流值 | A | AI | [105 empty] | PSCADA_NFZS | POWEquipment | AI | 709 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | AEIV | aeiAAAPSCADANFZS0001-709
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 上行道床电压值 | V | AI | [105 empty] | PSCADA_NFZS | POWEquipment | AI | 710 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | AEIV | aeiAAAPSCADANFZS0001-710
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 上侧壁床电压值 | V | AI | [105 empty] | PSCADA_NFZS | POWEquipment | AI | 711 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | AEIV | aeiAAAPSCADANFZS0001-711
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 地排流电压值 | V | AI | [105 empty] | PSCADA_NFZS | POWEquipment | AI | 712 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | AEIV | aeiAAAPSCADANFZS0001-712
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 下行道床电压值 | V | AI | [105 empty] | PSCADA_NFZS | POWEquipment | AI | 713 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | AEIV | aeiAAAPSCADANFZS0001-713
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 下行侧壁电压值 | V | AI | [105 empty] | PSCADA_NFZS | POWEquipment | AI | 714 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | AEIV | aeiAAAPSCADANFZS0001-714
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 上行道床排流熔断器熔断 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_NFZS | POWEquipment | DI1 | 715 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | DEIV | deiAAAPSCADANFZS0001-715
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 上行侧壁排流熔断器熔断 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_NFZS | POWEquipment | DI1 | 716 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | DEIV | deiAAAPSCADANFZS0001-716
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 地排流熔断器熔断 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_NFZS | POWEquipment | DI1 | 717 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | DEIV | deiAAAPSCADANFZS0001-717
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 下行道床排流熔断器熔断 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_NFZS | POWEquipment | DI1 | 718 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | DEIV | deiAAAPSCADANFZS0001-718
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 下行侧壁排流熔断器熔断 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_NFZS | POWEquipment | DI1 | 719 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | DEIV | deiAAAPSCADANFZS0001-719
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 上行道床排流IGBT故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_NFZS | POWEquipment | DI1 | 720 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | DEIV | deiAAAPSCADANFZS0001-720
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 上行侧壁排流IGBT故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_NFZS | POWEquipment | DI1 | 721 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | DEIV | deiAAAPSCADANFZS0001-721
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 下行道床排流IGBT故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_NFZS | POWEquipment | DI1 | 722 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | DEIV | deiAAAPSCADANFZS0001-722
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 下行侧壁排流IGBT故障 |  | DI1 |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_NFZS | POWEquipment | DI1 | 723 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | DEIV | deiAAAPSCADANFZS0001-723
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 上行道床排流开关状态 |  | DI1 |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_NFZS | POWEquipment | DI1 | 724 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | DEIV | deiAAAPSCADANFZS0001-724
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 上行侧壁排流开关状态 |  | DI1 |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_NFZS | POWEquipment | DI1 | 725 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | DEIV | deiAAAPSCADANFZS0001-725
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 地排流开关状态 |  | DI1 |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_NFZS | POWEquipment | DI1 | 726 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | DEIV | deiAAAPSCADANFZS0001-726
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 下行道床排流开关状态 |  | DI1 |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_NFZS | POWEquipment | DI1 | 727 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | DEIV | deiAAAPSCADANFZS0001-727
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 下行侧壁排流开关状态 |  | DI1 |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_NFZS | POWEquipment | DI1 | 728 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | DEIV | deiAAAPSCADANFZS0001-728
|  |  |  | AAA |  | PSCADA | 1500V | NFZS | 杂散电流监测装置 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_NFZS | POWEquipment | DI1/SOE | 729 | :R:A:AAA:PSCADA:NFZS0001 | <alias>AAAPSCADANFZS0001 | [6 empty] | DEIV | deiAAAPSCADANFZS0001-729
|  |  |  | AAA |  | PSCADA | 1500V | PLGA | 排流柜 |  | 排流支路1电流 | A | AI | [105 empty] | PSCADA_PLGA | POWEquipment | AI | 730 | :R:A:AAA:PSCADA:PLGA0001 | <alias>AAAPSCADAPLGA0001 | [6 empty] | AEIV | aeiAAAPSCADAPLGA0001-730
|  |  |  | AAA |  | PSCADA | 1500V | PLGA | 排流柜 |  | 排流支路2电流 | A | AI | [105 empty] | PSCADA_PLGA | POWEquipment | AI | 731 | :R:A:AAA:PSCADA:PLGA0001 | <alias>AAAPSCADAPLGA0001 | [6 empty] | AEIV | aeiAAAPSCADAPLGA0001-731
|  |  |  | AAA |  | PSCADA | 1500V | PLGA | 排流柜 |  | 地排流支路1电压 | V | AI | [105 empty] | PSCADA_PLGA | POWEquipment | AI | 732 | :R:A:AAA:PSCADA:PLGA0001 | <alias>AAAPSCADAPLGA0001 | [6 empty] | AEIV | aeiAAAPSCADAPLGA0001-732
|  |  |  | AAA |  | PSCADA | 1500V | PLGA | 排流柜 |  | 地排流支路2电压 | V | AI | [105 empty] | PSCADA_PLGA | POWEquipment | AI | 733 | :R:A:AAA:PSCADA:PLGA0001 | <alias>AAAPSCADAPLGA0001 | [6 empty] | AEIV | aeiAAAPSCADAPLGA0001-733
|  |  |  | AAA |  | PSCADA | 1500V | PLGA | 排流柜 |  | 熔断器1故障 |  | DI1 |  | 恢复 |  |  |  | 故障 | [99 empty] | PSCADA_PLGA | POWEquipment | DI1 | 734 | :R:A:AAA:PSCADA:PLGA0001 | <alias>AAAPSCADAPLGA0001 | [6 empty] | DEIV | deiAAAPSCADAPLGA0001-734
|  |  |  | AAA |  | PSCADA | 1500V | PLGA | 排流柜 |  | 熔断器2故障 |  | DI1 |  | 恢复 |  |  |  | 故障 | [99 empty] | PSCADA_PLGA | POWEquipment | DI1 | 735 | :R:A:AAA:PSCADA:PLGA0001 | <alias>AAAPSCADAPLGA0001 | [6 empty] | DEIV | deiAAAPSCADAPLGA0001-735
|  |  |  | AAA |  | PSCADA | 1500V | PLGA | 排流柜 |  | 排流支路1投入 |  | DI1 |  | 退出 |  |  |  | 投入 | [99 empty] | PSCADA_PLGA | POWEquipment | DI1 | 736 | :R:A:AAA:PSCADA:PLGA0001 | <alias>AAAPSCADAPLGA0001 | [6 empty] | DEIV | deiAAAPSCADAPLGA0001-736
|  |  |  | AAA |  | PSCADA | 1500V | PLGA | 排流柜 |  | 排流支路2投入 |  | DI1 |  | 退出 |  |  |  | 投入 | [99 empty] | PSCADA_PLGA | POWEquipment | DI1 | 737 | :R:A:AAA:PSCADA:PLGA0001 | <alias>AAAPSCADAPLGA0001 | [6 empty] | DEIV | deiAAAPSCADAPLGA0001-737
|  |  |  | AAA |  | PSCADA | 1500V | PLGA | 排流柜 |  | 远方/就地操作方式 |  | DI1 |  | 就地 |  |  |  | 远方 | [99 empty] | PSCADA_PLGA | POWEquipment | DI1 | 738 | :R:A:AAA:PSCADA:PLGA0001 | <alias>AAAPSCADAPLGA0001 | [6 empty] | DEIV | deiAAAPSCADAPLGA0001-738
|  |  |  | AAA |  | PSCADA | 1500V | PLGA | 排流柜 |  | 与PSCADA通信状态 |  | DI1/SOE |  | 正常 |  |  |  | 中断 | 2 | [98 empty] | PSCADA_PLGA | POWEquipment | DI1/SOE | 739 | :R:A:AAA:PSCADA:PLGA0001 | <alias>AAAPSCADAPLGA0001 | [6 empty] | DEIV | deiAAAPSCADAPLGA0001-739
|  |  |  | AAA |  | PSCADA | 1500V | PLGA | 排流柜 |  | 排流1支路投入/退出 |  | DO2 | [5 empty] | 退出 |  |  |  | 投入 | [95 empty] | PSCADA_PLGA | POWEquipment | DO2 | 740 | :R:A:AAA:PSCADA:PLGA0001 | <alias>AAAPSCADAPLGA0001 | [6 empty] | DEOV | deoAAAPSCADAPLGA0001-740
|  |  |  | AAA |  | PSCADA | 1500V | PLGA | 排流柜 |  | 排流2支路投入/退出 |  | DO2 | [5 empty] | 退出 |  |  |  | 投入 | [95 empty] | PSCADA_PLGA | POWEquipment | DO2 | 741 | :R:A:AAA:PSCADA:PLGA0001 | <alias>AAAPSCADAPLGA0001 | [6 empty] | DEOV | deoAAAPSCADAPLGA0001-741
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 一重模块交流电流Ia1 | A | AI | [105 empty] | PSCADA_NBGA | POWEquipment | AI | 742 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | AEIV | aeiAAAPSCADANBGA0001-742
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 一重模块交流电流Ib1 | A | AI | [105 empty] | PSCADA_NBGA | POWEquipment | AI | 743 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | AEIV | aeiAAAPSCADANBGA0001-743
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 一重模块交流电流Ic1 | A | AI | [105 empty] | PSCADA_NBGA | POWEquipment | AI | 744 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | AEIV | aeiAAAPSCADANBGA0001-744
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 一重直流电流Id1 | A | AI | [105 empty] | PSCADA_NBGA | POWEquipment | AI | 745 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | AEIV | aeiAAAPSCADANBGA0001-745
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 二重模块交流电流Ia2 | A | AI | [105 empty] | PSCADA_NBGA | POWEquipment | AI | 746 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | AEIV | aeiAAAPSCADANBGA0001-746
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 二重模块交流电流Ib2 | A | AI | [105 empty] | PSCADA_NBGA | POWEquipment | AI | 747 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | AEIV | aeiAAAPSCADANBGA0001-747
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 二重模块交流电流Ic2 | A | AI | [105 empty] | PSCADA_NBGA | POWEquipment | AI | 748 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | AEIV | aeiAAAPSCADANBGA0001-748
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 二重直流电流Id2 | A | AI | [105 empty] | PSCADA_NBGA | POWEquipment | AI | 749 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | AEIV | aeiAAAPSCADANBGA0001-749
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 中间直流电压Ud | V | AI | [105 empty] | PSCADA_NBGA | POWEquipment | AI | 750 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | AEIV | aeiAAAPSCADANBGA0001-750
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 牵引网压Unet | V | AI | [105 empty] | PSCADA_NBGA | POWEquipment | AI | 751 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | AEIV | aeiAAAPSCADANBGA0001-751
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 一重模块温度T1 | ℃ | AI | [105 empty] | PSCADA_NBGA | POWEquipment | AI | 752 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | AEIV | aeiAAAPSCADANBGA0001-752
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 二重模块温度T2 | ℃ | AI | [105 empty] | PSCADA_NBGA | POWEquipment | AI | 753 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | AEIV | aeiAAAPSCADANBGA0001-753
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 回馈电能 | kWh | AI | [105 empty] | PSCADA_NBGA | POWEquipment | AI | 754 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | AEIV | aeiAAAPSCADANBGA0001-754
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 充电接触器KM1状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 755 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-755
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 断路器QF950A状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 756 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-756
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 断路器QF950B状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 757 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-757
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 风机接触器状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 758 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-758
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 风机断路器状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 759 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-759
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 断路器QF950A合位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 760 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-760
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 断路器QF950A分位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 761 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-761
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 断路器QF950B合位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 762 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-762
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 断路器QF950B分位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 763 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-763
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 1500V断路器215合位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 764 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-764
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 1500V断路器215分位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 765 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-765
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 冷却风机接触器合位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 766 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-766
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 冷却风机接触器分位失败 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 767 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-767
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 充电接触器合位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 768 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-768
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 充电接触器分位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 769 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-769
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 冷却风机断路器QMF跳闸 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 770 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-770
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 框架保护 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 771 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-771
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | AC380V电源掉电保护 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 772 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-772
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | DCU与逆变模块1通讯异常 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 773 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-773
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | DCU与逆变模块2通讯异常 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 774 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-774
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 一支路逆变模块保护 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 775 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-775
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 二支路逆变模块保护 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 776 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-776
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 一支路模块超温 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 777 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-777
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 二支路模块超温 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 778 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-778
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 两支路间电流不平衡 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 779 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-779
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 一支路三相电流不平衡 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 780 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-780
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 二支路三相电流不平衡 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 781 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-781
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 一支路交流过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 782 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-782
|  |  |  | AAA |  | PSCADA | 能馈 | NBGA | 逆变柜 |  | 二支路交流过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NBGA | POWEquipment | DI | 783 | :R:A:AAA:PSCADA:NBGA0001 | <alias>AAAPSCADANBGA0001 | [6 empty] | DEIV | deiAAAPSCADANBGA0001-783
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 断路器501状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 784 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-784
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 断路器502状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 785 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-785
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 能馈装置工作模式 |  | DI |  | 运营 | 运营 |  |  | 调试 | 2 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 786 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-786
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 能馈装置控制模式 |  | DI |  | 就地 |  |  |  | 远方 | 2 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 787 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-787
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 能馈装置退出工况 |  | DI |  | 无意义 |  |  |  | 退出 | 2 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 788 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-788
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 能馈装置投入工况 |  | DI |  | 无意义 |  |  |  | 投入 | 2 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 789 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-789
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 总故障信号 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 790 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-790
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 总报警信号 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 791 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-791
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 断路器501合位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 792 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-792
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 断路器501分位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 793 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-793
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 断路器502合位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 794 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-794
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 断路器502分位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 795 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-795
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 35kV断路器321异常分断 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 796 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-796
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 门联锁报警 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 797 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-797
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 充电超时 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 798 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-798
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 电流反向保护 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 799 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-799
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 联跳35kV断路器321失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 800 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-800
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 参数设置错误 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 801 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-801
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 35kV母线过压 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 802 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-802
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 35kV母线欠压 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 803 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-803
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 35kV母线失电 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 804 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-804
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 35kV母线频率异常 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 805 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-805
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 直流母线网压I级过压 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 806 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-806
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 直流母线网压II级过压 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 807 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-807
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 直流母线网压欠压 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 808 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-808
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 直流过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 809 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-809
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 1180V侧一支路过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 810 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-810
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 1180V侧二支路过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 811 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-811
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | PLC与DCU通讯异常 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 812 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-812
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 框架电压保护报警 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 813 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-813
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 框架电压保护跳闸 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 814 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-814
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 框架电流保护报警 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 815 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-815
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 框架电流保护跳闸 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_BWKG | POWEquipment | DI | 816 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEIV | deiAAAPSCADABWKG0001-816
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 系统投退遥控指令 |  | DO2 | [5 empty] | 退出 |  |  |  | 投入 | [95 empty] | PSCADA_BWKG | POWEquipment | DO2 | 817 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEOV | deoAAAPSCADABWKG0001-817
|  |  |  | AAA |  | PSCADA | 能馈 | BWKG | 并网开关柜 |  | 系统复位遥控指令 |  | DO2 | [9 empty] | 复归 | [95 empty] | PSCADA_BWKG | POWEquipment | DO2 | 818 | :R:A:AAA:PSCADA:BWKG0001 | <alias>AAAPSCADABWKG0001 | [6 empty] | DEOV | deoAAAPSCADABWKG0001-818
|  |  |  | AAA |  | PSCADA | 能馈 | NKKG | 能馈控制柜 |  | 电动隔离开关2031状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_NKKG | POWEquipment | DI | 819 | :R:A:AAA:PSCADA:NKKG0001 | <alias>AAAPSCADANKKG0001 | [6 empty] | DEIV | deiAAAPSCADANKKG0001-819
|  |  |  | AAA |  | PSCADA | 能馈 | NKKG | 能馈控制柜 |  | 本地复位信号 |  | DI |  | 无意义 |  |  |  | 复位 | 2 | [98 empty] | PSCADA_NKKG | POWEquipment | DI | 820 | :R:A:AAA:PSCADA:NKKG0001 | <alias>AAAPSCADANKKG0001 | [6 empty] | DEIV | deiAAAPSCADANKKG0001-820
|  |  |  | AAA |  | PSCADA | 能馈 | NKKG | 能馈控制柜 |  | 电动隔离开关2031合位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NKKG | POWEquipment | DI | 821 | :R:A:AAA:PSCADA:NKKG0001 | <alias>AAAPSCADANKKG0001 | [6 empty] | DEIV | deiAAAPSCADANKKG0001-821
|  |  |  | AAA |  | PSCADA | 能馈 | NKKG | 能馈控制柜 |  | 电动隔离开关2031分位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NKKG | POWEquipment | DI | 822 | :R:A:AAA:PSCADA:NKKG0001 | <alias>AAAPSCADANKKG0001 | [6 empty] | DEIV | deiAAAPSCADANKKG0001-822
|  |  |  | AAA |  | PSCADA | 能馈 | NKKG | 能馈控制柜 |  | 紧急停机 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_NKKG | POWEquipment | DI | 823 | :R:A:AAA:PSCADA:NKKG0001 | <alias>AAAPSCADANKKG0001 | [6 empty] | DEIV | deiAAAPSCADANKKG0001-823
|  |  |  | AAA |  | PSCADA | 能馈 | NKKG | 能馈控制柜 |  | 电抗器超温报警 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_NKKG | POWEquipment | DI | 824 | :R:A:AAA:PSCADA:NKKG0001 | <alias>AAAPSCADANKKG0001 | [6 empty] | DEIV | deiAAAPSCADANKKG0001-824
|  |  |  | AAA |  | PSCADA | 能馈 | NKKG | 能馈控制柜 |  | 电抗器超温跳闸 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_NKKG | POWEquipment | DI | 825 | :R:A:AAA:PSCADA:NKKG0001 | <alias>AAAPSCADANKKG0001 | [6 empty] | DEIV | deiAAAPSCADANKKG0001-825
|  |  |  | AAA |  | PSCADA | 能馈 | GLBY | 隔离变压器 |  | 隔离变压器A相温度 | ℃ | AI | [105 empty] | PSCADA_GLBY | POWEquipment | AI | 826 | :R:A:AAA:PSCADA:GLBY0001 | <alias>AAAPSCADAGLBY0001 | [6 empty] | AEIV | aeiAAAPSCADAGLBY0001-826
|  |  |  | AAA |  | PSCADA | 能馈 | GLBY | 隔离变压器 |  | 隔离变压器B相温度 | ℃ | AI | [105 empty] | PSCADA_GLBY | POWEquipment | AI | 827 | :R:A:AAA:PSCADA:GLBY0001 | <alias>AAAPSCADAGLBY0001 | [6 empty] | AEIV | aeiAAAPSCADAGLBY0001-827
|  |  |  | AAA |  | PSCADA | 能馈 | GLBY | 隔离变压器 |  | 隔离变压器C相温度 | ℃ | AI | [105 empty] | PSCADA_GLBY | POWEquipment | AI | 828 | :R:A:AAA:PSCADA:GLBY0001 | <alias>AAAPSCADAGLBY0001 | [6 empty] | AEIV | aeiAAAPSCADAGLBY0001-828
|  |  |  | AAA |  | PSCADA | 能馈 | GLBY | 隔离变压器 |  | 隔离变压器铁芯温度 | ℃ | AI | [105 empty] | PSCADA_GLBY | POWEquipment | AI | 829 | :R:A:AAA:PSCADA:GLBY0001 | <alias>AAAPSCADAGLBY0001 | [6 empty] | AEIV | aeiAAAPSCADAGLBY0001-829
|  |  |  | AAA |  | PSCADA | 能馈 | GLBY | 隔离变压器 |  | 隔离变压器风机运行状态 |  | DI |  | 停止 |  |  |  | 运行 | 2 | [98 empty] | PSCADA_GLBY | POWEquipment | DI | 830 | :R:A:AAA:PSCADA:GLBY0001 | <alias>AAAPSCADAGLBY0001 | [6 empty] | DEIV | deiAAAPSCADAGLBY0001-830
|  |  |  | AAA |  | PSCADA | 能馈 | GLBY | 隔离变压器 |  | 隔离变压器绕组超温报警 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_GLBY | POWEquipment | DI | 831 | :R:A:AAA:PSCADA:GLBY0001 | <alias>AAAPSCADAGLBY0001 | [6 empty] | DEIV | deiAAAPSCADAGLBY0001-831
|  |  |  | AAA |  | PSCADA | 能馈 | GLBY | 隔离变压器 |  | 隔离变压器绕组超温跳闸 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_GLBY | POWEquipment | DI | 832 | :R:A:AAA:PSCADA:GLBY0001 | <alias>AAAPSCADAGLBY0001 | [6 empty] | DEIV | deiAAAPSCADAGLBY0001-832
|  |  |  | AAA |  | PSCADA | 能馈 | GLBY | 隔离变压器 |  | 隔离变压器铁芯超温报警 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_GLBY | POWEquipment | DI | 833 | :R:A:AAA:PSCADA:GLBY0001 | <alias>AAAPSCADAGLBY0001 | [6 empty] | DEIV | deiAAAPSCADAGLBY0001-833
|  |  |  | AAA |  | PSCADA | 能馈 | GLBY | 隔离变压器 |  | 隔离变压器风机故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_GLBY | POWEquipment | DI | 834 | :R:A:AAA:PSCADA:GLBY0001 | <alias>AAAPSCADAGLBY0001 | [6 empty] | DEIV | deiAAAPSCADAGLBY0001-834
|  |  |  | AAA |  | PSCADA | 能馈 | GLBY | 隔离变压器 |  | 隔离变压器温控装置故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_GLBY | POWEquipment | DI | 835 | :R:A:AAA:PSCADA:GLBY0001 | <alias>AAAPSCADAGLBY0001 | [6 empty] | DEIV | deiAAAPSCADAGLBY0001-835
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 中间直流电压Ud | V | AI | [105 empty] | PSCADA_MLKZ | POWEquipment | AI | 836 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | AEIV | aeiAAAPSCADAMLKZ0001-836
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 牵引网压Unet | V | AI | [105 empty] | PSCADA_MLKZ | POWEquipment | AI | 837 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | AEIV | aeiAAAPSCADAMLKZ0001-837
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 回馈电能 | kWh | AI | [105 empty] | PSCADA_MLKZ | POWEquipment | AI | 838 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | AEIV | aeiAAAPSCADAMLKZ0001-838
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 牵引电能 | kWh | AI | [105 empty] | PSCADA_MLKZ | POWEquipment | AI | 839 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | AEIV | aeiAAAPSCADAMLKZ0001-839
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 充电接触器KM3状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 840 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-840
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 风机接触器状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 841 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-841
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 风机断路器状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 842 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-842
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 电动隔离开关QS状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 843 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-843
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 能馈装置工作模式 |  | DI |  | 运营 |  |  |  | 调试 | 3 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 844 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-844
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 能馈装置控制模式 |  | DI |  | 就地 |  |  |  | 远方 | 3 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 845 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-845
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 能馈装置退出工况 |  | DI |  | 无意义 |  |  |  | 退出 | 2 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 846 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-846
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 能馈装置投入工况 |  | DI |  | 无意义 |  |  |  | 投入 | 2 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 847 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-847
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 总故障信号 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 848 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-848
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 总报警信号 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 849 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-849
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 本地复位信号 |  | DI |  | 无意义 |  |  |  | 复位 | 2 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 850 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-850
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 冷却风机接触器合位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 851 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-851
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 冷却风机接触器分位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 852 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-852
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 充电接触器合位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 853 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-853
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 充电接触器分位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 854 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-854
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 电动隔离开关QS合位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 855 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-855
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 电动隔离开关QS分位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 856 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-856
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 冷却风机断路器QMF跳闸 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 857 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-857
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 充电断路器QA10跳闸 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 858 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-858
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 门联锁报警 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 859 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-859
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 漏电保护 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 860 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-860
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | AC380V电源掉电保护 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 861 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-861
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 充电超时 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 862 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-862
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 紧急停机 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 863 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-863
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 参数设置错误 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 864 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-864
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 35kV母线过压 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 865 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-865
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 35kV母线欠压 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 866 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-866
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 35kV母线失电 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 867 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-867
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 35kV母线频率异常 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 868 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-868
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 直流母线网压I级过压 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 869 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-869
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 直流母线网压II级过压 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 870 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-870
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 直流母线网压欠压 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 871 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-871
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 四重支路间电流不平衡 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 872 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-872
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | PLC与DCU通讯异常 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 873 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-873
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 框架电压保护报警 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 874 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-874
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 框架电压保护跳闸 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 875 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-875
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 框架电流保护报警 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 876 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-876
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 框架电流保护跳闸 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 877 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-877
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 1500V断路器215分位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 878 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-878
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 1500V断路器215合位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 879 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-879
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 35kV断路器326分位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 880 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-880
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 35kV断路器326合位失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 881 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-881
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 充电断路器QA10状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 882 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-882
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 锁相失败 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_MLKZ | POWEquipment | DI | 883 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEIV | deiAAAPSCADAMLKZ0001-883
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 系统投退遥控指令 |  | DO2 | [5 empty] | 退出 |  |  |  | 投入 | [95 empty] | PSCADA_MLKZ | POWEquipment | DO2 | 884 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEOV | deoAAAPSCADAMLKZ0001-884
|  |  |  | AAA |  | PSCADA | 能馈 | MLKZ | 能馈控制柜 |  | 系统复位遥控指令 |  | DO2 | [9 empty] | 复归 | [95 empty] | PSCADA_MLKZ | POWEquipment | DO2 | 885 | :R:A:AAA:PSCADA:MLKZ0001 | <alias>AAAPSCADAMLKZ0001 | [6 empty] | DEOV | deoAAAPSCADAMLKZ0001-885
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 一重模块交流电流Ia1 | A | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 886 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-886
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 一重模块交流电流Ib1 | A | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 887 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-887
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 一重模块交流电流Ic1 | A | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 888 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-888
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 一重直流电流Id1 | A | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 889 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-889
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 二重模块交流电流Ia2 | A | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 890 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-890
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 二重模块交流电流Ib2 | A | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 891 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-891
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 二重模块交流电流Ic2 | A | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 892 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-892
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 二重直流电流Id2 | A | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 893 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-893
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 一重模块温度T1 | ℃ | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 894 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-894
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 二重模块温度T2 | ℃ | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 895 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-895
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | DCU与逆变模块1通讯异常 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 896 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-896
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | DCU与逆变模块2通讯异常 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 897 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-897
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 一支路逆变模块保护 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 898 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-898
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 二支路逆变模块保护 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 899 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-899
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 一支路模块超温 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 900 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-900
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 二支路模块超温 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 901 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-901
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 一支路直流侧过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 902 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-902
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 二支路直流侧过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 903 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-903
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 一支路三相电流不平衡 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 904 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-904
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 二支路三相电流不平衡 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 905 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-905
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 一支路交流过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 906 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-906
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 二支路交流过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 907 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-907
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 一重变流柜三相电抗器超温 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 908 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-908
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 三重模块交流电流Ia3 | A | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 909 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-909
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 三重模块交流电流Ib3 | A | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 910 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-910
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 三重模块交流电流Ic3 | A | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 911 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-911
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 三重直流电流Id3 | A | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 912 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-912
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 四重模块交流电流Ia4 | A | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 913 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-913
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 四重模块交流电流Ib4 | A | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 914 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-914
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 四重模块交流电流Ic4 | A | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 915 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-915
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 四重直流电流Id4 | A | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 916 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-916
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 三重模块温度T3 | ℃ | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 917 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-917
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 四重模块温度T4 | ℃ | AI | [105 empty] | PSCADA_MLNB | POWEquipment | AI | 918 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | AEIV | aeiAAAPSCADAMLNB0001-918
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | DCU与逆变模块3通讯异常 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 919 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-919
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | DCU与逆变模块4通讯异常 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 920 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-920
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 三支路逆变模块保护 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 921 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-921
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 四支路逆变模块保护 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 922 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-922
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 三支路模块超温 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 923 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-923
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 四支路模块超温 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 924 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-924
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 三支路直流侧过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 925 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-925
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 四支路直流侧过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 926 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-926
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 三支路三相电流不平衡 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 927 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-927
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 四支路三相电流不平衡 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 928 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-928
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 三支路交流过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 929 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-929
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 四支路交流过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 930 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-930
|  |  |  | AAA |  | PSCADA | 能馈 | MLNB | 逆变柜 |  | 二重变流柜三相电抗器超温 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_MLNB | POWEquipment | DI | 931 | :R:A:AAA:PSCADA:MLNB0001 | <alias>AAAPSCADAMLNB0001 | [6 empty] | DEIV | deiAAAPSCADAMLNB0001-931
|  |  |  | AAA |  | PSCADA | 能馈 | YHKZ | 能馈控制柜 |  | DC1500V断路器215合闸失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_YHKZ | POWEquipment | DI | 932 | :R:A:AAA:PSCADA:YHKZ0001 | <alias>AAAPSCADAYHKZ0001 | [6 empty] | DEIV | deiAAAPSCADAYHKZ0001-932
|  |  |  | AAA |  | PSCADA | 能馈 | YHKZ | 能馈控制柜 |  | DC1500V断路器215分闸失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_YHKZ | POWEquipment | DI | 933 | :R:A:AAA:PSCADA:YHKZ0001 | <alias>AAAPSCADAYHKZ0001 | [6 empty] | DEIV | deiAAAPSCADAYHKZ0001-933
|  |  |  | AAA |  | PSCADA | 能馈 | YHKZ | 能馈控制柜 |  | 辅助电源掉电故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHKZ | POWEquipment | DI | 934 | :R:A:AAA:PSCADA:YHKZ0001 | <alias>AAAPSCADAYHKZ0001 | [6 empty] | DEIV | deiAAAPSCADAYHKZ0001-934
|  |  |  | AAA |  | PSCADA | 能馈 | YHKZ | 能馈控制柜 |  | 急停 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_YHKZ | POWEquipment | DI | 935 | :R:A:AAA:PSCADA:YHKZ0001 | <alias>AAAPSCADAYHKZ0001 | [6 empty] | DEIV | deiAAAPSCADAYHKZ0001-935
|  |  |  | AAA |  | PSCADA | 能馈 | YHKZ | 能馈控制柜 |  | 隔离开关分闸失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_YHKZ | POWEquipment | DI | 936 | :R:A:AAA:PSCADA:YHKZ0001 | <alias>AAAPSCADAYHKZ0001 | [6 empty] | DEIV | deiAAAPSCADAYHKZ0001-936
|  |  |  | AAA |  | PSCADA | 能馈 | YHKZ | 能馈控制柜 |  | 隔离开关合闸失败 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_YHKZ | POWEquipment | DI | 937 | :R:A:AAA:PSCADA:YHKZ0001 | <alias>AAAPSCADAYHKZ0001 | [6 empty] | DEIV | deiAAAPSCADAYHKZ0001-937
|  |  |  | AAA |  | PSCADA | 能馈 | YHKZ | 能馈控制柜 |  | 逆变柜工作模式 |  | DI |  | 运营 |  |  |  | 调试 | 3 | [98 empty] | PSCADA_YHKZ | POWEquipment | DI | 938 | :R:A:AAA:PSCADA:YHKZ0001 | <alias>AAAPSCADAYHKZ0001 | [6 empty] | DEIV | deiAAAPSCADAYHKZ0001-938
|  |  |  | AAA |  | PSCADA | 能馈 | YHKZ | 能馈控制柜 |  | 逆变柜控制方式 |  | DI |  | 就地 |  |  |  | 远方 | 3 | [98 empty] | PSCADA_YHKZ | POWEquipment | DI | 939 | :R:A:AAA:PSCADA:YHKZ0001 | <alias>AAAPSCADAYHKZ0001 | [6 empty] | DEIV | deiAAAPSCADAYHKZ0001-939
|  |  |  | AAA |  | PSCADA | 能馈 | YHKZ | 能馈控制柜 |  | 逆变柜运行状态 |  | DI |  | 无意义 |  |  |  | 退出 | 3 |  |  | 待机 | 3 |  |  | 整流 | 3 |  |  | 逆变 | 3 |  |  | 故障 | 3 | [82 empty] | PSCADA_YHKZ | POWEquipment | DI | 940 | :R:A:AAA:PSCADA:YHKZ0001 | <alias>AAAPSCADAYHKZ0001 | [6 empty] | DEIV | deiAAAPSCADAYHKZ0001-940
|  |  |  | AAA |  | PSCADA | 能馈 | YHKZ | 能馈控制柜 |  | 逆变柜运行状态 |  | DI |  | 无意义 |  |  |  | 待机 | 3 | [98 empty] | PSCADA_YHKZ | POWEquipment | DI | 940 | :R:A:AAA:PSCADA:YHKZ0002 | <alias>AAAPSCADAYHKZ0002 | [6 empty] | DEIV | deiAAAPSCADAYHKZ0002-940
|  |  |  | AAA |  | PSCADA | 能馈 | YHKZ | 能馈控制柜 |  | 逆变柜运行状态 |  | DI |  | 无意义 |  |  |  | 整流 | 3 | [98 empty] | PSCADA_YHKZ | POWEquipment | DI | 940 | :R:A:AAA:PSCADA:YHKZ0003 | <alias>AAAPSCADAYHKZ0003 | [6 empty] | DEIV | deiAAAPSCADAYHKZ0003-940
|  |  |  | AAA |  | PSCADA | 能馈 | YHKZ | 能馈控制柜 |  | 逆变柜运行状态 |  | DI |  | 无意义 |  |  |  | 逆变 | 3 | [98 empty] | PSCADA_YHKZ | POWEquipment | DI | 940 | :R:A:AAA:PSCADA:YHKZ0004 | <alias>AAAPSCADAYHKZ0004 | [6 empty] | DEIV | deiAAAPSCADAYHKZ0004-940
|  |  |  | AAA |  | PSCADA | 能馈 | YHKZ | 能馈控制柜 |  | 逆变柜运行状态 |  | DI |  | 无意义 |  |  |  | 故障 | 3 | [98 empty] | PSCADA_YHKZ | POWEquipment | DI | 940 | :R:A:AAA:PSCADA:YHKZ0005 | <alias>AAAPSCADAYHKZ0005 | [6 empty] | DEIV | deiAAAPSCADAYHKZ0005-940
|  |  |  | AAA |  | PSCADA | 能馈 | YHKZ | 能馈控制柜 |  | DC1500V断路器215状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_YHKZ | POWEquipment | DI | 945 | :R:A:AAA:PSCADA:YHKZ0001 | <alias>AAAPSCADAYHKZ0001 | [6 empty] | DEIV | deiAAAPSCADAYHKZ0001-945
|  |  |  | AAA |  | PSCADA | 能馈 | YHKZ | 能馈控制柜 |  | 隔离开关状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_YHKZ | POWEquipment | DI | 946 | :R:A:AAA:PSCADA:YHKZ0001 | <alias>AAAPSCADAYHKZ0001 | [6 empty] | DEIV | deiAAAPSCADAYHKZ0001-946
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | A相电压 | V | AI | [105 empty] | PSCADA_YHNB | POWEquipment | AI | 947 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | AEIV | aeiAAAPSCADAYHNB0001-947
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | B相电压 | V | AI | [105 empty] | PSCADA_YHNB | POWEquipment | AI | 948 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | AEIV | aeiAAAPSCADAYHNB0001-948
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | C相电压 | V | AI | [105 empty] | PSCADA_YHNB | POWEquipment | AI | 949 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | AEIV | aeiAAAPSCADAYHNB0001-949
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | A相电流 | A | AI | [105 empty] | PSCADA_YHNB | POWEquipment | AI | 950 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | AEIV | aeiAAAPSCADAYHNB0001-950
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | B相电流 | A | AI | [105 empty] | PSCADA_YHNB | POWEquipment | AI | 951 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | AEIV | aeiAAAPSCADAYHNB0001-951
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | C相电流 | A | AI | [105 empty] | PSCADA_YHNB | POWEquipment | AI | 952 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | AEIV | aeiAAAPSCADAYHNB0001-952
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 直流电压 | V | AI | [105 empty] | PSCADA_YHNB | POWEquipment | AI | 953 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | AEIV | aeiAAAPSCADAYHNB0001-953
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 直流电流 | A | AI | [105 empty] | PSCADA_YHNB | POWEquipment | AI | 954 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | AEIV | aeiAAAPSCADAYHNB0001-954
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 框架保护 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 955 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-955
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 35kV交流电网过压 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 956 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-956
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 35kV交流电网欠压 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 957 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-957
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 35kV交流电网频率异常 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 958 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-958
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 逆变柜冷却风机故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 959 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-959
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 35kV断路器325状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 960 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-960
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 逆变柜预充故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 961 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-961
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 35kV断路器325合闸失败 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 962 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-962
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 35kV断路器325失败 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 963 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-963
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 直流电网过压Ⅰ级 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 964 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-964
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 直流电网过压Ⅱ级 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 965 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-965
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 直流电网欠压Ⅰ级 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 966 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-966
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 直流电网欠压Ⅱ级 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 967 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-967
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 直流电流过流Ⅰ段 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 968 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-968
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 直流电流过流Ⅱ段 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 969 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-969
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 交流电流过流Ⅰ段 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 970 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-970
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 交流电流过流Ⅱ段 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 971 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-971
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 逆变柜1#进线三相电流不平衡 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 972 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-972
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 逆变柜门联锁信号 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 973 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-973
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 逆变柜2#进线三相电流不平衡 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 974 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-974
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 逆变柜1#逆变模块故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 975 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-975
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 逆变柜2#逆变模块故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 976 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-976
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 逆变柜3#逆变模块故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 977 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-977
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 逆变柜4#逆变模块故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 978 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-978
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 逆变柜5#逆变模块故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 979 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-979
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 逆变柜6#逆变模块故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 980 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-980
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 逆变柜1#逆变模块超温 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 981 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-981
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 逆变柜2#逆变模块超温 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 982 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-982
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 逆变柜3#逆变模块超温 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 983 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-983
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 逆变柜4#逆变模块超温 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 984 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-984
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 逆变柜5#逆变模块超温 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 985 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-985
|  |  |  | AAA |  | PSCADA | 能馈 | YHNB | 逆变柜 |  | 逆变柜6#逆变模块超温 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHNB | POWEquipment | DI | 986 | :R:A:AAA:PSCADA:YHNB0001 | <alias>AAAPSCADAYHNB0001 | [6 empty] | DEIV | deiAAAPSCADAYHNB0001-986
|  |  |  | AAA |  | PSCADA | 能馈 | YHGB | 隔离变压器 |  | 能馈变压器超温报警 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHGB | POWEquipment | DI | 987 | :R:A:AAA:PSCADA:YHGB0001 | <alias>AAAPSCADAYHGB0001 | [6 empty] | DEIV | deiAAAPSCADAYHGB0001-987
|  |  |  | AAA |  | PSCADA | 能馈 | YHGB | 隔离变压器 |  | 能馈变压器超温跳闸 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_YHGB | POWEquipment | DI | 988 | :R:A:AAA:PSCADA:YHGB0001 | <alias>AAAPSCADAYHGB0001 | [6 empty] | DEIV | deiAAAPSCADAYHGB0001-988
|  |  |  | AAA |  | PSCADA | 能馈 | YHGB | 隔离变压器 |  | 能馈变压器铁芯超温报警 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHGB | POWEquipment | DI | 989 | :R:A:AAA:PSCADA:YHGB0001 | <alias>AAAPSCADAYHGB0001 | [6 empty] | DEIV | deiAAAPSCADAYHGB0001-989
|  |  |  | AAA |  | PSCADA | 能馈 | YHGB | 隔离变压器 |  | 能馈变压器风机故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHGB | POWEquipment | DI | 990 | :R:A:AAA:PSCADA:YHGB0001 | <alias>AAAPSCADAYHGB0001 | [6 empty] | DEIV | deiAAAPSCADAYHGB0001-990
|  |  |  | AAA |  | PSCADA | 能馈 | YHGB | 隔离变压器 |  | 能馈变压器故障报警 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_YHGB | POWEquipment | DI | 991 | :R:A:AAA:PSCADA:YHGB0001 | <alias>AAAPSCADAYHGB0001 | [6 empty] | DEIV | deiAAAPSCADAYHGB0001-991
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 阀侧电压归算值 | V | AI | [105 empty] | PSCADA_CDGL | POWEquipment | AI | 992 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | AEIV | aeiAAAPSCADACDGL0001-992
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 直流网压 | V | AI | [105 empty] | PSCADA_CDGL | POWEquipment | AI | 993 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | AEIV | aeiAAAPSCADACDGL0001-993
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 电容电压 | V | AI | [105 empty] | PSCADA_CDGL | POWEquipment | AI | 994 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | AEIV | aeiAAAPSCADACDGL0001-994
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 斩波待机或运行时，KM1断开 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 995 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-995
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 1500V断路器218状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 996 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-996
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 隔离开关QS状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 997 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-997
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | KM1状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 998 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-998
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | KM2状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 999 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-999
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 隔离开关QS卡合 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 1000 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-1000
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 隔离开关QS卡分 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 1001 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-1001
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 1500V断路器218卡分 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 1002 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-1002
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | KM1卡合 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 1003 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-1003
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | KM1卡分 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 1004 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-1004
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | KM2卡合 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 1005 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-1005
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | KM2卡分 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 1006 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-1006
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 控制电源故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 1007 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-1007
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 网压传感器测量信号偏高故障 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 1008 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-1008
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 网压传感器测量信号偏低故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 1009 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-1009
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 电容传感器1测量信号偏高故障 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 1010 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-1010
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 电容传感器1测量信号偏低故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 1011 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-1011
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 电容传感器2测量信号偏高故障 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 1012 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-1012
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 电容传感器2测量信号偏低故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 1013 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-1013
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 2个电容传感器均故障 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 1014 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-1014
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 电容充电故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 1015 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-1015
|  |  |  | AAA |  | PSCADA | 能馈 | CDGL | 能吸隔离柜 |  | 电容放电故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDGL | POWEquipment | DI | 1016 | :R:A:AAA:PSCADA:CDGL0001 | <alias>AAAPSCADACDGL0001 | [6 empty] | DEIV | deiAAAPSCADACDGL0001-1016
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 总电流 | A | AI | [105 empty] | PSCADA_CDZB | POWEquipment | AI | 1017 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | AEIV | aeiAAAPSCADACDZB0001-1017
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 起斩阀值 | V | AI | [105 empty] | PSCADA_CDZB | POWEquipment | AI | 1018 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | AEIV | aeiAAAPSCADACDZB0001-1018
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | QF跳闸标记序号 |  | AI | [105 empty] | PSCADA_CDZB | POWEquipment | AI | 1019 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | AEIV | aeiAAAPSCADACDZB0001-1019
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 实时斩波占空比 |  | AI | [105 empty] | PSCADA_CDZB | POWEquipment | AI | 1020 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | AEIV | aeiAAAPSCADACDZB0001-1020
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 支路1电流 | A | AI | [105 empty] | PSCADA_CDZB | POWEquipment | AI | 1021 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | AEIV | aeiAAAPSCADACDZB0001-1021
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 支路2电流 | A | AI | [105 empty] | PSCADA_CDZB | POWEquipment | AI | 1022 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | AEIV | aeiAAAPSCADACDZB0001-1022
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 支路3电流 | A | AI | [105 empty] | PSCADA_CDZB | POWEquipment | AI | 1023 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | AEIV | aeiAAAPSCADACDZB0001-1023
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 支路4电流 | A | AI | [105 empty] | PSCADA_CDZB | POWEquipment | AI | 1024 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | AEIV | aeiAAAPSCADACDZB0001-1024
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 支路5电流 | A | AI | [105 empty] | PSCADA_CDZB | POWEquipment | AI | 1025 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | AEIV | aeiAAAPSCADACDZB0001-1025
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 支路6电流 | A | AI | [105 empty] | PSCADA_CDZB | POWEquipment | AI | 1026 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | AEIV | aeiAAAPSCADACDZB0001-1026
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 隔离开关QS遥控指令 |  | DO2 | [5 empty] | 控分 |  |  |  | 控合 | [95 empty] | PSCADA_CDZB | POWEquipment | DO2 | 1027 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEOV | deoAAAPSCADACDZB0001-1027
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 系统复位遥控指令 |  | DO2 | [9 empty] | 复归 | [95 empty] | PSCADA_CDZB | POWEquipment | DO2 | 1028 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEOV | deoAAAPSCADACDZB0001-1028
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 报警指示 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1029 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1029
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 故障指示 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1030 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1030
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | QF允投指示 |  | DI |  | 不允投 |  |  |  | 允投 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1031 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1031
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 远方/就地工作模式 |  | DI |  | 远方 |  |  |  | 就地 | 3 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1032 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1032
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | QS1状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1033 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1033
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | QS2状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1034 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1034
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | QS3状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1035 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1035
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | QS4状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1036 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1036
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | QS5状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1037 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1037
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | QS6状态 |  | DI |  | 分位 |  |  |  | 合位 | 3 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1038 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1038
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 调试模式下上高压 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1039 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1039
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 电容过压故障1 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1040 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1040
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 电容过压故障2 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1041 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1041
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 直流网压过高故障 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1042 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1042
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 直流网压过低故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1043 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1043
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | PT侧电压过高故障 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1044 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1044
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | PT侧电压过低故障 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1045 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1045
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 报警支路数过多 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1046 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1046
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 斩波运行故障1 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1047 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1047
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 斩波运行故障2 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1048 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1048
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 支路1过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1049 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1049
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 支路2过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1050 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1050
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 支路3过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1051 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1051
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 支路4过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1052 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1052
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 支路5过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1053 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1053
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 支路6过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1054 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1054
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 总电流过流 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1055 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1055
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 支路1快熔熔断 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1056 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1056
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 支路2快熔熔断 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1057 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1057
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 支路3快熔熔断 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1058 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1058
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 支路4快熔熔断 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1059 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1059
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 支路5快熔熔断 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1060 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1060
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 支路6快熔熔断 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1061 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1061
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | IGBT1回报故障 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1062 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1062
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | IGBT2回报故障 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1063 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1063
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | IGBT3回报故障 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1064 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1064
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | IGBT4回报故障 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1065 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1065
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | IGBT5回报故障 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1066 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1066
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | IGBT6回报故障 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1067 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1067
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | IGBT模块1过热 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1068 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1068
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | IGBT模块2过热 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1069 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1069
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | IGBT模块3过热 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1070 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1070
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | IGBT1短路故障 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1071 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1071
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | IGBT2短路故障 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1072 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1072
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | IGBT3短路故障 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1073 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1073
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | IGBT4短路故障 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1074 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1074
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | IGBT5短路故障 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1075 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1075
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | IGBT6短路故障 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1076 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1076
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 框架电压保护报警 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1077 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1077
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 框架电压保护跳闸 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1078 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1078
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 框架电流保护报警 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1079 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1079
|  |  |  | AAA |  | PSCADA | 能馈 | CDZB | 能吸斩波柜 |  | 框架电流保护跳闸 |  | DI |  | 复归 |  |  |  | 动作 | 1 | [98 empty] | PSCADA_CDZB | POWEquipment | DI | 1080 | :R:A:AAA:PSCADA:CDZB0001 | <alias>AAAPSCADACDZB0001 | [6 empty] | DEIV | deiAAAPSCADACDZB0001-1080
|  |  |  | AAA |  | PSCADA | 能馈 | CDDZ | 能吸电阻柜 |  | 电阻柜温度超过200 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDDZ | POWEquipment | DI | 1081 | :R:A:AAA:PSCADA:CDDZ0001 | <alias>AAAPSCADACDDZ0001 | [6 empty] | DEIV | deiAAAPSCADACDDZ0001-1081
|  |  |  | AAA |  | PSCADA | 能馈 | CDDZ | 能吸电阻柜 |  | 电阻柜温度超过220 |  | DI |  | 恢复 |  |  |  | 报警 | 2 | [98 empty] | PSCADA_CDDZ | POWEquipment | DI | 1082 | :R:A:AAA:PSCADA:CDDZ0001 | <alias>AAAPSCADACDDZ0001 | [6 empty] | DEIV | deiAAAPSCADACDDZ0001-1082
|  |  |  | AAA |  | PSCADA | 能馈 | CDDZ | 能吸电阻柜 |  | 电阻柜温度超过235 |  | DI |  | 恢复 |  |  |  | 报警 | 2

## Note
Column Name | Column Description 描述 | Respond Party
Equipment Location 设备所在地 | Description of the location of equipment in layout 设备在布局图中的位置描述 | Column shoud be filled by Contractor 子系统合同商应填写的列
Equipment Type Code 设备类代码 | Equipment Code identifies the type equipment. Should be on 4 characters 代表设备类型的设备代码,应为4个字符.
HMI Equipment Label 装置标签描述 | Equipment lable display in HMI. The length of label should within 10 characters. 在人机界面中显示出来的设备装置标签.标签长度应小于10个字符.
Equipment Code 设备编码 | HMI显示的设备编码，同设计图纸上设备编码
Equipment Description 设备描述 | HMI显示的设备名称，同设计图纸上设备名称
Mode Command 模式指令 | The BAS mode triggered after received the FAS alarm. (Using for FAS IO only) 在接收到FAS报警后触发的BAS模式 (仅用于FAS IO)
Attribute Description 属性描述 （中文) | Any meaningful text describing the attribute of the equipment. 设备属性的文字描述
Digital Meaning Type 数字表示类型 | Input Digital Meaning Type. For the digital signal, it is the text associated if the value is at 0,1… i.e. 0 = Open, 1 Close. 输入数字表示类型. 对于数字信号, 当输入值为0,1…时对应的文字描述. 例如: 0 = 开, 1 = 关.
IO type Analog/Digital - Input/Output IO 类型 | Specify the type of point: DI, DO: Digital input/output AI, AO: Analog input/output SI, SO: Structure input/output for non-standard exchange (messages, Alarm Text…) 输入输出点的类型描述: DI, DO: 数字输入/输出 AI, AO: 模拟输入/输出 SI, SO: 结构输入/输出, 针对非标准的交换信息(信息,报警文本...)
Register Address 寄存器地址 | Register address shall be filled with according to the protocol design document. 应根据协议设计文档填写寄存器地址.
Register Bit / Bit number 寄存器比特 / 比特号 | Bit number for representing the equipment status/Alarm. 标识设备状态/报警的比特号.
Related AutoCAD Drawing name 对应的图纸名 | The drawing name that subsystem equipment location could be found 描述子系统设备位置的图纸名
Analog valid range Min before scale 度量前模拟有效范围最低值 | The minimum value send to ISCS before scalling 度量前发送给ISCS系统的最低值
Analog valid range Max before scale 度量前模拟有效范围最高值 | The maximum value send to ISCS before scalling 度量前发送给ISCS系统的最高值
Analog scale(a) = (Value+b)*a 模拟度量 | The scale used to calculate the figures for analog in ISCS. (Analog value displayed in HMI= Analog valid range * Analog scaling) 在ISCS中显示的模拟量的度量值. (人机界面中显示的模拟量值=模拟量有效值*模拟度量)
Jitter Factor 抖动量 | Jitter Factor is a numberical range for analog point that determinating whether the value updating in MMI and recorded in ISCS. Normally, it is should be defined as 0.2% of the maximun analog valid range after scaled. 抖动值是一个模拟点的数字范围,供以决定是否在人机界面中显示或在ISCS中记录其值的变化.一般来说,抖动值定义为度量后的最大有效值的0.2%.
Lower Alarm Limit 报警下限 | For analogue input point only: designed for alarm triggering when the value below the defults limits 仅针对模拟输入点: 当点值低于限制,触发报警.
Upper Alarm Limit 报警上限 | For analogue input point only: designed for alarm triggering when the value over the defults limits 仅针对模拟输入点: 当点值高于限制,触发报警.
Accuracy 精确度 | For analogue input point only: Designed for number of decemial place that display in HMI. (eg. X.XX) 仅针对模拟输入点: 指定在人机界面中显示的小数点后的位数.
Analog Unit 模拟单位 | Only need to input if IO Type is Analog (i.e. AI, AO) 只针对输入/输出点类型为模拟量的点(如AI, AO)。 Please input in English. 请用英文输入。 Analog unit is the unit used by Analog input/output. e.g. 模拟单位为模拟输入/输出使用的单位， 如 - No unit/无单位 - Voltage/伏特 - Amps /安培 - 1000 V/千伏
Severity 严重读 | 0：Equipment Failure Alarm设备故障告警，提示维护人员及时处理。 1：Emergency Alarm,only including fire alarm and PSCADA important keys (e.g. 10KV,750V,400V keys) shutting down 紧急报警，仅限于火灾报警、供电系统关键设备（例如10kV、750V、400V开关）发生跳闸事故。 2：Accident Alarm,operators must treat at once.For example, the key systerm or equipment failure which makes trains or lines not operate.事故报警，需要操作员立即干预，如关键系统或设备发生故障，影响到列车或地铁线的正常运行。 3：Normal Alarm,operators should treat in given time,such as unimportant equipment failure alarms and foreell alarms.普通报警，需要操作员在给定时间内干预，如非关键设备故障、预告报警。 4：No-critical Alarm,not need to do anything,just pay attention.非关键报警，不需人员干预的报警，但有必要引起操作员注意。
Addressing (FEP) | Internal information | Column shoud be filled by ISCS Contractor ISCS合同商应填写的列
Scadasoft Database | Internal information
MMI | Internal information
*Remarks:
If any discrepancy between IO class and IO list, all the software development, production and Testing should be reference IO class | 如果IO点表和类表有不一致,所有软件开发,生产及测试将以IO类表为准.
The contents now in the template are just examples, not all IO class. | 模板中所列仅为举例，不包括所有类点