## Revision
Revision
Date | Version | Author | Observations
2015-09-13 | A0.2 | A. TRAN | Creation | CHANGE TO :
2016-03-02 | A1.1 | C.CAMARA | Update following adopted ICD template
2016-03-16 | A2 | C.CAMARA | Update SIL2; Modbus and TVS Mode
2016-04-06 | B- | C.CAMARA | Update following workshop on the 04/04/2016
2016-08-24 | B0.2 | F.BLAISE | Update following new template and Cegelec comments
2016-09-09 | B0.3 | F.BLAISE | Update analog input following Cegelec comments
2016-09-21 | B0.4 | F.BLAISE | Add DI received by SCADA for SIL-2 commands Add select/execute for A0 type commands
2016-09-27 | B0.5 | Software Team | Modeling LCP, IOC, AHU and SCB equipment classes
2016-11-03 | B0.6 | Software Team | Modeling TVF, CJF and JET equipment classes
2016-11-30 | B0.6 | O. Bernard | Added SIL2 commands from B0.5, SW started their B0.6 from older version. Added size of point type in Definitions tab (used in IO Class) Added "Is Animated" column in Class List
2017-01-30 | B0.7 | C. CAMARA | Update SIL2 and class for rationalization activities
2017-02-06 | B0.8 | E. SANDOZ | Review and correction before sending to HK
2017-04-12 | B0.8 | E. SANDOZ | Back from HK
2017-04-22 | B0.9 | T.MARTINEZ | Migration to 0.34 + VBA code enhancement.
2017-05-10 | B0.9 | H. SALIHEDDINE | - Add Column "Revision" in Class list and Instance List - index address and position bit filling in Class list sheet ( the filling depends on the used protocol) - Instance ID filling in Instance List sheet - VBA code update for point address calculation - I.O class small update for DI, DI , AI Point type corresponding data
2017-05-15 | B0.10 | H. SALIHEDDINE | B0.10_SP18_1 - Add "OPERATING MODE " AI and DI2 points for FXL and MUL Classes B0.10_SP18_2 - Replace « MODBUS:1:Read:Coils » by « MODBUS:4:Read:Input Registers » in column « Operation code (FC, ASDU, ...) » - Manual filling of "Index Address" column in class list
2017-06-28 | B0.10_SP18_3 | T.LO | In "1-Class List", - update class MUL and FXL range min = 1 and range max = 16 for "OPERATING MODE SELECT" and "OPERATNG MODE EXECUTE" - Fix register type (originally input type usesfunc code16, output type uses func code 4…etc) - Update "Index Address" for class MUL In "B-AddressQty", - Enlarge FXL address index In "2-Instance List", - Update "RTU Name" to OCC_TUN and BOCC_TUN - Update "Equipment name" of OTS equipment to OTS01 and OTS02 - Update "Equipment name" of LCP equipment to LCP01" - Update "Sublocation" from TVS:SCR_SCB01 to TVS:SCR-SCB01 In "4-External Variables" - Add CJF class EV
2017-10-18 | B1.1 | MTE | IO List major correction following a dedicated TVS workshop (October 2017).
2017-11-20 | B1.2 | MTE | IO List major correction following a dedicated TVS workshop (20th November 2017).
2017-11-29 | B1.3 | MTE | IO List major correction following dedicated TVS workshops (22nd & 26th November 2017).
2017-11-30 | B1.4 | MTE | Emergency Scenarios Workshop
2017-12-12 | B1.5 | MTE | Class List: Ventilation Normal & Congested Modes Update Emergency Scenarios Update MMS Classes Update - CPELX class to be splitted in several subclasses Instance List: MAR01 & MAR0A available
2017-12-17 | B1.6 | MTE | Class List: MMS Workshop Instance List: MMS Workshop for MAR01 & MAR0A Emergency Scenario
2017-12-21 | B1.7 | MTE | Class List: Correction VENTILATION, PFA, EXF & SED. Instance List: 8 Smoke Curtains.
2018-01-05 | B1.8 | MTE | Class List: Correction of Point Type in class EMERGENCY - Mode Correction of Point Type in class MPLC - PLC-B Status Correction in class MPLC - Operational Status: not animated Addition of the alarm label related to WATCHDOG Instance List: Addition of EC1-01, EC1-0A, QAP-01 and QEC-01 stations
2018-01-10 | B2 | MTE | Delivery revision PLC points: Deletion of previous content, obsolete after Class list changes
2018-03-08 | B2.1 | Chao | 1-Class List:delete a space after "STOP" in ROW110 and ROW151, COLUMN P 2-Instance List: Update Column G and Column K to meet the DB path for TVS for lusail

## Introduction
Introduction
Recommandations
1 | Use one ECI file for each ICD document (one ICD=one subsystem)
2 | Do not change the organisation of the ECI file:
- Sheet "Equipment classes" : define all classes for the relative subsystem (see meaning of each field in the "Definitions" sheet)
- Sheet "Equipment instances" : define all instances for the relative subsystem (see meaning of each field in the "Definitions" sheet)
3 | For each sheet, do not change the organisation of the sheet (does not remove any column) in order to be able to use the standard export/import tools
4 | Create the necessary number of classes: for example, if similar equipment have different numbers of DI, DO, AI, create one class for each case
5 | Define, if possible, contiguous addresses for equipments/points within the same class.
Use the internal macro (### to be implemented in next release ###) to check the consistency of all data included in the sheet "Equipment classes" and "Equipment instances"
Notes
Issues to be addressed in future release
## Use appropriate point & bit value descriptions to create alarm label (DI) #####
### define rules for separators

## Definitions
Subsystem TVS - Equipment classes & instances
Definitions
1-Class List
Column Class | Column Name | Column Description | Values
| Revision | Identifiy the IO revision in witch the information was added , deleted or modified | version (string)
| isAComment | Specify whether the line is a comment or not | Y or N
EQUIPMENT CLASSES
| System | Define the trigram of the system's name in which the equipment is included | XXX
| Sub-system | Define the trigram of the sub-system's name in which the equipment is included | XXX
| Class name | Short equipment name on XXX characters number (minimum 3 characters - maximum 12 characters)
| CSS Point Name | Normalized name, used within the SCADA
EXTERNAL SYSTEM DATA
| Point Name | Name of equipment point from supplier
| Point Description | Any useful documentation on the point
| Point Type | Point can be qualified as Event or Alarm. Operational are not sent to MMS, Technical and Meter are sent to MMS. Hence, supported values are | Operational Event |  | Event which are from the nominal mode of the equipment. For exmaple open/close, locked/unlocked …
|  |  | Operational Alarm |  | Alarm that are from the nominal operation mode of the equipment. For example operator changing mode which put the equipment in Alarm state or equipment changing its status triggering an alarm.
|  |  | Technical Alarm |  | Alarm that deviated from the nominal operation mode. For example all detect fault. These are not part of the system nominal behavior
|  |  | Meter |  | Event which are needed for maintenance procedures.
Command
| Frequency | Time interval between data transmissions from SCADA to MMS | Daily
Weekly
Monthly
| Data Type | Digital Input | DI | 1 | bit
|  |  | DI2 | 2 | bits
|  | Digital Output | DO | 1 | bits
|  |  | DO2 | 2 | bits
|  | Analog Input | AI | 16 | bits
|  |  | AI2 | 32 | bits
|  | Analog Output | AO | 16 | bits
|  |  | AO2 | 32 | bits
EXTERNAL SYSTEM DATA DETAILS
| SIL Level | Identify the SIL level for the equipment point which can be | SIL0
SIL2_Monitoring
SIL2_Control
| Protocol | Applicable protocol: may be Modbus or IEC104
| Operation code | Operation code needed to manage the point at protocol level
| Memory Block | TODO
DI POINT
| DI/DI2 Value = 0 | For a DI or DI2, definition of the supervised status when the value is set to 0
| DI/DI2 Value = 1 | For a DI or DI2, definition of the supervised status when the value is set to 1
| DI2 Value = 2 | For a DI2, definition of the supervised status when the value is set to 2
| DI2 Value = 3 | For a DI2, definition of the supervised status when the value is set to 3
| Default value | Default value of the equipment point
| Alarm severity | Define the alarm severity for each value with the format (value1: severity label 1, value2: severity label 2, etc) Severity labels are: - None for events - Min for Minor alarms - Maj for Major alarms - Crit for Critical alarms Example: - 0: None, 1: Maj - 0: None, 1: None
| Alarm label | This label will be presented to the operators on the HMI for english language. It consists of: CCS Point Name: DI value when=0 / DI value when=1 / …
DO POINT
| DO/DO2 Value = 0 | For a DO or DO2, definition of the supervised status when the value is set to 0
| DO/DO2 Value = 1 | For a DO or DO2, definition of the supervised status when the value is set to 1
| DO2 Value = 2 | For a DO2, definition of the supervised status when the value is set to 2
| DO2 Value = 3 | For a DO2, definition of the supervised status when the value is set to 3
| Default value | Define the default value of the equipment point
| Output duration (ms) | Give the properties of the output signal command in ms: <empty>: continuous signal integer value: temporal duration of the pulse (in ms)
| Timeout for reaction (s) | Expected response time between the command sending and the modification of the associated status
| Initial condition | Pre-condition to be checked before sending the command
| Final condition | Post-condition to be checked to make sure the command is successful
| Associated return status | Return equipment status associated with the command
AI POINT
| Unit | Give the measurement unity of the analog data
| Min value | Define the minimum value of the data
| Max value | Define the maximum value of the data
| Limit 1 (optional) | Threshold in order to add range of the supervised value between min and max values
| Limit 2 (optional) | Threshold in order to add range of the supervised value between min and max values
In the template, alarm thresholds are defined through two value limits plus a minimum value and a maximum value. As shown in the figure on the right, this defines 5 ranges for which an alarm may be defined
| Range <i> alarm severity | Define the alarm severity for a range Severity labels are: - None for events - Min for Minor alarms - Maj for Major alarms - Crit for Critical alarms
| Range <i> alarm label | Define the alarm label for a range
| Dead band | Define the tolerance of variation around a threshold
| Default value | Define the default value of the equipment point
| Alarm label | This label will be presented to the operators on the HMI. It consists on: Equipment description (displayed in HMI): under Min value / under Max value / etc.
AO POINT
| Unit | Give the measurement unity of the analog data
| Range Min value | Define the minimum range of the command value
| Range Max value | Define the maximum range of the command value
| Output duration (ms) | Give the properties of the output signal command in ms: Nothing to fill: continuous signal XXX: temporal duration of the pulse
| Timeout for reaction (s) | Response time between the command and the associated status modification on the equipment
| Initial condition | Conditions to verify before sending the command
| Final condition | Conditions to verify after the sending of the command
| Associated return status | Return equipment status associated with the command
2-Instance List
Column Class | Column Name | Column Description
| Revision | Identifiy the IO revision in witch the information was added , deleted or modified
| GBS Code | TBC
| LBS Code (LRT) | TBC
| LBS Code (QRC) | TBC
| Description | Textual description or precision about the Location/sublocation of the equipment instance
| Location | Define in a short designation the geographical location in which the equipment is based
| Sublocation | Define in a short designation the sublocation (Subsystem / Level / Building / room) in which the equipment is based
| Class name | Class name identical to the class name defined in the "1-Class List" tab
| Equipment name | Give the instance name of the equipment.
| RTU Name | Name of the concentrator (as viewed in the SCADA subsystem) for the equipment
| PLC Name | Name of the partner PLC
| InvalidVar1 | name of the first external variable used to invalidate this equipement (usually comStatus of the gateway or PRTU)
| InvalidVar2 | name of the second external variable used to invalidate this equipement (usually comStatus of the gateway or PRTU)
| InvalidVar3 | name of the third external variable used to invalidate this equipement (usually comStatus of the gateway or PRTU)

## Generation
Execute |  | To do before Generation => Check that there are no ROW filters set in the Class and instance worksheets
Tool version | v2.2 | #NAME?
Generation Time: | 2018/3/8 at 17:31:28
Found Classes: | 33
Found Errors: | 3801
Found Warnings: | 3801
Not Found Classes: | 0

## 1-Class List
|  | EQUIPMENT CLASSES |  |  |  | EXTERNAL SYSTEM DATA |  |  |  |  | EXTERNAL SYSTEM DATA DETAILS |  |  |  | DI or DI2 | [6 empty] | DO | [8 empty] | AI | [17 empty] | AO | [8 empty] | MMS | SE Engineering |  |  |  | SW Engineering | HMI details (dictionnaries)
Revision | isAComment | System | Sub-system | Class name | CSS Point Name | Point Name | Point Description | Point Type | Frequency | Data Type | SIL Level | Protocol | Operation code (FC, ASDU, ...) | Memory Block | DI or DI2 value = 0 (00) | DI or DI2 value = 1(01) | DI2 value = 2 (10) | DI2 value = 3 (11) | Default value | Alarm severity | Alarm label | DO or DO2 value = 0 (00) | DO or DO2 value = 1(01) | DO2 value = 2 (10) | DO2 value = 3 (11) | Output duration (ms) | Timeout for reaction (s) | Initial condition | Final condition | Associated return status | Unit | Min value | Max value | Limit 1 (optional) | Limit 2 (optional) | Range 1 alarm severity ] -∞,min value] | Range 1 alarm label ] -∞,min value] | Range 2 alarm severity ]min value,limit1] | Range 2 alarm label ]min value,limit1] | Range 3 alarm severity ]limit1,limit2] | Range 3 alarm label ]limit1,limit2] | Range 4 alarm severity ]limit2,max value] | Range 4 alarm label ]limit2,max value] | Range 5 alarm severity ]max value,+∞[ | Range 5 alarm label ]max value,+∞[ | Dead band | Default value | Formula | Unit | Range Min value | Range Max value | Output duration (ms) | Timeout for reaction (s) | Initial condition | Final condition | Associated return status | Formula | [Lusail] PBS code | Data Length | Index Address | Bit position | IsAnimated | Code
| Y | This part should be filled up by System Engineering and gives the indication on how to modelize prototypes
B1.5 | Y | + |  |  | MASTER PLCs (MPLC)
B1.1 | N | TUN | TVS | MPLC | PLC STATE | PLC STATE | PLC A/B OFFLINE | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | OFFLINE | ONLINE |  |  | ONLINE | 0: Crit, 1: None | PLC STATE : OFFLINE/ONLINE | [37 empty] | #NAME? |  |  | YES | Point1
B1.8 | N | TUN | TVS | MPLC | OPERATIONAL STATUS | OPERATIONAL STATUS | PLC RUNNING. | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | STOP | RUNNING |  |  | RUNNING | 0: Crit, 1: None | OPERATIONAL STATUS : STOP/RUNNING | [37 empty] | #NAME? |  |  | NO | Point2
B1.3 | N | TUN | TVS | MPLC | PLC-A STATUS | PRIMARY MODE ACTIVE | PLC A/B : PRIMARY MODE ACTIVE | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | STANDBY | ACTIVE |  |  | ACTIVE | 0: Maj, 1: None | PLC-A STATUS : STANDBY/ACTIVE | [37 empty] | #NAME? |  |  | YES | Point3
B1.8 | N | TUN | TVS | MPLC | PLC-B STATUS | SECONDARY MODE ACTIVE (STANDBY) | PLC A/B: SECONDARY MODE ACTIVE (STANDBY) | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | STANDBY | ACTIVE |  |  | STANDBY | 0: None, 1: None | PLC-B STATUS : STANDBY/ACTIVE | [37 empty] | #NAME? |  |  | YES | Point4
B1.3 | N | TUN | TVS | MPLC | APPLICATIONS ARE DIFFERENT ON THE TWO PLCS | APPLICATIONS ARE DIFFERENT ON THE TWO PLCS | APPLICATIONS ARE DIFFERENT ON THE TWO PLCS | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | APPLICATIONS ARE DIFFERENT ON THE TWO PLCS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point5
B1.1 | N | TUN | TVS | MPLC | POWER SUPPLY STATUS | POWER SUPPLY FAULT | PLC A/B: POWER SUPPLY FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | POWER SUPPLY STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point6
B1.2 | N | TUN | TVS | MPLC | CPU MODULE STATUS | CPU MODULE FAULT | PLC A/B: CPU MODULE FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | CPU MODULE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point7
B1.2 | N | TUN | TVS | MPLC | CRP MODULE STATUS | CRP MODULE FAULT | PLC A/B: CRP MODULE FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | CRP MODULE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point8
B1.3 | N | TUN | TVS | MPLC | NOE MODULE COMMUNICATION [SCADA] STATUS | NOE MODULE FAULT (SCADA COMMUNICATION) | PLC A/B: NOE MODULE FAULT (SCADA COMMUNICATION) | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | NOE MODULE COMMUNICATION [SCADA] STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point9
B1.3 | N | TUN | TVS | MPLC | NOE MODULE COMMUNICATION [STATION PLC] STATUS | NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION) | PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION) | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | NOE MODULE COMMUNICATION [STATION PLC] STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point10
B1.2 | N | TUN | TVS | MPLC | COMMUNICATION WITH SCADA STATUS | COMMUNICATION FAULT WITH SCADA | PLC A/B: COMMUNICATION FAULT WITH SCADA | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH SCADA STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point11
B1.2 | N | TUN | TVS | MPLC | COMMUNICATION WITH STATION PEA-01 PLC STATUS | COMMUNICATION FAULT WITH STATION PEA-01 PLC | PLC A/B: COMMUNICATION FAULT WITH STATION PEA-01 PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH STATION PEA-01 PLC STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point12
B1.2 | N | TUN | TVS | MPLC | COMMUNICATION WITH STATION MAR-01 PLC STATUS | COMMUNICATION FAULT WITH STATION MAR-01 PLC | PLC A/B: COMMUNICATION FAULT WITH STATION MAR-01 PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH STATION MAR-01 PLC STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point13
B1.2 | N | TUN | TVS | MPLC | COMMUNICATION WITH STATION MAR-02 PLC STATUS | COMMUNICATION FAULT WITH STATION MAR-02 PLC | PLC A/B: COMMUNICATION FAULT WITH STATION MAR-02 PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH STATION MAR-02 PLC STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point14
B1.2 | N | TUN | TVS | MPLC | COMMUNICATION WITH STATION MAR-03 PLC STATUS | COMMUNICATION FAULT WITH STATION MAR-03 PLC | PLC A/B: COMMUNICATION FAULT WITH STATION MAR-03 PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH STATION MAR-03 PLC STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point15
B1.2 | N | TUN | TVS | MPLC | COMMUNICATION WITH STATION MAR-04 PLC STATUS | COMMUNICATION FAULT WITH STATION MAR-04 PLC | PLC A/B: COMMUNICATION FAULT WITH STATION MAR-04 PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH STATION MAR-04 PLC STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point16
B1.2 | N | TUN | TVS | MPLC | COMMUNICATION WITH STATION QEC-01 PLC STATUS | COMMUNICATION FAULT WITH STATION QEC-01 PLC | PLC A/B: COMMUNICATION FAULT WITH STATION QEC-01 PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH STATION QEC-01 PLC STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point17
B1.2 | N | TUN | TVS | MPLC | COMMUNICATION WITH STATION EC1-01 PLC STATUS | COMMUNICATION FAULT WITH STATION EC1-01 PLC | PLC A/B: COMMUNICATION FAULT WITH STATION EC1-01 PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH STATION EC1-01 PLC STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point18
B1.2 | N | TUN | TVS | MPLC | COMMUNICATION WITH STATION QAP-01 PLC STATUS | COMMUNICATION FAULT WITH STATION QAP-01 PLC | PLC A/B: COMMUNICATION FAULT WITH STATION QAP-01 PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH STATION QAP-01 PLC STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point19
B1.2 | N | TUN | TVS | MPLC | COMMUNICATION WITH STATION FXH-02 PLC STATUS | COMMUNICATION FAULT WITH STATION FXH-02 PLC | PLC A/B: COMMUNICATION FAULT WITH STATION FXH-02 PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH STATION FXH-02 PLC STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point20
B1.2 | N | TUN | TVS | MPLC | COMMUNICATION WITH SHAFT PEA-0A PLC STATUS | COMMUNICATION FAULT WITH SHAFT PEA-0A PLC | PLC A/B: COMMUNICATION FAULT WITH SHAFT PEA-0A PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH SHAFT PEA-0A PLC STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point21
B1.2 | N | TUN | TVS | MPLC | COMMUNICATION WITH SHAFT PEA-1B PLC STATUS | COMMUNICATION FAULT WITH SHAFT PEA-1B PLC | PLC A/B: COMMUNICATION FAULT WITH SHAFT PEA-1B PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH SHAFT PEA-1B PLC STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point22
B1.2 | N | TUN | TVS | MPLC | COMMUNICATION WITH SHAFT MAR-0A PLC STATUS | COMMUNICATION FAULT WITH SHAFT MAR-0A PLC | PLC A/B: COMMUNICATION FAULT WITH SHAFT MAR-0A PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH SHAFT MAR-0A PLC STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point23
B1.2 | N | TUN | TVS | MPLC | COMMUNICATION WITH SHAFT EC1-0A PLC STATUS | COMMUNICATION FAULT WITH SHAFT EC1-0A PLC | PLC A/B: COMMUNICATION FAULT WITH SHAFT EC1-0A PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH SHAFT EC1-0A PLC STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point24
B1.2 | N | TUN | TVS | MPLC | COMMUNICATION WITH SHAFT QAP-1B PLC STATUS | COMMUNICATION FAULT WITH SHAFT QAP-1B PLC | PLC A/B: COMMUNICATION FAULT WITH SHAFT QAP-1B PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH SHAFT QAP-1B PLC STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | Point25
B0.9 | Y | + |  |  | Watchdog (WTDG)
B1.1 | N | TUN | TVS | WTDG | Watchdog Counter | Watchdog Counter | Watchdog Counter for each TVS Master PLC | Operational Alarm |  | AI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | Count | 0 | 65535 |  |  | Critical | Watchdog Counter Failure | [10 empty] | UINT | [10 empty] | #NAME? |  |  | NO | TODO
B1.5 | Y | + |  |  | SWITCH
B1.2 | N | TUN | TVS | SWI | SWITCH STATUS | SWITCH FAULT | SWITCH FAULT | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SWITCH STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | YES | TODO
B1.5 | Y | + |  |  | STATION/SHAFT PLC
B1.3 | N | TUN | TVS | SPLC | PLC STATE | PLC STATE | PLC A/B OFFLINE | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | OFFLINE | ONLINE |  |  | ONLINE | 0: Crit, 1: None | PLC STATE : OFFLINE/ONLINE | [37 empty] | #NAME? |  |  | YES | TODO
B1.3 | N | TUN | TVS | SPLC | OPERATIONAL STATUS | OPERATIONAL STATUS | PLC RUNNING. | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | STOP | RUNNING |  |  | RUNNING | 0: Crit, 1: None | OPERATIONAL STATUS : STOP/RUNNING | [37 empty] | #NAME? |  |  | YES | TODO
B1.3 | N | TUN | TVS | SPLC | POWER SUPPLY STATUS | POWER SUPPLY FAULT | PLC A/B: POWER SUPPLY FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | POWER SUPPLY STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | SPLC | CPU MODULE STATUS | CPU MODULE FAULT | PLC A/B: CPU MODULE FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | CPU MODULE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | SPLC | CRP MODULE STATUS | CRP MODULE FAULT | PLC A/B: CRP MODULE FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | CRP MODULE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | SPLC | CRA MODULE STATUS | NRP MODULE FAULT | NRP MODULE FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | CRA MODULE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | SPLC | NRP MODULE STATUS | NRP MODULE FAULT | NRP MODULE FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | NRP MODULE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | SPLC | NOE MODULE COMMUNICATION STATUS | NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION) | PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION) | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | NOE MODULE COMMUNICATION STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | SPLC | IO MODULE STATUS | NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION) | PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION) | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | IO MODULE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | Y | + |  |  | FIRE MANUAL OVERRIDE PANEL (FMOP)
B1.3 | N | TUN | TVS | FMOP | LOCAL FIRE PANEL EMERGENCY MODE | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL EMERGENCY MODE : INACTIVE/ACTIVE | [37 empty] | #NAME? |  |  | YES | TODO
B1.3 | N | TUN | TVS | FMOP | LOCAL FIRE PANEL RIGHT SCENARIO PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL RIGHT SCENARIO PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | FMOP | LOCAL FIRE PANEL LEFT SCENARIO PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL LEFT SCENARIO PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | #NAME? |  |  | NO | TODO
B0.9 | Y | + |  |  | LOCAL CONTROL PANEL (LCP) [STATION HMI]
B1.2 | N | TUN | TVS | LCP | COMMUNICATION WITH PLC STATUS | COMMUNICATION FAULT WITH PLC | COMMUNICATION FAULT WITH PLC | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | COMMUNICATION WITH PLC STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | YES | TODO
B1.1 | N | TUN | TVS | LCP | LCP MODE | LCP MODE | LOCAL / REMOTE STATUS | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | REMOTE | LOCAL |  |  | REMOTE | 0: None, 1: Maj | LCP MODE : REMOTE/LOCAL | [37 empty] | #NAME? |  |  | YES | TODO
B1.5 | Y | + |  |  | TUNNEL NORMAL & CONGESTED VENTILATION MODES
B1.5 | N | TUN | TVS | VENTILATION | OPERATING MODE | OPERATING MODE | OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP) | Operational Event |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | AUTO PLC | MANUAL SCADA |  |  | AUTO PLC | 0: None, 1: None | OPERATING MODE : AUTO PLC/MANUAL SCADA | [37 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | VENTILATION | ACTIVE VENTILATION MODE | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | PISTON | MECHANICAL | COOLING | INCONSISTANT | PISTON | 0: None, 1: None, 2: None, 3: Crit | ACTIVE VENTILATION MODE : PISTON/MECHANICAL/COOLING/INCONSISTANT | [37 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | VENTILATION | PLC AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | Command |  | DO | SIL0 | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE AUTO MODE |  |  |  | 10 | OPERATING MODE = MANUAL SCADA |  | OPERATING MODE = AUTO PLC | [28 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | VENTILATION | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 2 | OPERATING MODE = AUTO PLC |  | SCADA MANUAL MODE SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | VENTILATION | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | VENTILATION | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 10 | OPERATING MODE = AUTO PLC |  | SCADA MANUAL MODE EXECUTE ACK = ACKNOWLEDGE and OPERATING MODE = MANUAL SCADA | [28 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | VENTILATION | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | VENTILATION | PISTON MODE SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE PISTON MODE |  |  |  | 2 | ACTIVE VENTILATION MODE != PISTON MODE |  | PISTON MODE SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | VENTILATION | PISTON MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | PISTON MODE SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | VENTILATION | PISTON MODE EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE PISTON MODE |  |  |  | 40 | ACTIVE VENTILATION MODE != PISTON MODE |  | PISTON MODE EXECUTE ACK = ACKNOWLEDGE and ACTIVE VENTILATION MODE = PISTON MODE | [28 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | VENTILATION | PISTON MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | PISTON MODE EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | VENTILATION | MECHANICAL MODE SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE MECHANICAL MODE |  |  |  | 2 | ACTIVE VENTILATION MODE != MECHANICAL MODE |  | MECHANICAL MODE SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | VENTILATION | MECHANICAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | MECHANICAL MODE SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | VENTILATION | MECHANICAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE MECHANICAL MODE |  |  |  | 40 | ACTIVE VENTILATION MODE != MECHANICAL MODE |  | MECHANICAL MODE EXECUTE ACK = ACKNOWLEDGE and ACTIVE VENTILATION MODE = MECHANICAL MODE | [28 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | VENTILATION | MECHANICAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | MECHANICAL MODE EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | VENTILATION | COOLING MODE SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE COOLING MODE |  |  |  | 2 | ACTIVE VENTILATION MODE != COOLING MODE |  | COOLING MODE SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | VENTILATION | COOLING MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | COOLING MODE SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | VENTILATION | COOLING MODE EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE COOLING MODE |  |  |  | 40 | ACTIVE VENTILATION MODE != COOLING MODE |  | COOLING MODE EXECUTE ACK = ACKNOWLEDGE and ACTIVE VENTILATION MODE = COOLING MODE | [28 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | VENTILATION | COOLING MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | COOLING MODE EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | Y | + |  |  | EMERGENCY SCENARIO
B1.8 | N | TUN | TVS | EMERGENCY | SCENARIO ACTIVATION PROPOSAL BY TVS | OPERATING MODE | OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP) | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | SCENARIO ACTIVATION PROPOSAL BY TVS : INACTIVE/ACTIVE | [37 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | EMERGENCY | ACTIVATION STATUS OF EMERGENCY SCENARIO | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | ACTIVATION STATUS OF EMERGENCY SCENARIO : INACTIVE/ACTIVE | [37 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | EMERGENCY | SCENARIO CONFIRMATION BY SCADA OPERATOR SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | SCENARIO CONFIRMATION |  |  |  | 2 | SCENARIO ACTIVATION PROPOSAL BY TVS = ACTIVE and ACTIVATION STATUS OF EMERGENCY SCENARIO = INACTIVE |  | SCENARIO CONFIRMATION BY SCADA OPERATOR SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | EMERGENCY | SCENARIO CONFIRMATION BY SCADA OPERATOR SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCENARIO CONFIRMATION BY SCADA OPERATOR SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | EMERGENCY | SCENARIO CONFIRMATION BY SCADA OPERATOR EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | SCENARIO CONFIRMATION |  |  |  | 10 | SCENARIO ACTIVATION PROPOSAL BY TVS = ACTIVE and ACTIVATION STATUS OF EMERGENCY SCENARIO = INACTIVE |  | SCENARIO CONFIRMATION BY SCADA OPERATOR EXECUTE ACK = ACKNOWLEDGE and ACTIVATION STATUS OF EMERGENCY SCENARIO = ACTIVE | [28 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | EMERGENCY | SCENARIO CONFIRMATION BY SCADA OPERATOR EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCENARIO CONFIRMATION BY SCADA OPERATOR EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | Y | + |  |  | MAIN UNDERGROUND LINE AVERAGE TEMPERATURE
B1.5 | N | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 1 | AVERAGE TUNNEL TEMPERATURE ZONE 1 | AVERAGE TUNNEL TEMPERATURE ZONE 1 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 2 | AVERAGE TUNNEL TEMPERATURE ZONE 2 | AVERAGE TUNNEL TEMPERATURE ZONE 2 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 3 | AVERAGE TUNNEL TEMPERATURE ZONE 3 | AVERAGE TUNNEL TEMPERATURE ZONE 3 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 4 | AVERAGE TUNNEL TEMPERATURE ZONE 4 | AVERAGE TUNNEL TEMPERATURE ZONE 4 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 5 | AVERAGE TUNNEL TEMPERATURE ZONE 5 | AVERAGE TUNNEL TEMPERATURE ZONE 5 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 6 | AVERAGE TUNNEL TEMPERATURE ZONE 6 | AVERAGE TUNNEL TEMPERATURE ZONE 6 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 7 | AVERAGE TUNNEL TEMPERATURE ZONE 7 | AVERAGE TUNNEL TEMPERATURE ZONE 7 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 8 | AVERAGE TUNNEL TEMPERATURE ZONE 8 | AVERAGE TUNNEL TEMPERATURE ZONE 8 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 9 | AVERAGE TUNNEL TEMPERATURE ZONE 9 | AVERAGE TUNNEL TEMPERATURE ZONE 9 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 10 | AVERAGE TUNNEL TEMPERATURE ZONE 10 | AVERAGE TUNNEL TEMPERATURE ZONE 10 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 11 | AVERAGE TUNNEL TEMPERATURE ZONE 11 | AVERAGE TUNNEL TEMPERATURE ZONE 11 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 12 | AVERAGE TUNNEL TEMPERATURE ZONE 12 | AVERAGE TUNNEL TEMPERATURE ZONE 12 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 13 | AVERAGE TUNNEL TEMPERATURE ZONE 13 | AVERAGE TUNNEL TEMPERATURE ZONE 13 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 14 | AVERAGE TUNNEL TEMPERATURE ZONE 14 | AVERAGE TUNNEL TEMPERATURE ZONE 14 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 15 | AVERAGE TUNNEL TEMPERATURE ZONE 15 | AVERAGE TUNNEL TEMPERATURE ZONE 15 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | MUL | AVERAGE OUTDOOR TEMPERATURE | AVERAGE OUTDOOR TEMPERATURE | AVERAGE OUTDOOR TEMPERATURE | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.5 | Y | + |  |  | FOXHILL LINE AVERAGE TEMPERATURE
B1.5 | N | TUN | TVS | FXL | AVERAGE TUNNEL TEMPERATURE ZONE 16 | AVERAGE TUNNEL TEMPERATURE ZONE 16 | AVERAGE TUNNEL TEMPERATURE ZONE 16 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | FXL | AVERAGE TUNNEL TEMPERATURE ZONE 17 | AVERAGE TUNNEL TEMPERATURE ZONE 17 | AVERAGE TUNNEL TEMPERATURE ZONE 17 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | FXL | AVERAGE OUTDOOR TEMPERATURE | AVERAGE OUTDOOR TEMPERATURE | AVERAGE OUTDOOR TEMPERATURE | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B0.9 | Y | + |  |  | TUNNEL VENTILATION FAN (TVF)
B1.3 | N | TUN | TVS | TVF | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | OFF | LOCAL | REMOTE | INCONSISTANT | REMOTE | 0: Crit, 1: Maj, 2: None, 3: Crit | ELECTRICAL PANEL SELECTOR SWITCH STATUS : OFF/LOCAL/REMOTE/INCONSISTANT | [37 empty] | #NAME? |  |  | YES | TODO
B1.3 | N | TUN | TVS | TVF | OPERATING MODE | OPERATING MODE | OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP) | Operational Event |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | AUTO SCADA | MANUAL SCADA |  |  | AUTO SCADA | 0: None, 1: None | OPERATING MODE : AUTO SCADA/MANUAL SCADA | [37 empty] | #NAME? |  |  | YES | TODO
B2.1 | N | TUN | TVS | TVF | RUN STATUS | RUN STATUS | SUPPLY / EXHAUST / STOP STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | STOP | REVERSE | FORWARD | INCONSISTANT | STOP | 0: None, 1: None, 2: None, 3: Crit | RUN STATUS : STOP/REVERSE/FORWARD/INCONSISTANT | [37 empty] | #NAME? |  |  | YES | TODO
B1.1 | N | TUN | TVS | TVF | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | Command |  | DO | SIL0 | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE AUTO MODE |  |  |  | 10 | OPERATING MODE = MANUAL SCADA |  | OPERATING MODE = AUTO SCADA | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVF | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 2 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVF | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVF | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 10 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE EXECUTE ACK = ACKNOWLEDGE and OPERATING MODE = MANUAL SCADA | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVF | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TVF | VSD ELECTRICAL STATUS | VSD ELECTRICAL STATUS | VSD ELECTRICAL STATUS | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | VSD ELECTRICAL STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TVF | VSD FAIL TO START STATUS | VSD FAIL TO START | VSD FAIL TO START | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | VSD FAIL TO START STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TVF | VSD FAIL TO STOP STATUS | VSD FAIL TO STOP | VSD FAIL TO STOP | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | VSD FAIL TO STOP STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | TVF | VSD SPEED FREQUENCY | VSD SPEED FREQUENCY | VSD SPEED FREQUENCY | Meter | Daily | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | Hz | 0 | 60 | [14 empty] | UINT | [10 empty] | #NAME? |  |  | YES | TODO
B1.2 | N | TUN | TVS | TVF | VSD SPEED ORDER | VSD SPEED ORDER | VSD SPEED ORDER | Command |  | DO2 | SIL0 | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | LOW SPEED | HIGH SPEED | INVALID |  | NA | No initial condition Toggle command, either low or high selected | No final condition Toggle command, either low or high selected | No associated return status Change on VSD SPEED FREQUENCY AI | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVF | STOP ORDER (VSD) SELECT | STOP ORDER (VSD) SELECT | STOP ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | STOP SELECTION |  |  |  | 2 | RUN STATUS = FORWARD or RUN STATUS = REVERSE |  | STOP ORDER (VSD) SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVF | STOP ORDER (VSD) SELECT ACK | STOP ORDER (VSD) SELECT ACK | STOP ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | STOP ORDER (VSD) SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVF | STOP ORDER (VSD) EXECUTE | STOP ORDER (VSD) EXECUTE | STOP ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | STOP CONFIRMATION |  |  |  | 40 | RUN STATUS = FORWARD or RUN STATUS = REVERSE |  | STOP ORDER (VSD) EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = STOP | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVF | STOP ORDER (VSD) EXECUTE ACK | STOP ORDER (VSD) EXECUTE ACK | STOP ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | STOP ORDER (VSD) EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVF | FORWARD ORDER (VSD) SELECT | FORWARD ORDER (VSD) SELECT | FORWARD DIRECTION ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | FORWARD SELECTION |  |  |  | 2 | RUN STATUS = STOP |  | FORWARD ORDER (VSD) SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVF | FORWARD ORDER (VSD) SELECT ACK | FORWARD ORDER (VSD) SELECT ACK | FORWARD DIRECTION ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | FORWARD ORDER (VSD) SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVF | FORWARD ORDER (VSD) EXECUTE | FORWARD ORDER (VSD) EXECUTE | FORWARD DIRECTION ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | FORWARD CONFIRMATION |  |  |  | 40 | RUN STATUS = STOP |  | FORWARD ORDER (VSD) EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = FORWARD | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVF | FORWARD ORDER (VSD) EXECUTE ACK | FORWARD ORDER (VSD) EXECUTE ACK | FORWARD DIRECTION ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | FORWARD ORDER (VSD) EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVF | REVERSE ORDER (VSD) SELECT | REVERSE ORDER (VSD) SELECT | REVERSE DIRECTION ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | REVERSE SELECTION |  |  |  | 2 | RUN STATUS = STOP |  | REVERSE ORDER (VSD) SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVF | REVERSE ORDER (VSD) SELECT ACK | REVERSE ORDER (VSD) SELECT ACK | REVERSE DIRECTION ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | REVERSE ORDER (VSD) SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVF | REVERSE ORDER (VSD) EXECUTE | REVERSE ORDER (VSD) EXECUTE | REVERSE DIRECTION ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | REVERSE CONFIRMATION |  |  |  | 40 | RUN STATUS = STOP |  | REVERSE ORDER (VSD) EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = REVERSE | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVF | REVERSE ORDER (VSD) EXECUTE ACK | REVERSE ORDER (VSD) EXECUTE ACK | REVERSE DIRECTION ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | REVERSE ORDER (VSD) EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TVF | FAN AVAILABILITY STATUS | FAN AVAILABILITY STATUS | FAN UNAVAILABLE STATUS | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | AVAILABLE | UNAVAILABLE |  |  | AVAILABLE | 0: None, 1: Crit | FAN AVAILABILITY STATUS : AVAILABLE/UNAVAILABLE | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TVF | CIRCUIT BREAKER POSITION | CIRCUIT BREAKER OPEN | VSD CIRCUIT BREAKER OPEN | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | OPEN | CLOSE |  |  | OPEN | 0: None, 1: None | CIRCUIT BREAKER POSITION : OPEN/CLOSE | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TVF | CIRCUIT BREAKER TRIPPED STATUS | CIRCUIT BREAKER OUTAGE | VSD CIRCUIT BREAKER FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Crit | CIRCUIT BREAKER TRIPPED STATUS : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TVF | FAN HEATER CIRCUIT BREAKER POSITION | FAN HEATER CIRCUIT BREAKER OPEN | FAN HEATER CIRCUIT BREAKER OPEN | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | OPEN | CLOSE |  |  | OPEN | 0: None, 1: None | FAN HEATER CIRCUIT BREAKER POSITION : OPEN/CLOSE | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TVF | FAN HEATER CIRCUIT BREAKER TRIPPED STATUS | FAN HEATER CIRCUIT BREAKER OUTAGE | FAN HEATER CIRCUIT BREAKER FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | FAN HEATER CIRCUIT BREAKER TRIPPED STATUS : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TVF | FORWARD START-UP MISMATCH OUTAGE STATUS | FORWARD START-UP MISMATCH OUTAGE | FORWARD COMMAND MISMATCH ALARM | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | FORWARD START-UP MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TVF | REVERSE START-UP MISMATCH OUTAGE STATUS | REVERSE START-UP MISMATCH OUTAGE | REVERSE COMMAND MISMATCH ALARM | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | REVERSE START-UP MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TVF | STOP MISMATCH OUTAGE STATUS | STOP MISMATCH OUTAGE | STOP COMMAND MISMATCH ALARM | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | STOP MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TVF | WINDING TEMPERATURE STATUS | WINDING TEMPERATURE | WINDING TEMPERATURE FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | WINDING TEMPERATURE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TVF | FRONT BEARING TEMPERATURE STATUS | FRONT BEARING TEMPERATURE 1 FAULT | FRONT BEARING TEMPERATURE 1 FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | FRONT BEARING TEMPERATURE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TVF | REAR BEARING TEMPERATURE STATUS | REAR BEARING TEMPERATURE 1 FAULT | REAR BEARING TEMPERATURE 1 FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | REAR BEARING TEMPERATURE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TVF | VIBRATION 1ST LEVEL STATUS | VIBRATION 1ST LEVEL ALARM | VIBRATION 1ST LEVEL ALARM | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VIBRATION 1ST LEVEL STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TVF | VIBRATION 2ND LEVEL STATUS | VIBRATION 2ND LEVEL ALARM | VIBRATION 2ND LEVEL ALARM | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | VIBRATION 2ND LEVEL STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TVF | MORE THAN 10 STARTUP PER HOUR STATUS | MORE THAN 6 STARTUP PER HOUR | MORE THAN 6 STARTUP PER HOUR | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | MORE THAN 10 STARTUP PER HOUR STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TVF | RUNNING HOURS | RUNNING HOURS | RUNNING HOURS | Meter | Daily | AI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | h | 0 | 65535 | [14 empty] | UINT | [10 empty] | #NAME? |  |  | NO | TODO
B0.9 | Y | + |  |  | JET FAN
B1.3 | N | TUN | TVS | JET | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | OFF | LOCAL | REMOTE | INCONSISTANT | REMOTE | 0: Crit, 1: Maj, 2: None, 3: Crit | ELECTRICAL PANEL SELECTOR SWITCH STATUS : OFF/LOCAL/REMOTE/INCONSISTANT | [37 empty] | #NAME? |  |  | YES | TODO
B1.3 | N | TUN | TVS | JET | OPERATING MODE | OPERATING MODE | OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP) | Operational Event |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | AUTO SCADA | MANUAL SCADA |  |  | AUTO SCADA | 0: None, 1: None | OPERATING MODE : AUTO SCADA/MANUAL SCADA | [37 empty] | #NAME? |  |  | YES | TODO
B2.1 | N | TUN | TVS | JET | RUN STATUS | RUN STATUS | SUPPLY / EXHAUST / STOP STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | STOP | REVERSE | FORWARD | INCONSISTANT | STOP | 0: None, 1: None, 2: None, 3: Crit | RUN STATUS : STOP/REVERSE/FORWARD/INCONSISTANT | [37 empty] | #NAME? |  |  | YES | TODO
B1.1 | N | TUN | TVS | JET | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | Command |  | DO | SIL0 | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE AUTO MODE |  |  |  | 10 | OPERATING MODE = MANUAL SCADA |  | OPERATING MODE = AUTO SCADA | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | JET | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 2 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | JET | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | JET | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 10 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE EXECUTE ACK = ACKNOWLEDGE and OPERATING MODE = MANUAL SCADA | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | JET | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | JET | VSD ELECTRICAL STATUS | VSD ELECTRICAL STATUS | VSD ELECTRICAL STATUS | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | VSD ELECTRICAL STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | JET | VSD FAIL TO START STATUS | VSD FAIL TO START | VSD FAIL TO START | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | VSD FAIL TO START STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | JET | VSD FAIL TO STOP STATUS | VSD FAIL TO STOP | VSD FAIL TO STOP | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | VSD FAIL TO STOP STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | JET | VSD SPEED FREQUENCY | VSD SPEED FREQUENCY | VSD SPEED FREQUENCY | Meter | Daily | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | Hz | 0 | 60 | [14 empty] | UINT | [10 empty] | #NAME? |  |  | YES | TODO
B1.2 | N | TUN | TVS | JET | VSD SPEED ORDER | VSD SPEED ORDER | VSD SPEED ORDER | Command |  | DO | SIL0 | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | HIGH SPEED |  |  |  | NA | No initial condition Toggle command, either low or high selected | No final condition Toggle command, either low or high selected | No associated return status Change on VSD SPEED FREQUENCY AI | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | JET | STOP ORDER (VSD) SELECT | STOP ORDER (VSD) SELECT | STOP ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | STOP SELECTION |  |  |  | 2 | RUN STATUS = FORWARD or RUN STATUS = REVERSE |  | STOP ORDER (VSD) SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | JET | STOP ORDER (VSD) SELECT ACK | STOP ORDER (VSD) SELECT ACK | STOP ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | STOP ORDER (VSD) SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | JET | STOP ORDER (VSD) EXECUTE | STOP ORDER (VSD) EXECUTE | STOP ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | STOP CONFIRMATION |  |  |  | 40 | RUN STATUS = FORWARD or RUN STATUS = REVERSE |  | STOP ORDER (VSD) EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = STOP | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | JET | STOP ORDER (VSD) EXECUTE ACK | STOP ORDER (VSD) EXECUTE ACK | STOP ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | STOP ORDER (VSD) EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | JET | FORWARD ORDER (VSD) SELECT | FORWARD ORDER (VSD) SELECT | FORWARD DIRECTION ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | FORWARD SELECTION |  |  |  | 2 | RUN STATUS = STOP |  | FORWARD ORDER (VSD) SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | JET | FORWARD ORDER (VSD) SELECT ACK | FORWARD ORDER (VSD) SELECT ACK | FORWARD DIRECTION ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | FORWARD ORDER (VSD) SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | JET | FORWARD ORDER (VSD) EXECUTE | FORWARD ORDER (VSD) EXECUTE | FORWARD DIRECTION ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | FORWARD CONFIRMATION |  |  |  | 40 | RUN STATUS = STOP |  | FORWARD ORDER (VSD) EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = FORWARD | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | JET | FORWARD ORDER (VSD) EXECUTE ACK | FORWARD ORDER (VSD) EXECUTE ACK | FORWARD DIRECTION ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | FORWARD ORDER (VSD) EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | JET | REVERSE ORDER (VSD) SELECT | REVERSE ORDER (VSD) SELECT | REVERSE DIRECTION ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | REVERSE SELECTION |  |  |  | 2 | RUN STATUS = STOP |  | REVERSE ORDER (VSD) SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | JET | REVERSE ORDER (VSD) SELECT ACK | REVERSE ORDER (VSD) SELECT ACK | REVERSE DIRECTION ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | REVERSE ORDER (VSD) SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | JET | REVERSE ORDER (VSD) EXECUTE | REVERSE ORDER (VSD) EXECUTE | REVERSE DIRECTION ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | REVERSE CONFIRMATION |  |  |  | 40 | RUN STATUS = STOP |  | REVERSE ORDER (VSD) EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = REVERSE | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | JET | REVERSE ORDER (VSD) EXECUTE ACK | REVERSE ORDER (VSD) EXECUTE ACK | REVERSE DIRECTION ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | REVERSE ORDER (VSD) EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | JET | FAN AVAILABILITY STATUS | FAN AVAILABILITY STATUS | FAN UNAVAILABLE STATUS | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | AVAILABLE | UNAVAILABLE |  |  | AVAILABLE | 0: None, 1: Crit | FAN AVAILABILITY STATUS : AVAILABLE/UNAVAILABLE | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | JET | CIRCUIT BREAKER POSITION | CIRCUIT BREAKER OPEN | VSD CIRCUIT BREAKER OPEN | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | OPEN | CLOSE |  |  | OPEN | 0: None, 1: None | CIRCUIT BREAKER POSITION : OPEN/CLOSE | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | JET | CIRCUIT BREAKER TRIPPED STATUS | CIRCUIT BREAKER OUTAGE | VSD CIRCUIT BREAKER FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Crit | CIRCUIT BREAKER TRIPPED STATUS : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | JET | FAN HEATER CIRCUIT BREAKER POSITION | FAN HEATER CIRCUIT BREAKER OPEN | FAN HEATER CIRCUIT BREAKER OPEN | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | OPEN | CLOSE |  |  | OPEN | 0: None, 1: None | FAN HEATER CIRCUIT BREAKER POSITION : OPEN/CLOSE | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | JET | FAN HEATER CIRCUIT BREAKER TRIPPED STATUS | FAN HEATER CIRCUIT BREAKER OUTAGE | FAN HEATER CIRCUIT BREAKER FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | FAN HEATER CIRCUIT BREAKER TRIPPED STATUS : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | JET | FORWARD START-UP MISMATCH OUTAGE STATUS | FORWARD START-UP MISMATCH OUTAGE | FORWARD COMMAND MISMATCH ALARM | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | FORWARD START-UP MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | JET | REVERSE START-UP MISMATCH OUTAGE STATUS | REVERSE START-UP MISMATCH OUTAGE | REVERSE COMMAND MISMATCH ALARM | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | REVERSE START-UP MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | JET | STOP MISMATCH OUTAGE STATUS | STOP MISMATCH OUTAGE | STOP COMMAND MISMATCH ALARM | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | STOP MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | JET | WINDING TEMPERATURE STATUS | WINDING TEMPERATURE | WINDING TEMPERATURE FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | WINDING TEMPERATURE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | JET | FRONT BEARING TEMPERATURE STATUS | FRONT BEARING TEMPERATURE 1 | FRONT BEARING TEMPERATURE 1 FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | FRONT BEARING TEMPERATURE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | JET | REAR BEARING TEMPERATURE STATUS | REAR BEARING TEMPERATURE 1 | REAR BEARING TEMPERATURE 1 FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | REAR BEARING TEMPERATURE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | JET | VIBRATION 1ST LEVEL STATUS | VIBRATION 1ST LEVEL | VIBRATION 1ST LEVEL ALARM | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VIBRATION 1ST LEVEL STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | JET | VIBRATION 2ND LEVEL STATUS | VIBRATION 2ND LEVEL | VIBRATION 2ND LEVEL FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | VIBRATION 2ND LEVEL STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | JET | MORE THAN 10 STARTUP PER HOUR STATUS | MORE THAN 6 STARTUP PER HOUR | MORE THAN 6 STARTUP PER HOUR | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | MORE THAN 10 STARTUP PER HOUR STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | JET | RUNNING HOURS | RUNNING HOURS | RUNNING HOURS | Meter | Daily | AI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | h | 0 | 65535 | [14 empty] | UINT | [10 empty] | #NAME? |  |  | NO | TODO
B0.9 | Y | +
B1.3 | N | TUN | TVS | TVD | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | OFF | LOCAL | REMOTE | INCONSISTANT | REMOTE | 0: Crit, 1: Maj, 2: None, 3: Crit | ELECTRICAL PANEL SELECTOR SWITCH STATUS : OFF/LOCAL/REMOTE/INCONSISTANT | [37 empty] | #NAME? |  |  | YES | TODO
B1.3 | N | TUN | TVS | TVD | OPERATING MODE | OPERATING MODE | OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP) | Operational Event |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | AUTO SCADA | MANUAL SCADA |  |  | AUTO SCADA | 0: None, 1: None | OPERATING MODE : AUTO SCADA/MANUAL SCADA | [37 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | TVD | ARRAY STATUS | STATUS | DAMPER OPENED STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INCONSISTANT | OPEN | CLOSED | INCONSISTANT | CLOSED | 0: Maj, 1: None, 2: None, 3: Crit | ARRAY STATUS : INCONSISTANT/OPEN/CLOSED/INCONSISTANT | [37 empty] | #NAME? |  |  | YES | TODO
B1.1 | N | TUN | TVS | TVD | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | Command |  | DO | SIL0 | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE AUTO MODE |  |  |  | 10 | OPERATING MODE = MANUAL SCADA |  | OPERATING MODE = AUTO SCADA | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVD | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 2 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVD | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVD | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 10 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE EXECUTE ACK = ACKNOWLEDGE and OPERATING MODE = MANUAL SCADA | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVD | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVD | OPEN ORDER SELECT | OPEN ORDER SELECT | OPEN ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | OPEN SELECTION |  |  |  | 2 | STATUS = CLOSE |  | OPEN ORDER SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVD | OPEN ORDER SELECT ACK | OPEN ORDER SELECT ACK | OPEN ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | OPEN ORDER SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVD | OPEN ORDER EXECUTE | OPEN ORDER EXECUTE | OPEN ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | OPEN CONFIRMATION |  |  |  | 40 | STATUS = CLOSE |  | OPEN ORDER EXECUTE ACK = ACKNOWLEDGE and STATUS = OPEN | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVD | OPEN ORDER EXECUTE ACK | OPEN ORDER EXECUTE ACK | OPEN ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | OPEN ORDER EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVD | CLOSE ORDER SELECT | CLOSE ORDER SELECT | CLOSE ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | CLOSE SELECTION |  |  |  | 2 | STATUS = OPEN |  | CLOSE ORDER SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVD | CLOSE ORDER SELECT ACK | CLOSE ORDER SELECT ACK | CLOSE ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | CLOSE ORDER SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVD | CLOSE ORDER EXECUTE | CLOSE ORDER EXECUTE | CLOSE ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | CLOSE CONFIRMATION |  |  |  | 40 | STATUS = OPEN |  | CLOSE ORDER EXECUTE ACK = ACKNOWLEDGE and STATUS = CLOSE | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | TVD | CLOSE ORDER EXECUTE ACK | CLOSE ORDER EXECUTE ACK | CLOSE ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | CLOSE ORDER EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | TVD | DAMPER SUPPLY CIRCUIT BREAKER POSITION | DAMPER SUPPLY CIRCUIT BREAKER OPEN | DAMPER SUPPLY CIRCUIT BREAKER OPEN | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | OPEN | CLOSE |  |  | OPEN | 0: None, 1: None | DAMPER SUPPLY CIRCUIT BREAKER POSITION : OPEN/CLOSE | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | TVD | DAMPER SUPPLY CIRCUIT BREAKER TRIPPED STATUS | DAMPER SUPPLY CIRCUIT BREAKER OUTAGE | DAMPER SUPPLY CIRCUIT BREAKER FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Crit | DAMPER SUPPLY CIRCUIT BREAKER TRIPPED STATUS : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | TVD | OPEN MISMATCH OUTAGE STATUS | FAIL TO OPEN STATUS | OPEN MISMATCH ALARM | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | OPEN MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | TVD | CLOSE MISMATCH OUTAGE STATUS | FAIL TO CLOSE STATUS | CLOSE MISMATCH ALARM | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | CLOSE MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | Y | + |  |  | ISOLATION DAMPER (IDP)
B1.3 | N | TUN | TVS | IDP | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | OFF | LOCAL | REMOTE | INCONSISTANT | REMOTE | 0: Crit, 1: Maj, 2: None, 3: Crit | ELECTRICAL PANEL SELECTOR SWITCH STATUS : OFF/LOCAL/REMOTE/INCONSISTANT | [37 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | IDP | ARRAY STATUS | STATUS | DAMPER OPENED STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INCONSISTANT | OPEN | CLOSED | INCONSISTANT | CLOSED | 0: Maj, 1: None, 2: None, 3: Crit | ARRAY STATUS : INCONSISTANT/OPEN/CLOSED/INCONSISTANT | [37 empty] | #NAME? |  |  | YES | TODO
B1.3 | N | TUN | TVS | IDP | DAMPER SUPPLY CIRCUIT BREAKER POSITION | IDP-MCB-H closed status | IDP-MCB-H closed status | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | OPEN | CLOSE |  |  | OPEN | 0: None, 1: None | DAMPER SUPPLY CIRCUIT BREAKER POSITION : OPEN/CLOSE | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | IDP | DAMPER SUPPLY CIRCUIT BREAKER TRIPPED STATUS | IDP- MCB-H tripped status | IDP- MCB-H tripped status | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Crit | DAMPER SUPPLY CIRCUIT BREAKER TRIPPED STATUS : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | IDP | OPEN MISMATCH OUTAGE STATUS | FAIL TO OPEN STATUS | OPEN MISMATCH ALARM | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | OPEN MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | IDP | CLOSE MISMATCH OUTAGE STATUS | FAIL TO CLOSE STATUS | CLOSE MISMATCH ALARM | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | CLOSE MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B0.9 | Y | + |  |  | MOTORIZED SMOKE FIRE DAMPER (MSFD)
B1.5 | N | TUN | TVS | MSFD | ARRAY STATUS | STATUS | DAMPER OPENED STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INCONSISTANT | OPEN | CLOSED | INCONSISTANT | CLOSED | 0: Maj, 1: None, 2: None, 3: Crit | ARRAY STATUS : INCONSISTANT/OPEN/CLOSED/INCONSISTANT | [37 empty] | #NAME? |  |  | YES | TODO
B1.5 | N | TUN | TVS | MSFD | DAMPER SUPPLY CIRCUIT BREAKER POSITION | MSFD - CON- MCB closed status | MSFD - CON- MCB closed status | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | OPEN | CLOSE |  |  | OPEN | 0: None, 1: None | DAMPER SUPPLY CIRCUIT BREAKER POSITION : OPEN/CLOSE | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | MSFD | DAMPER SUPPLY CIRCUIT BREAKER TRIPPED STATUS | MSFD - CON- MCB tripped status | MSFD - CON- MCB tripped status | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Crit | DAMPER SUPPLY CIRCUIT BREAKER TRIPPED STATUS : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | MSFD | LOCAL MODE STATUS |  |  | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | AUTO | LOCAL |  |  | AUTO | 0: None, 1: Crit | LOCAL MODE STATUS : AUTO/LOCAL | [37 empty] | #NAME? |  |  | NO | TODO
B0.9 | Y | + |  |  | OUTDOOR TEMPERATURE SENSOR (OTS)
B1.2 | N | TUN | TVS | OTS | AVAILABILITY STATUS | AVAILABILITY STATUS | UNAVAILABLE STATUS | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | AVAILABLE | UNAVAILABLE |  |  | AVAILABLE | 0: None, 1: Maj | AVAILABILITY STATUS : AVAILABLE/UNAVAILABLE | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | Y | TUN | TVS | OTS | TEMPERATURE OUTAGE STATUS | SENSOR OUTAGE | SENSOR FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | TEMPERATURE OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | OTS | AVERAGE TEMPERATURE EXCLUSION STATUS | AVERAGE TEMPERATURE EXCLUSION | AVERAGE TEMPERATURE EXCLUSION | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | AVERAGE TEMPERATURE EXCLUSION STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B0.9 | N | TUN | TVS | OTS | TEMPERATURE MEASUREMENT | TEMPERATURE MEASUREMENT | TEMPERATURE MEASUREMENT | Meter | Daily | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B1.1 | Y | + |  |  | TUNNEL TEMPERATURE/HUMIDITY SENSOR (TTS)
B1.1 | N | TUN | TVS | TTS | AVAILABILITY STATUS | AVAILABILITY STATUS | UNAVAILABLE STATUS | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | AVAILABLE | UNAVAILABLE |  |  | AVAILABLE | 0: None, 1: Maj | AVAILABILITY STATUS : AVAILABLE/UNAVAILABLE | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TTS | TEMPERATURE SENSOR OUTAGE STATUS | TEMPERATURE SENSOR OUTAGE | TEMPERATURE SENSOR FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | TEMPERATURE SENSOR OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TTS | HUMIDITY SENSOR OUTAGE STATUS | HUMIDITY SENSOR OUTAGE | HUMIDITY SENSOR FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | HUMIDITY SENSOR OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | TTS | AVERAGE TEMPERATURE EXCLUSION STATUS | AVERAGE TEMPERATURE EXCLUSION | AVERAGE TEMPERATURE EXCLUSION | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | AVERAGE TEMPERATURE EXCLUSION STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B0.9 | N | TUN | TVS | TTS | TEMPERATURE MEASUREMENT | TEMPERATURE MEASUREMENT | TEMPERATURE MEASUREMENT | Meter | Daily | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B0.9 | N | TUN | TVS | TTS | HUMIDITY MEASUREMENT | HUMIDITY MEASUREMENT | HUMIDITY MEASUREMENT | Meter | Daily | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | % | 0 | 100 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B0.9 | Y | + |  |  | VELOCITY SENSOR (VES)
B1.1 | N | TUN | TVS | VS | AVAILABILITY STATUS | AVAILABILITY STATUS | UNAVAILABLE STATUS | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | AVAILABLE | UNAVAILABLE |  |  | AVAILABLE | 0: None, 1: Maj | AVAILABILITY STATUS : AVAILABLE/UNAVAILABLE | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | Y | TUN | TVS | VS | SENSOR OUTAGE STATUS | SENSOR OUTAGE | SENSOR FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SENSOR OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B0.9 | N | TUN | TVS | VS | VELOCITY MEASUREMENT | VELOCITY MEASUREMENT | VELOCITY MEASUREMENT | Meter | Daily | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | [16 empty] | m/s | -10 | 10 | [14 empty] | FLOAT | [10 empty] | #NAME? |  |  | YES | TODO
B0.9 | Y | + |  |  | AIR HANDLING UNIT
B1.3 | N | TUN | TVS | AHU | CONTROL MODE | OPERATING MODE | OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP) | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | REMOTE | LOCAL |  |  | REMOTE | 0: None, 1: Crit | CONTROL MODE : REMOTE/LOCAL | [37 empty] | #NAME? |  |  | YES | TODO
B1.3 | N | TUN | TVS | AHU | RUN STATUS | STATUS | RUN | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | STOPPED | RUNNING |  |  | STOPPED | 0: None, 1: None | RUN STATUS : STOPPED/RUNNING | [37 empty] | #NAME? |  |  | YES | TODO
B0.9 | Y | + |  |  | PRESSURIZATION FAN
B1.3 | N | TUN | TVS | PFA | CONTROL MODE | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | REMOTE | LOCAL |  |  | REMOTE | 0: None, 1: Crit | CONTROL MODE : REMOTE/LOCAL | [37 empty] | #NAME? |  |  | YES | TODO
B1.3 | N | TUN | TVS | PFA | OPERATING MODE | OPERATING MODE | OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP) | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | AUTO SCADA | MANUAL SCADA |  |  | AUTO SCADA | 0: None, 1: Maj | OPERATING MODE : AUTO SCADA/MANUAL SCADA | [37 empty] | #NAME? |  |  | YES | TODO
B1.3 | N | TUN | TVS | PFA | RUN STATUS | STATUS | RUN | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | STOPPED | RUNNING |  |  | STOPPED | 0: None, 1: None | RUN STATUS : STOPPED/RUNNING | [37 empty] | #NAME? |  |  | YES | TODO
B1.1 | N | TUN | TVS | PFA | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | Command |  | DO | SIL0 | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE AUTO MODE |  |  |  | 10 | OPERATING MODE = MANUAL SCADA |  | OPERATING MODE = AUTO SCADA | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | PFA | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 2 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | PFA | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | PFA | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 10 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE EXECUTE ACK = ACKNOWLEDGE and OPERATING MODE = MANUAL SCADA | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | PFA | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | PFA | RUN ORDER SELECT | RUN ORDER SELECT | RUN ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | RUN SELECTION |  |  |  | 2 | RUN STATUS = STOPPED |  | RUN ORDER SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | PFA | RUN ORDER SELECT ACK | RUN ORDER SELECT ACK | RUN ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | RUN ORDER SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | PFA | RUN ORDER EXECUTE | RUN ORDER EXECUTE | RUN ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | RUN CONFIRMATION |  |  |  | 40 | RUN STATUS = STOPPED |  | RUN ORDER EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = RUNNING | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | PFA | RUN ORDER EXECUTE ACK | RUN ORDER EXECUTE ACK | RUN ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | RUN ORDER EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | PFA | STOP ORDER SELECT | STOP ORDER SELECT | STOP ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | STOP SELECTION |  |  |  | 2 | RUN STATUS = RUNNING |  | STOP ORDER SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | PFA | STOP ORDER SELECT ACK | STOP ORDER SELECT ACK | STOP ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | STOP ORDER SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | PFA | STOP ORDER EXECUTE | STOP ORDER EXECUTE | STOP ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | STOP CONFIRMATION |  |  |  | 40 | RUN STATUS = RUNNING |  | STOP ORDER EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = STOPPED | [28 empty] | #NAME? |  |  | NO | TODO
B1.1 | N | TUN | TVS | PFA | STOP ORDER EXECUTE ACK | STOP ORDER EXECUTE ACK | STOP ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | STOP ORDER EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | PFA | START MISMATCH STATUS | START MISMATCH | START MISMATCH | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | START MISMATCH STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.2 | N | TUN | TVS | PFA | STOP MISMATCH STATUS | STOP MISMATCH | STOP MISMATCH | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | STOP MISMATCH STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | Y | + |  |  | EXTRACT FAN (for Pearl and fox Hill station)
B1.3 | N | TUN | TVS | EXF | CONTROL MODE | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | REMOTE | LOCAL |  |  | REMOTE | 0: None, 1: Crit | CONTROL MODE : REMOTE/LOCAL | [37 empty] | #NAME? |  |  | YES | TODO
B1.3 | N | TUN | TVS | EXF | OPERATING MODE | OPERATING MODE | OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP) | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | AUTO SCADA | MANUAL SCADA |  |  | AUTO SCADA | 0: None, 1: Maj | OPERATING MODE : AUTO SCADA/MANUAL SCADA | [37 empty] | #NAME? |  |  | YES | TODO
B1.3 | N | TUN | TVS | EXF | RUN STATUS | STATUS | RUN | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | STOPPED | RUNNING |  |  | STOPPED | 0: None, 1: None | RUN STATUS : STOPPED/RUNNING | [37 empty] | #NAME? |  |  | YES | TODO
B1.3 | N | TUN | TVS | EXF | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | Command |  | DO | SIL0 | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE AUTO MODE |  |  |  | 10 | OPERATING MODE = MANUAL SCADA |  | OPERATING MODE = AUTO SCADA | [28 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | EXF | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 2 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | EXF | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | EXF | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 10 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE EXECUTE ACK = ACKNOWLEDGE and OPERATING MODE = MANUAL SCADA | [28 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | EXF | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | EXF | RUN ORDER SELECT | RUN ORDER SELECT | RUN ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | RUN SELECTION |  |  |  | 2 | RUN STATUS = STOPPED |  | RUN ORDER SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | EXF | RUN ORDER SELECT ACK | RUN ORDER SELECT ACK | RUN ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | RUN ORDER SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | EXF | RUN ORDER EXECUTE | RUN ORDER EXECUTE | RUN ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | RUN CONFIRMATION |  |  |  | 40 | RUN STATUS = STOPPED |  | RUN ORDER EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = RUNNING | [28 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | EXF | RUN ORDER EXECUTE ACK | RUN ORDER EXECUTE ACK | RUN ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | RUN ORDER EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | EXF | STOP ORDER SELECT | STOP ORDER SELECT | STOP ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | STOP SELECTION |  |  |  | 2 | RUN STATUS = RUNNING |  | STOP ORDER SELECT ACK = ACKNOWLEDGE | [28 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | EXF | STOP ORDER SELECT ACK | STOP ORDER SELECT ACK | STOP ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | STOP ORDER SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | EXF | STOP ORDER EXECUTE | STOP ORDER EXECUTE | STOP ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | #N/A | [7 empty] | NONE | STOP CONFIRMATION |  |  |  | 40 | RUN STATUS = RUNNING |  | STOP ORDER EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = STOPPED | [28 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | EXF | STOP ORDER EXECUTE ACK | STOP ORDER EXECUTE ACK | STOP ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | STOP ORDER EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | EXF | START MISMATCH STATUS | START MISMATCH | START MISMATCH | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | START MISMATCH STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.3 | N | TUN | TVS | EXF | STOP MISMATCH STATUS | STOP MISMATCH | STOP MISMATCH | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | STOP MISMATCH STATUS : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B0.9 | Y | + |  |  | SMOKE CURTAINS
B1.3 | N | TUN | TVS | SMC | STATE | STATE | STATE | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | RAISED | DOWN |  |  | RAISED | 0: None, 1: Crit | STATE : RAISED/DOWN | [37 empty] | #NAME? |  |  | YES | TODO
B0.9 | Y | + |  |  | STATION ENTRANCE DOOR
B1.7 | N | TUN | TVS | SED | STATE | STATE | STATE | Operational Event |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSED | OPEN |  |  | CLOSED | 0: None, 1: None | STATE : CLOSED/OPEN | [37 empty] | #NAME? |  |  | YES | TODO
B1.7 | N | TUN | TVS | SED | OPEN ORDER SENT BY TVS | OPEN ORDER SENT BY TVS | OPEN ORDER SENT BY TVS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | OPEN ORDER SENT BY TVS : INACTIVE/ACTIVE | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | Y | + |  |  | STATION PLC CONTROL BAY
B1.5 | N | TUN | TVS | SPLCMMS | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | 240VAC SUPPLY VOLTAGE PRESENCE | 240VAC SUPPLY VOLTAGE PRESENCE | 240VAC SUPPLY VOLTAGE PRESENCE | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | 240VAC SUPPLY VOLTAGE PRESENCE : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | VOLTAGE RELAY CIRCUIT BREAKER OPEN | VOLTAGE RELAY CIRCUIT BREAKER OPEN | VOLTAGE RELAY CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VOLTAGE RELAY CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | VOLTAGE RELAY CIRCUIT BREAKER FAULT | VOLTAGE RELAY CIRCUIT BREAKER FAULT | VOLTAGE RELAY CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VOLTAGE RELAY CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | CABINET SOCKETS CIRCUIT BREAKERS OPEN | CABINET SOCKETS CIRCUIT BREAKERS OPEN | CABINET SOCKETS CIRCUIT BREAKERS OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | CABINET SOCKETS CIRCUIT BREAKERS OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | CABINET SOCKETS CIRCUIT BREAKERS FAULT | CABINET SOCKETS CIRCUIT BREAKERS FAULT | CABINET SOCKETS CIRCUIT BREAKERS FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | CABINET SOCKETS CIRCUIT BREAKERS FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | SERVICES CIRCUIT BREAKER OPEN | SERVICES CIRCUIT BREAKER OPEN | SERVICES CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | SERVICES CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | SERVICES CIRCUIT BREAKER FAULT | SERVICES CIRCUIT BREAKER FAULT | SERVICES CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | SERVICES CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | UPS CIRCUIT BREAKER OPEN | UPS CIRCUIT BREAKER OPEN | UPS CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | UPS CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | UPS CIRCUIT BREAKER FAULT | UPS CIRCUIT BREAKER FAULT | UPS CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | UPS CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | UPS DISCONNECTING SWITCH OPEN | UPS DISCONNECTING SWITCH OPEN | UPS DISCONNECTING SWITCH OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | UPS DISCONNECTING SWITCH OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | UPS FAULT | UPS FAULT | UPS FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | UPS FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | SWITCH CIRCUIT BREAKER OPEN | SWITCH CIRCUIT BREAKER OPEN | SWITCH CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SWITCH CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | SWITCH CIRCUIT BREAKER FAULT | SWITCH CIRCUIT BREAKER FAULT | SWITCH CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SWITCH CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | LCP CIRCUIT BREAKER OPEN | LCP CIRCUIT BREAKER OPEN | LCP CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | LCP CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | LCP CIRCUIT BREAKER FAULT | LCP CIRCUIT BREAKER FAULT | LCP CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | LCP CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | PLC SUPPLY 1 CIRCUIT BREAKER OPEN | PLC SUPPLY 1 CIRCUIT BREAKER OPEN | PLC SUPPLY 1 CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | PLC SUPPLY 1 CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | PLC SUPPLY 1 CIRCUIT BREAKER FAULT | PLC SUPPLY 1 CIRCUIT BREAKER FAULT | PLC SUPPLY 1 CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | PLC SUPPLY 1 CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | PLC SUPPLY 2 CIRCUIT BREAKER OPEN | PLC SUPPLY 2 CIRCUIT BREAKER OPEN | PLC SUPPLY 2 CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | PLC SUPPLY 2 CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | PLC SUPPLY 2 CIRCUIT BREAKER FAULT | PLC SUPPLY 2 CIRCUIT BREAKER FAULT | PLC SUPPLY 2 CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | PLC SUPPLY 2 CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.5 | N | TUN | TVS | SPLCMMS | SURGE ARRESTER TRIGGERED | SURGE ARRESTER TRIGGERED | SURGE ARRESTER TRIGGERED | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SURGE ARRESTER TRIGGERED : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | Y | + |  |  | MASTER PLC CONTROL BAY
B1.6 | N | TUN | TVS | MPLCMMS | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | 240VAC SUPPLY VOLTAGE PRESENCE | 240VAC SUPPLY VOLTAGE PRESENCE | 240VAC SUPPLY VOLTAGE PRESENCE | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | 240VAC SUPPLY VOLTAGE PRESENCE : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | VOLTAGE RELAY CIRCUIT BREAKER OPEN | VOLTAGE RELAY CIRCUIT BREAKER OPEN | VOLTAGE RELAY CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VOLTAGE RELAY CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | VOLTAGE RELAY CIRCUIT BREAKER FAULT | VOLTAGE RELAY CIRCUIT BREAKER FAULT | VOLTAGE RELAY CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VOLTAGE RELAY CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | CABINET SOCKETS CIRCUIT BREAKER OPEN | CABINET SOCKETS CIRCUIT BREAKER OPEN | CABINET SOCKETS CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | CABINET SOCKETS CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | CABINET SOCKETS CIRCUIT BREAKER FAULT | CABINET SOCKETS CIRCUIT BREAKER FAULT | CABINET SOCKETS CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | CABINET SOCKETS CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | SERVICES CIRCUIT BREAKER OPEN | SERVICES CIRCUIT BREAKER OPEN | SERVICES CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | SERVICES CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | SERVICES CIRCUIT BREAKER FAULT | SERVICES CIRCUIT BREAKER FAULT | SERVICES CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | SERVICES CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | SWITCH 1 CIRCUIT BREAKER OPEN | SWITCH 1 CIRCUIT BREAKER OPEN | SWITCH 1 CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SWITCH 1 CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | SWITCH 1 CIRCUIT BREAKER FAULT | SWITCH 1 CIRCUIT BREAKER FAULT | SWITCH 1 CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SWITCH 1 CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | SWITCH 2 CIRCUIT BREAKER OPEN | SWITCH 2 CIRCUIT BREAKER OPEN | SWITCH 2 CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SWITCH 2 CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | SWITCH 2 CIRCUIT BREAKER FAULT | SWITCH 2 CIRCUIT BREAKER FAULT | SWITCH 2 CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SWITCH 2 CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | PLC A CIRCUIT BREAKER OPEN | PLC A CIRCUIT BREAKER OPEN | PLC A CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | PLC A CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | PLC A CIRCUIT BREAKER FAULT | PLC A CIRCUIT BREAKER FAULT | PLC A CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | PLC A CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | PLC B CIRCUIT BREAKER OPEN | PLC B CIRCUIT BREAKER OPEN | PLC B CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | PLC B CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | PLC B CIRCUIT BREAKER FAULT | PLC B CIRCUIT BREAKER FAULT | PLC B CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | PLC B CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MPLCMMS | SURGE ARRESTER TRIGGERED | SURGE ARRESTER TRIGGERED | SURGE ARRESTER TRIGGERED | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SURGE ARRESTER TRIGGERED : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | Y | + |  |  | Auxiliary MCB (MCB)
B1.6 | N | TUN | TVS | MCB | Auxiliary MCB trip status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Crit | Auxiliary MCB trip status : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MCB | Auxiliary MCB closed status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Auxiliary MCB closed status : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | Y | + |  |  | Auxiliary Switch Isolator (ADS)
B1.6 | N | TUN | TVS | ADS | Load breaker switched closed |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Load breaker switched closed : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | ADS | LBS Auxiliary Switch racked position |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | IN | OUT |  |  | IN | 0: None, 1: Maj | LBS Auxiliary Switch racked position : IN/OUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | Y | + |  |  | TRANSFORMER (TRF)
B1.6 | N | TUN | TVS | TRF | Emergency power off |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Emergency power off : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | TRF | Transformer fault |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Transformer fault : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | TRF | Emergency power cut |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Emergency power cut : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | TRF | Transformer high Temperature pre alarm |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Transformer high Temperature pre alarm : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | TRF | Transformer high Temperature Alarm |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Transformer high Temperature Alarm : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | Y | + |  |  | Auxiliary Circuit Breaker (ACB)
B1.6 | N | TUN | TVS | ACB | Main circuit breaker fault |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Main circuit breaker fault : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | ACB | Main circuit breaker open/closed status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Main circuit breaker open/closed status : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | ACB | Main CBC ACB racked position |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | IN | OUT |  |  | IN | 0: None, 1: Maj | Main CBC ACB racked position : IN/OUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | Y | + |  |  | Main distribution board cabinet (MDB)
B1.6 | N | TUN | TVS | MDB | Power normal MCSD 1 status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Power normal MCSD 1 status : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MDB | Power replacement MCSD 2 status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Power replacement MCSD 2 status : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MDB | MDB-01 MCSD 1 racked position |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | IN | OUT |  |  | IN | 0: None, 1: Maj | MDB-01 MCSD 1 racked position : IN/OUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MDB | MDB-01 MCSD 2 racked position |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | IN | OUT |  |  | IN | 0: None, 1: Maj | MDB-01 MCSD 2 racked position : IN/OUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MDB | Change over |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Change over : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MDB | Phase failure relay 1 |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Phase failure relay 1 : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MDB | Phase failure relay 2 |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Phase failure relay 2 : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MDB | MCB closed status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | MCB closed status : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MDB | MCB tripped status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | MCB tripped status : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MDB | Emergency power cut (push button) |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Emergency power cut (push button) : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MDB | MCCB 1 Incomer EL2 status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | MCCB 1 Incomer EL2 status : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MDB | MCCB 1 Incomer EL2 trip |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | MCCB 1 Incomer EL2 trip : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MDB | MCCB 2 Incomer EL2 status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | MCCB 2 Incomer EL2 status : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MDB | MCCB 2 Incomer EL2 trip |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | MCCB 2 Incomer EL2 trip : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MDB | MCCB 3 Incomer EL2 status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | MCCB 3 Incomer EL2 status : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MDB | MCCB 3 Incomer EL2 trip |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | MCCB 3 Incomer EL2 trip : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | Y | + |  |  | Electrical Control Panel (EL)
B1.6 | N | TUN | TVS | EL | Phase failure relay |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Phase failure relay : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | EL | LBS Main incomer isolator status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | LBS Main incomer isolator status : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | EL | UPS supply status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | UPS supply status : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | EL | UPS faulty |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | UPS faulty : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | EL | 24VDC UPS power status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | 24VDC UPS power status : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | Y | + |  |  | MCCB
B1.6 | N | TUN | TVS | MCCB | MCCB trip status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Crit | MCCB trip status : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | MCCB | MCCB closed status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | MCCB closed status : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | Y | + |  |  | LBS
B1.6 | N | TUN | TVS | LBS | LBS closed status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | LBS closed status : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | Y | + |  |  | Shaft Main distribution board cabinet (SMDB)
B1.6 | N | TUN | TVS | SMDB | Power normal ACB 1 closed |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Power normal ACB 1 closed : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | Power normal ACB 1 tripped |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | Power normal ACB 1 tripped : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | Power replacement ACB 2 closed status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Power replacement ACB 2 closed status : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | Power replacement ACB 2 Triped status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | Power replacement ACB 2 Triped status : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | MDB-01 ACB 1 racked position |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | IN | OUT |  |  | IN | 0: None, 1: Maj | MDB-01 ACB 1 racked position : IN/OUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | MDB-01 ACB 2 racked position |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | IN | OUT |  |  | IN | 0: None, 1: Maj | MDB-01 ACB 2 racked position : IN/OUT | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | Change over |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Change over : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | Phase failure relay 1 |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Phase failure relay 1 : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | Phase failure relay 2 |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Phase failure relay 2 : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | MCB closed status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | MCB closed status : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | MCB tripped status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | MCB tripped status : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | Emergency power cut (push button) |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Emergency power cut (push button) : NORMAL/FAULTY | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | Control cabinet MCCB PLC01 closed status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Control cabinet MCCB PLC01 closed status : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | Control cabinet MCCB PLC01 on tripped status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | Control cabinet MCCB PLC01 on tripped status : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | Control cabinet MCCB VSD1 closed status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Control cabinet MCCB VSD1 closed status : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | Control cabinet MCCB VSD1 on tripped status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | Control cabinet MCCB VSD1 on tripped status : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | Control cabinet MCCB VSD2 closed status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Control cabinet MCCB VSD2 closed status : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | Control cabinet MCCB VSD2 on tripped status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | Control cabinet MCCB VSD2 on tripped status : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | Spare E1 cabinet closed status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Spare E1 cabinet closed status : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | Spare E1 tripped status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | Spare E1 tripped status : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | Spare E2 cabinet closed status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Spare E2 cabinet closed status : CLOSE/OPEN | [37 empty] | #NAME? |  |  | NO | TODO
B1.6 | N | TUN | TVS | SMDB | Spare E2 tripped status |  |  | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | #N/A | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | Spare E2 tripped status : NORMAL/TRIPPED | [37 empty] | #NAME? |  |  | NO | TODO

## 2-Instance List
|  | LRT/QRC DESIGNATION |  | EQUIPMENT INSTANCES | [8 empty] | PRTU Configuration
Revision | isAComment | [Lusail] GBS Code | Description | Location | Sublocation | Class name | Equipment name | RTU Name | PLC Name | InvalidVar1 | InvalidVar2 | InvalidVar3 | Instance Id | External System Name | Device Unit Id | FEP Name | FEP instance Id | Short name | Unique ID code | SCADA Transfert function (Internal THALES) | Address | ToBeInstantiated
B0.9 | Y |  |  | BOCC
B0.9 | Y |  |  | MASTER PLCs (MPLC)
B2.1 | N |  | Master PLC at BOCC | TUN:BOCC | MPLC | MPLC | MPLC01 | BOCC_RTU | [9 empty] | &MPLC01 | TUN_BOCC_MPLC_MPLC01 |  |  | YES | TUNBOCCMPLCMPLC01 | 17
B1.6 | Y |  |  | MMS Equipment
B2.1 | N |  | Master PLC at BOCC (MMS) | TUN:BOCC | MMS | MPLCMMS | MPLC01 | BOCC_RTU | [9 empty] | &MPLC01 | TUN_BOCC_MMS_MPLC01 |  |  | YES | TUNBOCCMMSMPLC01 | 16
B0.9 | Y |  |  | Watchdog (WTGD)
B2.1 | N |  | Watchdog TVS Master PLC BOCC | TUN:BOCC | WTDG | WTDG | WTDG01 | BOCC_RTU | [9 empty] | &WTDG01 | TUN_BOCC_WTDG_WTDG01 |  |  | YES | TUNBOCCWTDGWTDG01 | 17
B0.9 | Y |  |  | Switch
B2.1 | N |  | Switch 1 | TUN:BOCC | SWI | SWI | SWI01 | BOCC_RTU | [9 empty] | &SWI01 | TUN_BOCC_SWI_SWI01 |  |  | YES | TUNBOCCSWISWI01 | 15
B2.1 | N |  | Switch 2 | TUN:BOCC | SWI | SWI | SWI02 | BOCC_RTU | [9 empty] | &SWI02 | TUN_BOCC_SWI_SWI02 |  |  | YES | TUNBOCCSWISWI02 | 15
B0.9 | Y |  |  | OCC
B0.9 | Y |  |  | MASTER PLCs (MPLC)
B2.1 | N |  | Master PLC at OCC | TUN:OCC | MPLC | MPLC | MPLC01 | OCC_RTU | [9 empty] | &MPLC01 | TUN_OCC_MPLC_MPLC01 |  |  | YES | TUNOCCMPLCMPLC01 | 16
B1.6 | Y |  |  | MMS Equipment
B2.1 | N |  | Master PLC at OCC (MMS) | TUN:OCC | MMS | MPLCMMS | MPLC01 | OCC_RTU | [9 empty] | &MPLC01 | TUN_OCC_MMS_MPLC01 |  |  | YES | TUNOCCMMSMPLC01 | 15
B0.9 | Y |  |  | Watchdog (WTGD)
B2.1 | N |  | Watchdog TVS Master PLC OCC | TUN:OCC | WTDG | WTDG | WTDG01 | OCC_RTU | [9 empty] | &WTDG01 | TUN_OCC_WTDG_WTDG01 |  |  | YES | TUNOCCWTDGWTDG01 | 16
B0.9 | Y |  |  | Switch
B2.1 | N |  | Switch 1 | TUN:OCC | SWI | SWI | SWI01 | OCC_RTU | [9 empty] | &SWI01 | TUN_OCC_SWI_SWI01 |  |  | YES | TUNOCCSWISWI01 | 14
B2.1 | N |  | Switch 2 | TUN:OCC | SWI | SWI | SWI02 | OCC_RTU | [9 empty] | &SWI02 | TUN_OCC_SWI_SWI02 |  |  | YES | TUNOCCSWISWI02 | 14
B1.5 | Y |  |  | MAIN UNDERGROUND LINE AVERAGE TEMPERATURE
B2.1 | N |  | MAIN UNDERGROUND AVERAGE TEMPERATURE | TUN:MUL | TEMP | MUL | MUL01 | OCC_RTU | [9 empty] | &MUL01 | TUN_MUL_TEMP_MUL01 |  |  | YES | TUNMULTEMPMUL01 | 15
B1.5 | Y |  |  | FOXHILL LINE AVERAGE TEMPERATURE
B2.1 | N |  | FOXHILL LINE AVERAGE TEMPERATURE | TUN:FXL | TEMP | FXL | FXL01 | OCC_RTU | [9 empty] | &FXL01 | TUN_FXL_TEMP_FXL01 |  |  | YES | TUNFXLTEMPFXL01 | 15
B1.5 | Y |  |  | TUNNEL NORMAL & CONGESTED VENTILATION MODES
B2.1 | N |  | TUNNEL NORMAL & CONGESTED VENTILATION MODES | TUN:OCC | MODES | VENTILATION | VENTILATION | OCC_RTU | [9 empty] | &VENTILATION | TUN_OCC_MODES_VENTILATION |  |  | YES | TUNMODESVENTILATION | 19
B1.5 | Y |  |  | EMERGENCY SCENARIOS
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1011 | OCC_RTU | [9 empty] | &SCENARIO1011 | TUN_OCC_EMERGENCY_SCENARIO1011 |  |  | YES | TUNEMERGENCYSCENARIO1011 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1012 | OCC_RTU | [9 empty] | &SCENARIO1012 | TUN_OCC_EMERGENCY_SCENARIO1012 |  |  | YES | TUNEMERGENCYSCENARIO1012 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1021 | OCC_RTU | [9 empty] | &SCENARIO1021 | TUN_OCC_EMERGENCY_SCENARIO1021 |  |  | YES | TUNEMERGENCYSCENARIO1021 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1022 | OCC_RTU | [9 empty] | &SCENARIO1022 | TUN_OCC_EMERGENCY_SCENARIO1022 |  |  | YES | TUNEMERGENCYSCENARIO1022 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1031 | OCC_RTU | [9 empty] | &SCENARIO1031 | TUN_OCC_EMERGENCY_SCENARIO1031 |  |  | YES | TUNEMERGENCYSCENARIO1031 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1032 | OCC_RTU | [9 empty] | &SCENARIO1032 | TUN_OCC_EMERGENCY_SCENARIO1032 |  |  | YES | TUNEMERGENCYSCENARIO1032 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1041 | OCC_RTU | [9 empty] | &SCENARIO1041 | TUN_OCC_EMERGENCY_SCENARIO1041 |  |  | YES | TUNEMERGENCYSCENARIO1041 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1042 | OCC_RTU | [9 empty] | &SCENARIO1042 | TUN_OCC_EMERGENCY_SCENARIO1042 |  |  | YES | TUNEMERGENCYSCENARIO1042 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1051 | OCC_RTU | [9 empty] | &SCENARIO1051 | TUN_OCC_EMERGENCY_SCENARIO1051 |  |  | YES | TUNEMERGENCYSCENARIO1051 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1052 | OCC_RTU | [9 empty] | &SCENARIO1052 | TUN_OCC_EMERGENCY_SCENARIO1052 |  |  | YES | TUNEMERGENCYSCENARIO1052 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1061 | OCC_RTU | [9 empty] | &SCENARIO1061 | TUN_OCC_EMERGENCY_SCENARIO1061 |  |  | YES | TUNEMERGENCYSCENARIO1061 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1062 | OCC_RTU | [9 empty] | &SCENARIO1062 | TUN_OCC_EMERGENCY_SCENARIO1062 |  |  | YES | TUNEMERGENCYSCENARIO1062 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1071 | OCC_RTU | [9 empty] | &SCENARIO1071 | TUN_OCC_EMERGENCY_SCENARIO1071 |  |  | YES | TUNEMERGENCYSCENARIO1071 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1072 | OCC_RTU | [9 empty] | &SCENARIO1072 | TUN_OCC_EMERGENCY_SCENARIO1072 |  |  | YES | TUNEMERGENCYSCENARIO1072 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1081 | OCC_RTU | [9 empty] | &SCENARIO1081 | TUN_OCC_EMERGENCY_SCENARIO1081 |  |  | YES | TUNEMERGENCYSCENARIO1081 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1082 | OCC_RTU | [9 empty] | &SCENARIO1082 | TUN_OCC_EMERGENCY_SCENARIO1082 |  |  | YES | TUNEMERGENCYSCENARIO1082 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1091 | OCC_RTU | [9 empty] | &SCENARIO1091 | TUN_OCC_EMERGENCY_SCENARIO1091 |  |  | YES | TUNEMERGENCYSCENARIO1091 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1092 | OCC_RTU | [9 empty] | &SCENARIO1092 | TUN_OCC_EMERGENCY_SCENARIO1092 |  |  | YES | TUNEMERGENCYSCENARIO1092 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1101 | OCC_RTU | [9 empty] | &SCENARIO1101 | TUN_OCC_EMERGENCY_SCENARIO1101 |  |  | YES | TUNEMERGENCYSCENARIO1101 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1102 | OCC_RTU | [9 empty] | &SCENARIO1102 | TUN_OCC_EMERGENCY_SCENARIO1102 |  |  | YES | TUNEMERGENCYSCENARIO1102 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1111 | OCC_RTU | [9 empty] | &SCENARIO1111 | TUN_OCC_EMERGENCY_SCENARIO1111 |  |  | YES | TUNEMERGENCYSCENARIO1111 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1112 | OCC_RTU | [9 empty] | &SCENARIO1112 | TUN_OCC_EMERGENCY_SCENARIO1112 |  |  | YES | TUNEMERGENCYSCENARIO1112 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1121 | OCC_RTU | [9 empty] | &SCENARIO1121 | TUN_OCC_EMERGENCY_SCENARIO1121 |  |  | YES | TUNEMERGENCYSCENARIO1121 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1122 | OCC_RTU | [9 empty] | &SCENARIO1122 | TUN_OCC_EMERGENCY_SCENARIO1122 |  |  | YES | TUNEMERGENCYSCENARIO1122 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1131 | OCC_RTU | [9 empty] | &SCENARIO1131 | TUN_OCC_EMERGENCY_SCENARIO1131 |  |  | YES | TUNEMERGENCYSCENARIO1131 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1132 | OCC_RTU | [9 empty] | &SCENARIO1132 | TUN_OCC_EMERGENCY_SCENARIO1132 |  |  | YES | TUNEMERGENCYSCENARIO1132 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1141 | OCC_RTU | [9 empty] | &SCENARIO1141 | TUN_OCC_EMERGENCY_SCENARIO1141 |  |  | YES | TUNEMERGENCYSCENARIO1141 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1142 | OCC_RTU | [9 empty] | &SCENARIO1142 | TUN_OCC_EMERGENCY_SCENARIO1142 |  |  | YES | TUNEMERGENCYSCENARIO1142 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1151 | OCC_RTU | [9 empty] | &SCENARIO1151 | TUN_OCC_EMERGENCY_SCENARIO1151 |  |  | YES | TUNEMERGENCYSCENARIO1151 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1152 | OCC_RTU | [9 empty] | &SCENARIO1152 | TUN_OCC_EMERGENCY_SCENARIO1152 |  |  | YES | TUNEMERGENCYSCENARIO1152 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1161 | OCC_RTU | [9 empty] | &SCENARIO1161 | TUN_OCC_EMERGENCY_SCENARIO1161 |  |  | YES | TUNEMERGENCYSCENARIO1161 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1162 | OCC_RTU | [9 empty] | &SCENARIO1162 | TUN_OCC_EMERGENCY_SCENARIO1162 |  |  | YES | TUNEMERGENCYSCENARIO1162 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1171 | OCC_RTU | [9 empty] | &SCENARIO1171 | TUN_OCC_EMERGENCY_SCENARIO1171 |  |  | YES | TUNEMERGENCYSCENARIO1171 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1172 | OCC_RTU | [9 empty] | &SCENARIO1172 | TUN_OCC_EMERGENCY_SCENARIO1172 |  |  | YES | TUNEMERGENCYSCENARIO1172 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2510 | OCC_RTU | [9 empty] | &SCENARIO2510 | TUN_OCC_EMERGENCY_SCENARIO2510 |  |  | YES | TUNEMERGENCYSCENARIO2510 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2520 | OCC_RTU | [9 empty] | &SCENARIO2520 | TUN_OCC_EMERGENCY_SCENARIO2520 |  |  | YES | TUNEMERGENCYSCENARIO2520 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2530 | OCC_RTU | [9 empty] | &SCENARIO2530 | TUN_OCC_EMERGENCY_SCENARIO2530 |  |  | YES | TUNEMERGENCYSCENARIO2530 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2540 | OCC_RTU | [9 empty] | &SCENARIO2540 | TUN_OCC_EMERGENCY_SCENARIO2540 |  |  | YES | TUNEMERGENCYSCENARIO2540 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2550 | OCC_RTU | [9 empty] | &SCENARIO2550 | TUN_OCC_EMERGENCY_SCENARIO2550 |  |  | YES | TUNEMERGENCYSCENARIO2550 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2560 | OCC_RTU | [9 empty] | &SCENARIO2560 | TUN_OCC_EMERGENCY_SCENARIO2560 |  |  | YES | TUNEMERGENCYSCENARIO2560 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2570 | OCC_RTU | [9 empty] | &SCENARIO2570 | TUN_OCC_EMERGENCY_SCENARIO2570 |  |  | YES | TUNEMERGENCYSCENARIO2570 | 24
B2.1 | N |  |  | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2580 | OCC_RTU | [9 empty] | &SCENARIO2580 | TUN_OCC_EMERGENCY_SCENARIO2580 |  |  | YES | TUNEMERGENCYSCENARIO2580 | 24
B0.9 | Y |  |  | MAR-01
B0.9 | Y |  |  | LOCAL CONTROL PANEL (LCP) [STATION HMI]
B2.1 | N |  | Local control panel | TUN:MAR01 | SCR | LCP | LCP01 | MAR01_RTU | [9 empty] | &LCP01 | TUN_MAR01_SCR_LCP01 |  |  | YES | TUNMAR01SCRLCP01 | 16
B1.5 | Y |  |  | FIRE MANUAL OVERRIDE PANEL (FMOP)
B2.1 | N |  | Fire control panel | TUN:MAR01 | SCR | FMOP | FMOP01 | MAR01_RTU | [9 empty] | &FMOP01 | TUN_MAR01_SCR_FMOP01 |  |  | YES | TUNMAR01SCRFMOP01 | 17
B0.9 | Y |  |  | Station PLC (SPLC)
B2.1 | N |  | Station PLC | TUN:MAR01 | TEL | SPLC | PLC01 | MAR01_RTU | [9 empty] | &PLC01 | TUN_MAR01_TEL_PLC01 |  |  | YES | TUNMAR01TELPLC01 | 16
B0.9 | Y |  |  | Switch (SWI)
B2.1 | N |  | Switch | TUN:MAR01 | TEL | SWI | SWI01 | MAR01_RTU | [9 empty] | &SWI01 | TUN_MAR01_TEL_SWI01 |  |  | YES | TUNMAR01TELSWI01 | 16
B0.9 | Y |  |  | PRESSURIZATION FAN (PFA)
B2.1 | N |  | Pressurization fan Lobby | TUN:MAR01 | NS01:PFA | PFA | CON-04 | MAR01_RTU | [9 empty] | &CON-04 | TUN_MAR01_NS01_PFA_CON-04 |  |  | YES | TUNMAR01NS01PFACON-04 | 21
B2.1 | N |  | Pressurization fan Staircase | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | MAR01_RTU | [9 empty] | &GRD-01 | TUN_MAR01_NS01_PFA_GRD-01 |  |  | YES | TUNMAR01NS01PFAGRD-01 | 21
B2.1 | N |  | Pressurization fan Lobby | TUN:MAR01 | SS01:PFA | PFA | CON-03 | MAR01_RTU | [9 empty] | &CON-03 | TUN_MAR01_SS01_PFA_CON-03 |  |  | YES | TUNMAR01SS01PFACON-03 | 21
B2.1 | N |  | Pressurization fan Staircase | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | MAR01_RTU | [9 empty] | &GRD-03 | TUN_MAR01_SS01_PFA_GRD-03 |  |  | YES | TUNMAR01SS01PFAGRD-03 | 21
B0.9 | Y |  |  | SMOKE CURTAINS (SMC)
B2.1 | N |  | Smoke Curtains 1 | TUN:MAR01 | SMC | SMC | SMC01 | MAR01_RTU | [9 empty] | &SMC01 | TUN_MAR01_SMC_SMC01 |  |  | YES | TUNMAR01SMCSMC01 | 16
B2.1 | N |  | Smoke Curtains 2 | TUN:MAR01 | SMC | SMC | SMC02 | MAR01_RTU | [9 empty] | &SMC02 | TUN_MAR01_SMC_SMC02 |  |  | YES | TUNMAR01SMCSMC02 | 16
B2.1 | N |  | Smoke Curtains 3 | TUN:MAR01 | SMC | SMC | SMC03 | MAR01_RTU | [9 empty] | &SMC03 | TUN_MAR01_SMC_SMC03 |  |  | YES | TUNMAR01SMCSMC03 | 16
B2.1 | N |  | Smoke Curtains 4 | TUN:MAR01 | SMC | SMC | SMC04 | MAR01_RTU | [9 empty] | &SMC04 | TUN_MAR01_SMC_SMC04 |  |  | YES | TUNMAR01SMCSMC04 | 16
B2.1 | N |  | Smoke Curtains 5 | TUN:MAR01 | SMC | SMC | SMC05 | MAR01_RTU | [9 empty] | &SMC05 | TUN_MAR01_SMC_SMC05 |  |  | YES | TUNMAR01SMCSMC05 | 16
B2.1 | N |  | Smoke Curtains 6 | TUN:MAR01 | SMC | SMC | SMC06 | MAR01_RTU | [9 empty] | &SMC06 | TUN_MAR01_SMC_SMC06 |  |  | YES | TUNMAR01SMCSMC06 | 16
B2.1 | N |  | Smoke Curtains 7 | TUN:MAR01 | SMC | SMC | SMC07 | MAR01_RTU | [9 empty] | &SMC07 | TUN_MAR01_SMC_SMC07 |  |  | YES | TUNMAR01SMCSMC07 | 16
B2.1 | N |  | Smoke Curtains 8 | TUN:MAR01 | SMC | SMC | SMC08 | MAR01_RTU | [9 empty] | &SMC08 | TUN_MAR01_SMC_SMC08 |  |  | YES | TUNMAR01SMCSMC08 | 16
B0.9 | Y |  |  | STATION ENTRANCE DOOR (SED)
B2.1 | N |  | Station entrance door 1 | TUN:MAR01 | SED | SED | SED01 | MAR01_RTU | [9 empty] | &SED01 | TUN_MAR01_SED_SED01 |  |  | YES | TUNMAR01SEDSED01 | 16
B2.1 | N |  | Station entrance door 2 | TUN:MAR01 | SED | SED | SED02 | MAR01_RTU | [9 empty] | &SED02 | TUN_MAR01_SED_SED02 |  |  | YES | TUNMAR01SEDSED02 | 16
B2.1 | N |  | Station entrance door 3 | TUN:MAR01 | SED | SED | SED03 | MAR01_RTU | [9 empty] | &SED03 | TUN_MAR01_SED_SED03 |  |  | YES | TUNMAR01SEDSED03 | 16
B2.1 | N |  | Station entrance door 4 | TUN:MAR01 | SED | SED | SED04 | MAR01_RTU | [9 empty] | &SED04 | TUN_MAR01_SED_SED04 |  |  | YES | TUNMAR01SEDSED04 | 16
B0.9 | Y |  |  | Outdoor temperature sensor (OTS)
B2.1 | N |  | Outdoor temperature sensor 1 | TUN:MAR01 | OTS | OTS | OTS001 | MAR01_RTU | [9 empty] | &OTS001 | TUN_MAR01_OTS_OTS001 |  |  | YES | TUNMAR01OTSOTS001 | 17
B2.1 | N |  | Outdoor temperature sensor 2 | TUN:MAR01 | OTS | OTS | OTS002 | MAR01_RTU | [9 empty] | &OTS002 | TUN_MAR01_OTS_OTS002 |  |  | YES | TUNMAR01OTSOTS002 | 17
B0.9 | Y |  |  | Tunnel ventilation fan (TVF)
B2.1 | N |  | North ShaftTunnel ventilation fan 1 | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | MAR01_RTU | [9 empty] | &VT1-TVF01 | TUN_MAR01_NS01_TVF_VT1-TVF01 |  |  | YES | TUNMAR01NS01TVFVT1-TVF01 | 24
B2.1 | N |  | North ShaftTunnel ventilation fan 2 | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | MAR01_RTU | [9 empty] | &VT2-TVF01 | TUN_MAR01_NS01_TVF_VT2-TVF01 |  |  | YES | TUNMAR01NS01TVFVT2-TVF01 | 24
B2.1 | N |  | South ShaftTunnel ventilation fan 3 | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | MAR01_RTU | [9 empty] | &VT3-TVF01 | TUN_MAR01_SS01_TVF_VT3-TVF01 |  |  | YES | TUNMAR01SS01TVFVT3-TVF01 | 24
B2.1 | N |  | SouthShaftTunnel ventilation fan 4 | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | MAR01_RTU | [9 empty] | &VT4-TVF01 | TUN_MAR01_SS01_TVF_VT4-TVF01 |  |  | YES | TUNMAR01SS01TVFVT4-TVF01 | 24
B0.9 | Y |  |  | Tunnel temperature & humidity sensor (TTS)
B2.1 | N |  | North Tunnel temperature sensor 1 | TUN:MAR01 | NS01:SENSOR | TTS | TS100269 | MAR01_RTU | [9 empty] | &TS100269 | TUN_MAR01_NS01_SENSOR_TS100269 |  |  | YES | TUNMAR01NS01SENSORTS100269 | 26
B2.1 | N |  | North Tunnel temperature sensor 2 | TUN:MAR01 | NS01:SENSOR | TTS | TS100222 | MAR01_RTU | [9 empty] | &TS100222 | TUN_MAR01_NS01_SENSOR_TS100222 |  |  | YES | TUNMAR01NS01SENSORTS100222 | 26
B2.1 | N |  | South Tunnel temperature sensor 1 | TUN:MAR01 | SS01:SENSOR | TTS | TS099914 | MAR01_RTU | [9 empty] | &TS099914 | TUN_MAR01_SS01_SENSOR_TS099914 |  |  | YES | TUNMAR01SS01SENSORTS099914 | 26
B2.1 | N |  | South Tunnel temperature sensor 2 | TUN:MAR01 | SS01:SENSOR | TTS | TS099816 | MAR01_RTU | [9 empty] | &TS099816 | TUN_MAR01_SS01_SENSOR_TS099816 |  |  | YES | TUNMAR01SS01SENSORTS099816 | 26
B0.9 | Y |  |  | Air velocity sensor (VS)
B2.1 | N |  | North Air velocity sensor 1 | TUN:MAR01 | NS01:SENSOR | VS | VS100253 | MAR01_RTU | [9 empty] | &VS100253 | TUN_MAR01_NS01_SENSOR_VS100253 |  |  | YES | TUNMAR01NS01SENSORVS100253 | 26
B2.1 | N |  | South Air velocity sensor 1 | TUN:MAR01 | SS01:SENSOR | VS | VS099848 | MAR01_RTU | [9 empty] | &VS099848 | TUN_MAR01_SS01_SENSOR_VS099848 |  |  | YES | TUNMAR01SS01SENSORVS099848 | 26
B0.9 | Y |  |  | TVS Damper : Tunnel damper (TDP)
B2.1 | N |  | North Shaft Tunnel damper 1 | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | MAR01_RTU | [9 empty] | &VT5-TDP01 | TUN_MAR01_NS01_DAMPER_VT5-TDP01 |  |  | YES | TUNMAR01NS01DAMPERVT5-TDP01 | 27
B2.1 | N |  | South Shaft Tunnel damper 2 | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | MAR01_RTU | [9 empty] | &VT6-TDP01 | TUN_MAR01_SS01_DAMPER_VT6-TDP01 |  |  | YES | TUNMAR01SS01DAMPERVT6-TDP01 | 27
B0.9 | Y |  |  | TVS Damper : Isolation damper (IDP)
B2.1 | N |  | Isolation damper 1 | TUN:MAR01 | NS01:DAMPER | IDP | VT1-IDP01 | MAR01_RTU | [9 empty] | &VT1-IDP01 | TUN_MAR01_NS01_DAMPER_VT1-IDP01 |  |  | YES | TUNMAR01NS01DAMPERVT1-IDP01 | 27
B2.1 | N |  | Isolation damper 2 | TUN:MAR01 | NS01:DAMPER | IDP | VT2-IDP01 | MAR01_RTU | [9 empty] | &VT2-IDP01 | TUN_MAR01_NS01_DAMPER_VT2-IDP01 |  |  | YES | TUNMAR01NS01DAMPERVT2-IDP01 | 27
B2.1 | N |  | Isolation damper 3 | TUN:MAR01 | SS01:DAMPER | IDP | VT3-IDP01 | MAR01_RTU | [9 empty] | &VT3-IDP01 | TUN_MAR01_SS01_DAMPER_VT3-IDP01 |  |  | YES | TUNMAR01SS01DAMPERVT3-IDP01 | 27
B2.1 | N |  | Isolation damper 4 | TUN:MAR01 | SS01:DAMPER | IDP | VT4-IDP01 | MAR01_RTU | [9 empty] | &VT4-IDP01 | TUN_MAR01_SS01_DAMPER_VT4-IDP01 |  |  | YES | TUNMAR01SS01DAMPERVT4-IDP01 | 27
B0.9 | Y |  |  | TVS Damper : Bypass damper (BDP)
B2.1 | N |  | North Shaft Bypass damper 1 | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | MAR01_RTU | [9 empty] | &FR1-BDP01 | TUN_MAR01_NS01_DAMPER_FR1-BDP01 |  |  | YES | TUNMAR01NS01DAMPERFR1-BDP01 | 27
B2.1 | N |  | South Shaft Bypass damper 2 | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | MAR01_RTU | [9 empty] | &FR2-BDP01 | TUN_MAR01_SS01_DAMPER_FR2-BDP01 |  |  | YES | TUNMAR01SS01DAMPERFR2-BDP01 | 27
B0.9 | Y |  |  | MEP Damper : Tunnel Cooling damper (TCDP)
B2.1 | N |  | North Shaft Tunnel Cooling damper 1 | TUN:MAR01 | NS01:DAMPER | MSFD | CON-54 | MAR01_RTU | [9 empty] | &CON-54 | TUN_MAR01_NS01_DAMPER_CON-54 |  |  | YES | TUNMAR01NS01DAMPERCON-54 | 24
B2.1 | N |  | South Shaft Tunnel Cooling damper 2 | TUN:MAR01 | SS01:DAMPER | MSFD | CON-63 | MAR01_RTU | [9 empty] | &CON-63 | TUN_MAR01_SS01_DAMPER_CON-63 |  |  | YES | TUNMAR01SS01DAMPERCON-63 | 24
B0.9 | Y |  |  | MEP damper : Station to exhaust duct Damper (SEDD)
B2.1 | N |  | North Shaft Station to exhaust duct damper 1 | TUN:MAR01 | NS01:DAMPER | MSFD | CON-51 | MAR01_RTU | [9 empty] | &CON-51 | TUN_MAR01_NS01_DAMPER_CON-51 |  |  | YES | TUNMAR01NS01DAMPERCON-51 | 24
B2.1 | N |  | North Shaft Station to exhaust duct damper 2 | TUN:MAR01 | NS01:DAMPER | MSFD | CON-56 | MAR01_RTU | [9 empty] | &CON-56 | TUN_MAR01_NS01_DAMPER_CON-56 |  |  | YES | TUNMAR01NS01DAMPERCON-56 | 24
B2.1 | N |  | South Shaft Station to exhaust duct damper 3 | TUN:MAR01 | SS01:DAMPER | MSFD | CON-61 | MAR01_RTU | [9 empty] | &CON-61 | TUN_MAR01_SS01_DAMPER_CON-61 |  |  | YES | TUNMAR01SS01DAMPERCON-61 | 24
B2.1 | N |  | South Shaft Station to exhaust duct damper 4 | TUN:MAR01 | SS01:DAMPER | MSFD | CON-66 | MAR01_RTU | [9 empty] | &CON-66 | TUN_MAR01_SS01_DAMPER_CON-66 |  |  | YES | TUNMAR01SS01DAMPERCON-66 | 24
B0.9 | Y |  |  | MEP damper : Station Cooling damper (SCD)
B2.1 | N |  | North Shaft Station Cooling damper 1 | TUN:MAR01 | NS01:DAMPER | MSFD | CON-52 | MAR01_RTU | [9 empty] | &CON-52 | TUN_MAR01_NS01_DAMPER_CON-52 |  |  | YES | TUNMAR01NS01DAMPERCON-52 | 24
B2.1 | N |  | North Shaft Station Cooling damper 2 | TUN:MAR01 | NS01:DAMPER | MSFD | CON-58 | MAR01_RTU | [9 empty] | &CON-58 | TUN_MAR01_NS01_DAMPER_CON-58 |  |  | YES | TUNMAR01NS01DAMPERCON-58 | 24
B2.1 | N |  | South Shaft Station Cooling damper 3 | TUN:MAR01 | SS01:DAMPER | MSFD | CON-59 | MAR01_RTU | [9 empty] | &CON-59 | TUN_MAR01_SS01_DAMPER_CON-59 |  |  | YES | TUNMAR01SS01DAMPERCON-59 | 24
B2.1 | N |  | South Shaft Station Cooling damper 4 | TUN:MAR01 | SS01:DAMPER | MSFD | CON-67 | MAR01_RTU | [9 empty] | &CON-67 | TUN_MAR01_SS01_DAMPER_CON-67 |  |  | YES | TUNMAR01SS01DAMPERCON-67 | 24
B0.9 | Y |  |  | Tunnel AIR HANDLING UNIT
B2.1 | N |  | North ShaftTunnel Air Handling Unit 1 | TUN:MAR01 | NS01:AHU | AHU | CON-05 | MAR01_RTU | [9 empty] | &CON-05 | TUN_MAR01_NS01_AHU_CON-05 |  |  | YES | TUNMAR01NS01AHUCON-05 | 21
B2.1 | N |  | North ShaftTunnel Air Handling Unit 2 | TUN:MAR01 | NS01:AHU | AHU | CON-06 | MAR01_RTU | [9 empty] | &CON-06 | TUN_MAR01_NS01_AHU_CON-06 |  |  | YES | TUNMAR01NS01AHUCON-06 | 21
B2.1 | N |  | South ShaftTunnel Air Handling Unit 1 | TUN:MAR01 | SS01:AHU | AHU | CON-07 | MAR01_RTU | [9 empty] | &CON-07 | TUN_MAR01_SS01_AHU_CON-07 |  |  | YES | TUNMAR01SS01AHUCON-07 | 21
B2.1 | N |  | South ShaftTunnel Air Handling Unit 2 | TUN:MAR01 | SS01:AHU | AHU | CON-08 | MAR01_RTU | [9 empty] | &CON-08 | TUN_MAR01_SS01_AHU_CON-08 |  |  | YES | TUNMAR01SS01AHUCON-08 | 21
B1.6 | Y |  |  | MMS Equipment
B2.1 | N |  | Station PLC (MMS) | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | MAR01_RTU | [9 empty] | &SPLC01 | TUN_MAR01_MMS_SPLC01 |  |  | YES | TUNMAR01MMSSPLC01 | 17
B1.6 | Y |  |  | Electrical Equipment
B2.1 | N |  | MAR01-EL2-LBS01 | TUN:MAR01 | MMS | ADS | EL2-LBS01 | MAR01_RTU | [9 empty] | &EL2-LBS01 | TUN_MAR01_MMS_EL2-LBS01 |  |  | YES | TUNMAR01MMSEL2-LBS01 | 20
B2.1 | N |  | MAR01-EL2-LBS02 | TUN:MAR01 | MMS | ADS | EL2-LBS02 | MAR01_RTU | [9 empty] | &EL2-LBS02 | TUN_MAR01_MMS_EL2-LBS02 |  |  | YES | TUNMAR01MMSEL2-LBS02 | 20
B2.1 | N |  | MAR01-MV-TRF01 | TUN:MAR01 | MMS | TRF | MV-TRF01 | MAR01_RTU | [9 empty] | &MV-TRF01 | TUN_MAR01_MMS_MV-TRF01 |  |  | YES | TUNMAR01MMSMV-TRF01 | 19
B2.1 | N |  | MAR01-MV-TRF02 | TUN:MAR01 | MMS | TRF | MV-TRF02 | MAR01_RTU | [9 empty] | &MV-TRF02 | TUN_MAR01_MMS_MV-TRF02 |  |  | YES | TUNMAR01MMSMV-TRF02 | 19
B2.1 | N |  | MAR01-EL2-CBC01 | TUN:MAR01 | MMS | ACB | EL2-CBC01 | MAR01_RTU | [9 empty] | &EL2-CBC01 | TUN_MAR01_MMS_EL2-CBC01 |  |  | YES | TUNMAR01MMSEL2-CBC01 | 20
B2.1 | N |  | MAR01-EL2-CBC02 | TUN:MAR01 | MMS | ACB | EL2-CBC02 | MAR01_RTU | [9 empty] | &EL2-CBC02 | TUN_MAR01_MMS_EL2-CBC02 |  |  | YES | TUNMAR01MMSEL2-CBC02 | 20
B2.1 | N |  | MAR01-LPS-MDB01 | TUN:MAR01 | MMS | MDB | LPS-MDB01 | MAR01_RTU | [9 empty] | &LPS-MDB01 | TUN_MAR01_MMS_LPS-MDB01 |  |  | YES | TUNMAR01MMSLPS-MDB01 | 20
B2.1 | N |  | MAR01-LPS-MDB02 | TUN:MAR01 | MMS | MDB | LPS-MDB02 | MAR01_RTU | [9 empty] | &LPS-MDB02 | TUN_MAR01_MMS_LPS-MDB02 |  |  | YES | TUNMAR01MMSLPS-MDB02 | 20
B1.6 | Y |  |  | Electrical Panel EL1 I/O 01
B2.1 | N |  | MAR01-EL1-IO01 | TUN:MAR01 | MMS | EL | EL1-IO01 | MAR01_RTU | [9 empty] | &EL1-IO01 | TUN_MAR01_MMS_EL1-IO01 |  |  | YES | TUNMAR01MMSEL1-IO01 | 19
B2.1 | N |  | MCCB MAR01-EL1-VSD01/02 | TUN:MAR01 | MMS | MCCB | EL1-VSD0102 | MAR01_RTU | [9 empty] | &EL1-VSD0102 | TUN_MAR01_MMS_EL1-VSD0102 |  |  | YES | TUNMAR01MMSEL1-VSD0102 | 22
B2.1 | N |  | LBS MAR01-EL1-VSD01/02 | TUN:MAR01 | MMS | LBS | EL1-VSD0102 | MAR01_RTU | [9 empty] | &EL1-VSD0102 | TUN_MAR01_MMS_EL1-VSD0102 |  |  | YES | TUNMAR01MMSEL1-VSD0102 | 22
B2.1 | N |  | MCB MAR01-EL1-VSD01 | TUN:MAR01 | MMS | MCB | EL1-VSD01 | MAR01_RTU | [9 empty] | &EL1-VSD01 | TUN_MAR01_MMS_EL1-VSD01 |  |  | YES | TUNMAR01MMSEL1-VSD01 | 20
B2.1 | N |  | MCB MAR01-EL1-VSD02 | TUN:MAR01 | MMS | MCB | EL1-VSD02 | MAR01_RTU | [9 empty] | &EL1-VSD02 | TUN_MAR01_MMS_EL1-VSD02 |  |  | YES | TUNMAR01MMSEL1-VSD02 | 20
B2.1 | N |  | MCB 3P MAR01-VT3-IDP01 | TUN:MAR01 | MMS | MCB | 3P-VT3-IDP01 | MAR01_RTU | [9 empty] | &3P-VT3-IDP01 | TUN_MAR01_MMS_3P-VT3-IDP01 |  |  | YES | TUNMAR01MMS3P-VT3-IDP01 | 23
B2.1 | N |  | MCB 2P MAR01-VT3-IDP01 | TUN:MAR01 | MMS | MCB | 2P-VT3-IDP01 | MAR01_RTU | [9 empty] | &2P-VT3-IDP01 | TUN_MAR01_MMS_2P-VT3-IDP01 |  |  | YES | TUNMAR01MMS2P-VT3-IDP01 | 23
B2.1 | N |  | MCB 3P MAR01-VT4-IDP01 | TUN:MAR01 | MMS | MCB | 3P-VT4-IDP01 | MAR01_RTU | [9 empty] | &3P-VT4-IDP01 | TUN_MAR01_MMS_3P-VT4-IDP01 |  |  | YES | TUNMAR01MMS3P-VT4-IDP01 | 23
B2.1 | N |  | MCB 2P MAR01-VT4-IDP01 | TUN:MAR01 | MMS | MCB | 2P-VT4-IDP01 | MAR01_RTU | [9 empty] | &2P-VT4-IDP01 | TUN_MAR01_MMS_2P-VT4-IDP01 |  |  | YES | TUNMAR01MMS2P-VT4-IDP01 | 23
B2.1 | N |  | MCB 3P MAR01-VT6-IDP01-01 | TUN:MAR01 | MMS | MCB | 3P-VT6-IDP01-01 | MAR01_RTU | [9 empty] | &3P-VT6-IDP01-01 | TUN_MAR01_MMS_3P-VT6-IDP01-01 |  |  | YES | TUNMAR01MMS3P-VT6-IDP01-01 | 26
B2.1 | N |  | MCB 2P MAR01-VT6-IDP01-01 | TUN:MAR01 | MMS | MCB | 2P-VT6-IDP01-01 | MAR01_RTU | [9 empty] | &2P-VT6-IDP01-01 | TUN_MAR01_MMS_2P-VT6-IDP01-01 |  |  | YES | TUNMAR01MMS2P-VT6-IDP01-01 | 26
B2.1 | N |  | MCB 3P MAR01-VT6-IDP01-02 | TUN:MAR01 | MMS | MCB | 3P-VT6-IDP01-02 | MAR01_RTU | [9 empty] | &3P-VT6-IDP01-02 | TUN_MAR01_MMS_3P-VT6-IDP01-02 |  |  | YES | TUNMAR01MMS3P-VT6-IDP01-02 | 26
B2.1 | N |  | MCB 2P MAR01-VT6-IDP01-02 | TUN:MAR01 | MMS | MCB | 2P-VT6-IDP01-02 | MAR01_RTU | [9 empty] | &2P-VT6-IDP01-02 | TUN_MAR01_MMS_2P-VT6-IDP01-02 |  |  | YES | TUNMAR01MMS2P-VT6-IDP01-02 | 26
B2.1 | N |  | MCB 3P MAR01-VT6-IDP01-03 | TUN:MAR01 | MMS | MCB | 3P-VT6-IDP01-03 | MAR01_RTU | [9 empty] | &3P-VT6-IDP01-03 | TUN_MAR01_MMS_3P-VT6-IDP01-03 |  |  | YES | TUNMAR01MMS3P-VT6-IDP01-03 | 26
B2.1 | N |  | MCB 2P MAR01-VT6-IDP01-03 | TUN:MAR01 | MMS | MCB | 2P-VT6-IDP01-03 | MAR01_RTU | [9 empty] | &2P-VT6-IDP01-03 | TUN_MAR01_MMS_2P-VT6-IDP01-03 |  |  | YES | TUNMAR01MMS2P-VT6-IDP01-03 | 26
B2.1 | N |  | MCB 3P MAR01-FR2-BDP01-01 | TUN:MAR01 | MMS | MCB | 3P-FR2-BDP01-01 | MAR01_RTU | [9 empty] | &3P-FR2-BDP01-01 | TUN_MAR01_MMS_3P-FR2-BDP01-01 |  |  | YES | TUNMAR01MMS3P-FR2-BDP01-01 | 26
B2.1 | N |  | MCB 2P MAR01-FR2-BDP01-01 | TUN:MAR01 | MMS | MCB | 2P-FR2-BDP01-01 | MAR01_RTU | [9 empty] | &2P-FR2-BDP01-01 | TUN_MAR01_MMS_2P-FR2-BDP01-01 |  |  | YES | TUNMAR01MMS2P-FR2-BDP01-01 | 26
B2.1 | N |  | MCB 3P MAR01-FR2-BDP01-02 | TUN:MAR01 | MMS | MCB | 3P-FR2-BDP01-02 | MAR01_RTU | [9 empty] | &3P-FR2-BDP01-02 | TUN_MAR01_MMS_3P-FR2-BDP01-02 |  |  | YES | TUNMAR01MMS3P-FR2-BDP01-02 | 26
B2.1 | N |  | MCB 2P MAR01-FR2-BDP01-02 | TUN:MAR01 | MMS | MCB | 2P-FR2-BDP01-02 | MAR01_RTU | [9 empty] | &2P-FR2-BDP01-02 | TUN_MAR01_MMS_2P-FR2-BDP01-02 |  |  | YES | TUNMAR01MMS2P-FR2-BDP01-02 | 26
B2.1 | N |  | MCB MAR01-MSFD-CON-63 | TUN:MAR01 | MMS | MCB | MSFD-CON-63 | MAR01_RTU | [9 empty] | &MSFD-CON-63 | TUN_MAR01_MMS_MSFD-CON-63 |  |  | YES | TUNMAR01MMSMSFD-CON-63 | 22
B2.1 | N |  | MCB MAR01-MSFD-CON-59 | TUN:MAR01 | MMS | MCB | MSFD-CON-59 | MAR01_RTU | [9 empty] | &MSFD-CON-59 | TUN_MAR01_MMS_MSFD-CON-59 |  |  | YES | TUNMAR01MMSMSFD-CON-59 | 22
B2.1 | N |  | MCB MAR01-MSFD-CON-67 | TUN:MAR01 | MMS | MCB | MSFD-CON-67 | MAR01_RTU | [9 empty] | &MSFD-CON-67 | TUN_MAR01_MMS_MSFD-CON-67 |  |  | YES | TUNMAR01MMSMSFD-CON-67 | 22
B1.6 | Y |  |  | Electrical Panel EL2 I/O 01
B2.1 | N |  | MAR01-EL2-IO01 | TUN:MAR01 | MMS | EL | EL2-IO01 | MAR01_RTU | [9 empty] | &EL2-IO01 | TUN_MAR01_MMS_EL2-IO01 |  |  | YES | TUNMAR01MMSEL2-IO01 | 19
B2.1 | N |  | MCB MAR01-EL2-LBS01 | TUN:MAR01 | MMS | MCB | EL2-LBS01 | MAR01_RTU | [9 empty] | &EL2-LBS01 | TUN_MAR01_MMS_EL2-LBS01 |  |  | YES | TUNMAR01MMSEL2-LBS01 | 20
B2.1 | N |  | MCB MAR01-EL2-LBS02 | TUN:MAR01 | MMS | MCB | EL2-LBS02 | MAR01_RTU | [9 empty] | &EL2-LBS02 | TUN_MAR01_MMS_EL2-LBS02 |  |  | YES | TUNMAR01MMSEL2-LBS02 | 20
B2.1 | N |  | MCB MAR01-EL2-CBC01 | TUN:MAR01 | MMS | MCB | EL2-CBC01 | MAR01_RTU | [9 empty] | &EL2-CBC01 | TUN_MAR01_MMS_EL2-CBC01 |  |  | YES | TUNMAR01MMSEL2-CBC01 | 20
B2.1 | N |  | MCB MAR01-EL2-CBC02 | TUN:MAR01 | MMS | MCB | EL2-CBC02 | MAR01_RTU | [9 empty] | &EL2-CBC02 | TUN_MAR01_MMS_EL2-CBC02 |  |  | YES | TUNMAR01MMSEL2-CBC02 | 20
B2.1 | N |  | MCCB 2P MAR01-EL2 | TUN:MAR01 | MMS | MCCB | EL2-2P | MAR01_RTU | [9 empty] | &EL2-2P | TUN_MAR01_MMS_EL2-2P |  |  | YES | TUNMAR01MMSEL2-2P | 17
B2.1 | N |  | LBS 2P MAR01-EL2 | TUN:MAR01 | MMS | LBS | EL2-2P | MAR01_RTU | [9 empty] | &EL2-2P | TUN_MAR01_MMS_EL2-2P |  |  | YES | TUNMAR01MMSEL2-2P | 17
B2.1 | N |  | MCB MAR01-EL2-CBC01 | TUN:MAR01 | MMS | MCB | EL2-CBC01 | MAR01_RTU | [9 empty] | &EL2-CBC01 | TUN_MAR01_MMS_EL2-CBC01 |  |  | YES | TUNMAR01MMSEL2-CBC01 | 20
B2.1 | N |  | MCB MAR01-EL2-CBC02 | TUN:MAR01 | MMS | MCB | EL2-CBC02 | MAR01_RTU | [9 empty] | &EL2-CBC02 | TUN_MAR01_MMS_EL2-CBC02 |  |  | YES | TUNMAR01MMSEL2-CBC02 | 20
B2.1 | N |  | MCB MAR01-EL2-VSD01 | TUN:MAR01 | MMS | MCB | EL2-VSD01 | MAR01_RTU | [9 empty] | &EL2-VSD01 | TUN_MAR01_MMS_EL2-VSD01 |  |  | YES | TUNMAR01MMSEL2-VSD01 | 20
B2.1 | N |  | MCB MAR01-EL2-VSD02 | TUN:MAR01 | MMS | MCB | EL2-VSD02 | MAR01_RTU | [9 empty] | &EL2-VSD02 | TUN_MAR01_MMS_EL2-VSD02 |  |  | YES | TUNMAR01MMSEL2-VSD02 | 20
B2.1 | N |  | MCB MAR01-EL2-LBS01 | TUN:MAR01 | MMS | MCB | EL2-LBS01 | MAR01_RTU | [9 empty] | &EL2-LBS01 | TUN_MAR01_MMS_EL2-LBS01 |  |  | YES | TUNMAR01MMSEL2-LBS01 | 20
B2.1 | N |  | MCB MAR01-EL2-LBS02 | TUN:MAR01 | MMS | MCB | EL2-LBS02 | MAR01_RTU | [9 empty] | &EL2-LBS02 | TUN_MAR01_MMS_EL2-LBS02 |  |  | YES | TUNMAR01MMSEL2-LBS02 | 20
B2.1 | N |  | MCB 3P MAR01-VT1-IDP01 | TUN:MAR01 | MMS | MCB | 3P-VT1-IDP01 | MAR01_RTU | [9 empty] | &3P-VT1-IDP01 | TUN_MAR01_MMS_3P-VT1-IDP01 |  |  | YES | TUNMAR01MMS3P-VT1-IDP01 | 23
B2.1 | N |  | MCB 2P MAR01-VT1-IDP01 | TUN:MAR01 | MMS | MCB | 2P-VT1-IDP01 | MAR01_RTU | [9 empty] | &2P-VT1-IDP01 | TUN_MAR01_MMS_2P-VT1-IDP01 |  |  | YES | TUNMAR01MMS2P-VT1-IDP01 | 23
B2.1 | N |  | MCB 3P MAR01-VT2-IDP01 | TUN:MAR01 | MMS | MCB | 3P-VT2-IDP01 | MAR01_RTU | [9 empty] | &3P-VT2-IDP01 | TUN_MAR01_MMS_3P-VT2-IDP01 |  |  | YES | TUNMAR01MMS3P-VT2-IDP01 | 23
B2.1 | N |  | MCB 2P MAR01-VT2-IDP01 | TUN:MAR01 | MMS | MCB | 2P-VT2-IDP01 | MAR01_RTU | [9 empty] | &2P-VT2-IDP01 | TUN_MAR01_MMS_2P-VT2-IDP01 |  |  | YES | TUNMAR01MMS2P-VT2-IDP01 | 23
B2.1 | N |  | MCB 3P MAR01-VT5-IDP01-01 | TUN:MAR01 | MMS | MCB | 3P-VT5-IDP01-01 | MAR01_RTU | [9 empty] | &3P-VT5-IDP01-01 | TUN_MAR01_MMS_3P-VT5-IDP01-01 |  |  | YES | TUNMAR01MMS3P-VT5-IDP01-01 | 26
B2.1 | N |  | MCB 2P MAR01-VT5-IDP01-01 | TUN:MAR01 | MMS | MCB | 2P-VT5-IDP01-01 | MAR01_RTU | [9 empty] | &2P-VT5-IDP01-01 | TUN_MAR01_MMS_2P-VT5-IDP01-01 |  |  | YES | TUNMAR01MMS2P-VT5-IDP01-01 | 26
B2.1 | N |  | MCB 3P MAR01-VT5-IDP01-02 | TUN:MAR01 | MMS | MCB | 3P-VT5-IDP01-02 | MAR01_RTU | [9 empty] | &3P-VT5-IDP01-02 | TUN_MAR01_MMS_3P-VT5-IDP01-02 |  |  | YES | TUNMAR01MMS3P-VT5-IDP01-02 | 26
B2.1 | N |  | MCB 2P MAR01-VT5-IDP01-02 | TUN:MAR01 | MMS | MCB | 2P-VT5-IDP01-02 | MAR01_RTU | [9 empty] | &2P-VT5-IDP01-02 | TUN_MAR01_MMS_2P-VT5-IDP01-02 |  |  | YES | TUNMAR01MMS2P-VT5-IDP01-02 | 26
B2.1 | N |  | MCB 3P MAR01-VT5-IDP01-03 | TUN:MAR01 | MMS | MCB | 3P-VT5-IDP01-03 | MAR01_RTU | [9 empty] | &3P-VT5-IDP01-03 | TUN_MAR01_MMS_3P-VT5-IDP01-03 |  |  | YES | TUNMAR01MMS3P-VT5-IDP01-03 | 26
B2.1 | N |  | MCB 2P MAR01-VT5-IDP01-03 | TUN:MAR01 | MMS | MCB | 2P-VT5-IDP01-03 | MAR01_RTU | [9 empty] | &2P-VT5-IDP01-03 | TUN_MAR01_MMS_2P-VT5-IDP01-03 |  |  | YES | TUNMAR01MMS2P-VT5-IDP01-03 | 26
B2.1 | N |  | MCB 3P MAR01-FR1-BDP01-01 | TUN:MAR01 | MMS | MCB | 3P-FR1-BDP01-01 | MAR01_RTU | [9 empty] | &3P-FR1-BDP01-01 | TUN_MAR01_MMS_3P-FR1-BDP01-01 |  |  | YES | TUNMAR01MMS3P-FR1-BDP01-01 | 26
B2.1 | N |  | MCB 2P MAR01-FR1-BDP01-01 | TUN:MAR01 | MMS | MCB | 2P-FR1-BDP01-01 | MAR01_RTU | [9 empty] | &2P-FR1-BDP01-01 | TUN_MAR01_MMS_2P-FR1-BDP01-01 |  |  | YES | TUNMAR01MMS2P-FR1-BDP01-01 | 26
B2.1 | N |  | MCB 3P MAR01-FR1-BDP01-02 | TUN:MAR01 | MMS | MCB | 3P-FR1-BDP01-02 | MAR01_RTU | [9 empty] | &3P-FR1-BDP01-02 | TUN_MAR01_MMS_3P-FR1-BDP01-02 |  |  | YES | TUNMAR01MMS3P-FR1-BDP01-02 | 26
B2.1 | N |  | MCB 2P MAR01-FR1-BDP01-02 | TUN:MAR01 | MMS | MCB | 2P-FR1-BDP01-02 | MAR01_RTU | [9 empty] | &2P-FR1-BDP01-02 | TUN_MAR01_MMS_2P-FR1-BDP01-02 |  |  | YES | TUNMAR01MMS2P-FR1-BDP01-02 | 26
B2.1 | N |  | MCB MAR01-MSFD-CON-54 | TUN:MAR01 | MMS | MCB | MSFD-CON-54 | MAR01_RTU | [9 empty] | &MSFD-CON-54 | TUN_MAR01_MMS_MSFD-CON-54 |  |  | YES | TUNMAR01MMSMSFD-CON-54 | 22
B2.1 | N |  | MCB MAR01-MSFD-CON-52 | TUN:MAR01 | MMS | MCB | MSFD-CON-52 | MAR01_RTU | [9 empty] | &MSFD-CON-52 | TUN_MAR01_MMS_MSFD-CON-52 |  |  | YES | TUNMAR01MMSMSFD-CON-52 | 22
B2.1 | N |  | MCB MAR01-MSFD-CON-58 | TUN:MAR01 | MMS | MCB | MSFD-CON-58 | MAR01_RTU | [9 empty] | &MSFD-CON-58 | TUN_MAR01_MMS_MSFD-CON-58 |  |  | YES | TUNMAR01MMSMSFD-CON-58 | 22
B1.5 | Y |  |  | MAR-0A SHAFT
B1.5 | Y |  |  | LOCAL CONTROL PANEL (LCP) [STATION HMI]
B2.1 | N |  | Local control panel | TUN:MAR0A | SCR | LCP | LCP01 | MAR0A_RTU | [9 empty] | &LCP01 | TUN_MAR0A_SCR_LCP01 |  |  | YES | TUNMAR0ASCRLCP01 | 16
B1.5 | Y |  |  | FIRE MANUAL OVERRIDE PANEL (FMOP)
B2.1 | N |  | Fire control panel | TUN:MAR0A | SCR | FMOP | FMOP01 | MAR0A_RTU | [9 empty] | &FMOP01 | TUN_MAR0A_SCR_FMOP01 |  |  | YES | TUNMAR0ASCRFMOP01 | 17
B1.5 | Y |  |  | Station PLC (SPLC)
B2.1 | N |  | Station PLC | TUN:MAR0A | TEL | SPLC | PLC01 | MAR0A_RTU | [9 empty] | &PLC01 | TUN_MAR0A_TEL_PLC01 |  |  | YES | TUNMAR0ATELPLC01 | 16
B1.5 | Y |  |  | Switch (SWI)
B2.1 | N |  | Switch | TUN:MAR0A | TEL | SWI | SWI01 | MAR0A_RTU | [9 empty] | &SWI01 | TUN_MAR0A_TEL_SWI01 |  |  | YES | TUNMAR0ATELSWI01 | 16
B1.5 | Y |  |  | Outdoor temperature sensor (OTS)
B2.1 | N |  | Outdoor temperature sensor 1 | TUN:MAR0A | OTS | OTS | OTS001 | MAR0A_RTU | [9 empty] | &OTS001 | TUN_MAR0A_OTS_OTS001 |  |  | YES | TUNMAR0AOTSOTS001 | 17
B1.5 | Y |  |  | Tunnel temperature & humidity sensor (TTS)
B2.1 | N |  | Tunnel temperature sensor 1 | TUN:MAR0A | SENSOR | TTS | TS099152 | MAR0A_RTU | [9 empty] | &TS099152 | TUN_MAR0A_SENSOR_TS099152 |  |  | YES | TUNMAR0ASENSORTS099152 | 23
B2.1 | N |  | Tunnel temperature sensor 2 | TUN:MAR0A | SENSOR | TTS | TS099343 | MAR0A_RTU | [9 empty] | &TS099343 | TUN_MAR0A_SENSOR_TS099343 |  |  | YES | TUNMAR0ASENSORTS099343 | 22
B2.1 | N |  | Tunnel temperature sensor 3 | TUN:MAR0A | SENSOR | TTS | TS099620 | MAR0A_RTU | [9 empty] | &TS099620 | TUN_MAR0A_SENSOR_TS099620 |  |  | YES | TUNMAR0ASENSORTS099620 | 22
B2.1 | N |  | Tunnel temperature sensor 4 | TUN:MAR0A | SENSOR | TTS | TS099718 | MAR0A_RTU | [9 empty] | &TS099718 | TUN_MAR0A_SENSOR_TS099718 |  |  | YES | TUNMAR0ASENSORTS099718 | 22
B1.5 | Y |  |  | Air velocity sensor (VS)
B2.1 | N |  | Air velocity sensor 1 -099216 | TUN:MAR0A | SENSOR | VS | VS099216 | MAR0A_RTU | [9 empty] | &VS099216 | TUN_MAR0A_SENSOR_VS099216 |  |  | YES | TUNMAR0ASENSORVS099216 | 22
B2.1 | N |  | Air velocity sensor 2 -099685 | TUN:MAR0A | SENSOR | VS | VS099685 | MAR0A_RTU | [9 empty] | &VS099685 | TUN_MAR0A_SENSOR_VS099685 |  |  | YES | TUNMAR0ASENSORVS099685 | 22
B1.5 | Y |  |  | Tunnel ventilation fan (TVF)
B2.1 | N |  | Shaft Tunnel ventilation fan 1 | TUN:MAR0A | TVF | TVF | VT1-TVF01 | MAR0A_RTU | [9 empty] | &VT1-TVF01 | TUN_MAR0A_TVF_VT1-TVF01 |  |  | YES | TUNMAR0ATVFVT1-TVF01 | 20
B2.1 | N |  | Shaft Tunnel ventilation fan 2 | TUN:MAR0A | TVF | TVF | VT2-TVF01 | MAR0A_RTU | [9 empty] | &VT2-TVF01 | TUN_MAR0A_TVF_VT2-TVF01 |  |  | YES | TUNMAR0ATVFVT2-TVF01 | 20
B1.5 | Y |  |  | TVS Damper : Isolation damper (IDP)
B2.1 | N |  | Isolation damper 1 | TUN:MAR0A | DAMPER | IDP | VT1-IDP01 | MAR0A_RTU | [9 empty] | &VT1-IDP01 | TUN_MAR0A_DAMPER_VT1-IDP01 |  |  | YES | TUNMAR0ADAMPERVT1-IDP01 | 23
B2.1 | N |  | Isolation damper 2 | TUN:MAR0A | DAMPER | IDP | VT2-IDP01 | MAR0A_RTU | [9 empty] | &VT2-IDP01 | TUN_MAR0A_DAMPER_VT2-IDP01 |  |  | YES | TUNMAR0ADAMPERVT2-IDP01 | 23
B1.5 | Y |  |  | PRESSURIZATION FAN (PFA)
B2.1 | N |  | Pressurization fan Lobby | TUN:MAR0A | PFA | PFA | GRD-01 | MAR0A_RTU | [9 empty] | &GRD-01 | TUN_MAR0A_PFA_GRD-01 |  |  | YES | TUNMAR0APFAGRD-01 | 17
B2.1 | N |  | Pressurization fan Staircase | TUN:MAR0A | PFA | PFA | GRD-02 | MAR0A_RTU | [9 empty] | &GRD-02 | TUN_MAR0A_PFA_GRD-02 |  |  | YES | TUNMAR0APFAGRD-02 | 17
B1.6 | Y |  |  | MMS Equipment
B2.1 | N |  | Station PLC (MMS) | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | MAR0A_RTU | [9 empty] | &SPLC01 | TUN_MAR0A_MMS_SPLC01 |  |  | YES | TUNMAR0AMMSSPLC01 | 17
B1.6 | Y |  |  | Electrical Equipment
B2.1 | N |  | MAR0A-EL3-LBW01 | TUN:MAR0A | MMS | ADS | EL3-LBW01 | MAR0A_RTU | [9 empty] | &EL3-LBW01 | TUN_MAR0A_MMS_EL3-LBW01 |  |  | YES | TUNMAR0AMMSEL3-LBW01 | 20
B2.1 | N |  | MAR0A-EL3-LBW02 | TUN:MAR0A | MMS | ADS | EL3-LBW02 | MAR0A_RTU | [9 empty] | &EL3-LBW02 | TUN_MAR0A_MMS_EL3-LBW02 |  |  | YES | TUNMAR0AMMSEL3-LBW02 | 20
B2.1 | N |  | MAR0A-EL3-TRF01 | TUN:MAR0A | MMS | TRF | EL3-TRF01 | MAR0A_RTU | [9 empty] | &EL3-TRF01 | TUN_MAR0A_MMS_EL3-TRF01 |  |  | YES | TUNMAR0AMMSEL3-TRF01 | 20
B2.1 | N |  | MAR0A-EL3-TRF02 | TUN:MAR0A | MMS | TRF | EL3-TRF02 | MAR0A_RTU | [9 empty] | &EL3-TRF02 | TUN_MAR0A_MMS_EL3-TRF02 |  |  | YES | TUNMAR0AMMSEL3-TRF02 | 20
B2.1 | N |  | MAR0A-EL3-MDB01 | TUN:MAR0A | MMS | MDB | EL3-MDB01 | MAR0A_RTU | [9 empty] | &EL3-MDB01 | TUN_MAR0A_MMS_EL3-MDB01 |  |  | YES | TUNMAR0AMMSEL3-MDB01 | 20
B1.6 | Y |  |  | Electrical Panel EL3 PLC 01
B2.1 | N |  | MAR0A-EL3-PLC01 | TUN:MAR0A | MMS | EL | EL3-PLC01 | MAR0A_RTU | [9 empty] | &EL3-PLC01 | TUN_MAR0A_MMS_EL3-PLC01 |  |  | YES | TUNMAR0AMMSEL3-PLC01 | 20
B2.1 | N |  | LBS 4P MAR0A-EL3 | TUN:MAR0A | MMS | LBS | EL3-4P | MAR0A_RTU | [9 empty] | &EL3-4P | TUN_MAR0A_MMS_EL3-4P |  |  | YES | TUNMAR0AMMSEL3-4P | 17
B2.1 | N |  | MCB MAR0A-EL3-LBW01 | TUN:MAR0A | MMS | MCB | EL3-LBW01 | MAR0A_RTU | [9 empty] | &EL3-LBW01 | TUN_MAR0A_MMS_EL3-LBW01 |  |  | YES | TUNMAR0AMMSEL3-LBW01 | 20
B2.1 | N |  | MCB MAR0A-EL3-LBW02 | TUN:MAR0A | MMS | MCB | EL3-LBW02 | MAR0A_RTU | [9 empty] | &EL3-LBW02 | TUN_MAR0A_MMS_EL3-LBW02 |  |  | YES | TUNMAR0AMMSEL3-LBW02 | 20
B2.1 | N |  | MCCB 2P MAR0A-EL3 | TUN:MAR0A | MMS | MCCB | EL3-2P | MAR0A_RTU | [9 empty] | &EL3-2P | TUN_MAR0A_MMS_EL3-2P |  |  | YES | TUNMAR0AMMSEL3-2P | 17
B2.1 | N |  | LBS 2P MAR0A-EL3 | TUN:MAR0A | MMS | LBS | EL3-2P | MAR0A_RTU | [9 empty] | &EL3-2P | TUN_MAR0A_MMS_EL3-2P |  |  | YES | TUNMAR0AMMSEL3-2P | 17
B2.1 | N |  | MCB MAR0A-EL3-VSD01 | TUN:MAR0A | MMS | MCB | EL3-VSD01 | MAR0A_RTU | [9 empty] | &EL3-VSD01 | TUN_MAR0A_MMS_EL3-VSD01 |  |  | YES | TUNMAR0AMMSEL3-VSD01 | 20
B2.1 | N |  | MCB MAR0A-EL3-VSD02 | TUN:MAR0A | MMS | MCB | EL3-VSD02 | MAR0A_RTU | [9 empty] | &EL3-VSD02 | TUN_MAR0A_MMS_EL3-VSD02 |  |  | YES | TUNMAR0AMMSEL3-VSD02 | 20
B2.1 | N |  | MCB MAR0A-EL3-LBW01 | TUN:MAR0A | MMS | MCB | EL3-LBW01 | MAR0A_RTU | [9 empty] | &EL3-LBW01 | TUN_MAR0A_MMS_EL3-LBW01 |  |  | YES | TUNMAR0AMMSEL3-LBW01 | 20
B2.1 | N |  | MCB MAR0A-EL3-LBW02 | TUN:MAR0A | MMS | MCB | EL3-LBW02 | MAR0A_RTU | [9 empty] | &EL3-LBW02 | TUN_MAR0A_MMS_EL3-LBW02 |  |  | YES | TUNMAR0AMMSEL3-LBW02 | 20
B2.1 | N |  | MCB MAR0A-EL3-MDB01 | TUN:MAR0A | MMS | MCB | EL3-MDB01 | MAR0A_RTU | [9 empty] | &EL3-MDB01 | TUN_MAR0A_MMS_EL3-MDB01 |  |  | YES | TUNMAR0AMMSEL3-MDB01 | 20
B2.1 | N |  | MCB 3P MAR0A-VT1-IDP01 | TUN:MAR0A | MMS | MCB | 3P-VT1-IDP01 | MAR0A_RTU | [9 empty] | &3P-VT1-IDP01 | TUN_MAR0A_MMS_3P-VT1-IDP01 |  |  | YES | TUNMAR0AMMS3P-VT1-IDP01 | 23
B2.1 | N |  | MCB 2P MAR0A-VT1-IDP01 | TUN:MAR0A | MMS | MCB | 2P-VT1-IDP01 | MAR0A_RTU | [9 empty] | &2P-VT1-IDP01 | TUN_MAR0A_MMS_2P-VT1-IDP01 |  |  | YES | TUNMAR0AMMS2P-VT1-IDP01 | 23
B2.1 | N |  | MCB 3P MAR0A-VT2-IDP01 | TUN:MAR0A | MMS | MCB | 3P-VT2-IDP01 | MAR0A_RTU | [9 empty] | &3P-VT2-IDP01 | TUN_MAR0A_MMS_3P-VT2-IDP01 |  |  | YES | TUNMAR0AMMS3P-VT2-IDP01 | 23
B2.1 | N |  | MCB 2P MAR0A-VT2-IDP01 | TUN:MAR0A | MMS | MCB | 2P-VT2-IDP01 | MAR0A_RTU | [9 empty] | &2P-VT2-IDP01 | TUN_MAR0A_MMS_2P-VT2-IDP01 |  |  | YES | TUNMAR0AMMS2P-VT2-IDP01 | 23
B1.8 | Y |  |  | EC1-01
B1.8 | Y |  |  | LOCAL CONTROL PANEL (LCP) [STATION HMI]
B2.1 | N |  | Local control panel | TUN:EC101 | SCR | LCP | LCP01 | EC101_RTU | [9 empty] | &LCP01 | TUN_EC101_SCR_LCP01 |  |  | YES | TUNEC101SCRLCP01 | 16
B1.8 | Y |  |  | FIRE MANUAL OVERRIDE PANEL (FMOP)
B2.1 | N |  | Fire control panel | TUN:EC101 | SCR | FMOP | FMOP01 | EC101_RTU | [9 empty] | &FMOP01 | TUN_EC101_SCR_FMOP01 |  |  | YES | TUNEC101SCRFMOP01 | 17
B1.8 | Y |  |  | Station PLC (SPLC)
B2.1 | N |  | Station PLC | TUN:EC101 | TEL | SPLC | PLC01 | EC101_RTU | [9 empty] | &PLC01 | TUN_EC101_TEL_PLC01 |  |  | YES | TUNEC101TELPLC01 | 16
B1.8 | Y |  |  | Switch (SWI)
B2.1 | N |  | Switch | TUN:EC101 | TEL | SWI | SWI01 | EC101_RTU | [9 empty] | &SWI01 | TUN_EC101_TEL_SWI01 |  |  | YES | TUNEC101TELSWI01 | 16
B1.8 | Y |  |  | PRESSURIZATION FAN (PFA)
B2.1 | N |  | Pressurization fan Lobby 1 | TUN:EC101 | WS01:PFA | PFA | CON-06 | EC101_RTU | [9 empty] | &CON-06 | TUN_EC101_WS01_PFA_CON-06 |  |  | YES | TUNEC101WS01PFACON-06 | 21
B2.1 | N |  | Pressurization fan Escape Staircase 1 | TUN:EC101 | WS01:PFA | PFA | GRD-01 | EC101_RTU | [9 empty] | &GRD-01 | TUN_EC101_WS01_PFA_GRD-01 |  |  | YES | TUNEC101WS01PFAGRD-01 | 21
B2.1 | N |  | Pressurization fan Lobby 2 | TUN:EC101 | ES01:PFA | PFA | CON-03 | EC101_RTU | [9 empty] | &CON-03 | TUN_EC101_ES01_PFA_CON-03 |  |  | YES | TUNEC101ES01PFACON-03 | 21
B2.1 | N |  | Pressurization fan Escape Staircase 2 | TUN:EC101 | ES01:PFA | PFA | CON-04 | EC101_RTU | [9 empty] | &CON-04 | TUN_EC101_ES01_PFA_CON-04 |  |  | YES | TUNEC101ES01PFACON-04 | 21
B2.1 | N |  | Pressurization fan Lobby 3 & Corridor 2 | TUN:EC101 | WS01:PFA | PFA | CON-07 | EC101_RTU | [9 empty] | &CON-07 | TUN_EC101_WS01_PFA_CON-07 |  |  | YES | TUNEC101WS01PFACON-07 | 21
B2.1 | N |  | Pressurization fan Staircase 4 | TUN:EC101 | WS01:PFA | PFA | PLA-01 | EC101_RTU | [9 empty] | &PLA-01 | TUN_EC101_WS01_PFA_PLA-01 |  |  | YES | TUNEC101WS01PFAPLA-01 | 21
B1.8 | Y |  |  | SMOKE CURTAINS (SMC)
B2.1 | N |  | Smoke Curtains 1 | TUN:EC101 | SMC | SMC | SMC01 | EC101_RTU | [9 empty] | &SMC01 | TUN_EC101_SMC_SMC01 |  |  | YES | TUNEC101SMCSMC01 | 16
B2.1 | N |  | Smoke Curtains 2 | TUN:EC101 | SMC | SMC | SMC02 | EC101_RTU | [9 empty] | &SMC02 | TUN_EC101_SMC_SMC02 |  |  | YES | TUNEC101SMCSMC02 | 16
B2.1 | N |  | Smoke Curtains 3 | TUN:EC101 | SMC | SMC | SMC03 | EC101_RTU | [9 empty] | &SMC03 | TUN_EC101_SMC_SMC03 |  |  | YES | TUNEC101SMCSMC03 | 16
B2.1 | N |  | Smoke Curtains 4 | TUN:EC101 | SMC | SMC | SMC04 | EC101_RTU | [9 empty] | &SMC04 | TUN_EC101_SMC_SMC04 |  |  | YES | TUNEC101SMCSMC04 | 16
B2.1 | N |  | Smoke Curtains 5 | TUN:EC101 | SMC | SMC | SMC05 | EC101_RTU | [9 empty] | &SMC05 | TUN_EC101_SMC_SMC05 |  |  | YES | TUNEC101SMCSMC05 | 16
B2.1 | N |  | Smoke Curtains 6 | TUN:EC101 | SMC | SMC | SMC06 | EC101_RTU | [9 empty] | &SMC06 | TUN_EC101_SMC_SMC06 |  |  | YES | TUNEC101SMCSMC06 | 16
B2.1 | N |  | Smoke Curtains 7 | TUN:EC101 | SMC | SMC | SMC07 | EC101_RTU | [9 empty] | &SMC07 | TUN_EC101_SMC_SMC07 |  |  | YES | TUNEC101SMCSMC07 | 16
B2.1 | N |  | Smoke Curtains 8 | TUN:EC101 | SMC | SMC | SMC08 | EC101_RTU | [9 empty] | &SMC08 | TUN_EC101_SMC_SMC08 |  |  | YES | TUNEC101SMCSMC08 | 16
B2.1 | N |  | Smoke Curtains 9 | TUN:EC101 | SMC | SMC | SMC09 | EC101_RTU | [9 empty] | &SMC09 | TUN_EC101_SMC_SMC09 |  |  | YES | TUNEC101SMCSMC09 | 16
B2.1 | N |  | Smoke Curtains 10 | TUN:EC101 | SMC | SMC | SMC10 | EC101_RTU | [9 empty] | &SMC10 | TUN_EC101_SMC_SMC10 |  |  | YES | TUNEC101SMCSMC10 | 16
B1.8 | Y |  |  | STATION ENTRANCE DOOR (SED)
B2.1 | N |  | Station entrance door 1 | TUN:EC101 | SED | SED | SED01 | EC101_RTU | [9 empty] | &SED01 | TUN_EC101_SED_SED01 |  |  | YES | TUNEC101SEDSED01 | 16
B2.1 | N |  | Station entrance door 2 | TUN:EC101 | SED | SED | SED02 | EC101_RTU | [9 empty] | &SED02 | TUN_EC101_SED_SED02 |  |  | YES | TUNEC101SEDSED02 | 16
B2.1 | N |  | Station entrance door 3 | TUN:EC101 | SED | SED | SED03 | EC101_RTU | [9 empty] | &SED03 | TUN_EC101_SED_SED03 |  |  | YES | TUNEC101SEDSED03 | 16
B2.1 | N |  | Station entrance door 4 | TUN:EC101 | SED | SED | SED04 | EC101_RTU | [9 empty] | &SED04 | TUN_EC101_SED_SED04 |  |  | YES | TUNEC101SEDSED04 | 16
B1.8 | Y |  |  | Outdoor temperature sensor (OTS)
B2.1 | N |  | Outdoor temperature sensor 1 | TUN:EC101 | OTS | OTS | OTS001 | EC101_RTU | [9 empty] | &OTS001 | TUN_EC101_OTS_OTS001 |  |  | YES | TUNEC101OTSOTS001 | 17
B2.1 | N |  | Outdoor temperature sensor 2 | TUN:EC101 | OTS | OTS | OTS002 | EC101_RTU | [9 empty] | &OTS002 | TUN_EC101_OTS_OTS002 |  |  | YES | TUNEC101OTSOTS002 | 17
B1.8 | Y |  |  | Tunnel ventilation fan (TVF)
B2.1 | N |  | West ShaftTunnel ventilation fan 1 | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | EC101_RTU | [9 empty] | &VT1-TVF01 | TUN_EC101_WS01_TVF_VT1-TVF01 |  |  | YES | TUNEC101WS01TVFVT1-TVF01 | 24
B2.1 | N |  | West ShaftTunnel ventilation fan 2 | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | EC101_RTU | [9 empty] | &VT2-TVF01 | TUN_EC101_WS01_TVF_VT2-TVF01 |  |  | YES | TUNEC101WS01TVFVT2-TVF01 | 24
B2.1 | N |  | East ShaftTunnel ventilation fan 3 | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | EC101_RTU | [9 empty] | &VT3-TVF01 | TUN_EC101_ES01_TVF_VT3-TVF01 |  |  | YES | TUNEC101ES01TVFVT3-TVF01 | 24
B2.1 | N |  | EastShaftTunnel ventilation fan 4 | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | EC101_RTU | [9 empty] | &VT4-TVF01 | TUN_EC101_ES01_TVF_VT4-TVF01 |  |  | YES | TUNEC101ES01TVFVT4-TVF01 | 24
B1.8 | Y |  |  | Tunnel temperature & humidity sensor (TTS)
B2.1 | N |  | West Tunnel temperature sensor 1 | TUN:EC101 | WS01:SENSOR | TTS | TS101561 | EC101_RTU | [9 empty] | &TS101561 | TUN_EC101_WS01_SENSOR_TS101561 |  |  | YES | TUNEC101WS01SENSORTS101561 | 26
B2.1 | N |  | West Tunnel temperature sensor 2 | TUN:EC101 | WS01:SENSOR | TTS | TS101647 | EC101_RTU | [9 empty] | &TS101647 | TUN_EC101_WS01_SENSOR_TS101647 |  |  | YES | TUNEC101WS01SENSORTS101647 | 26
B2.1 | N |  | East Tunnel temperature sensor 1 | TUN:EC101 | ES01:SENSOR | TTS | TS101045 | EC101_RTU | [9 empty] | &TS101045 | TUN_EC101_ES01_SENSOR_TS101045 |  |  | YES | TUNEC101ES01SENSORTS101045 | 26
B2.1 | N |  | East Tunnel temperature sensor 2 | TUN:EC101 | ES01:SENSOR | TTS | TS101184 | EC101_RTU | [9 empty] | &TS101184 | TUN_EC101_ES01_SENSOR_TS101184 |  |  | YES | TUNEC101ES01SENSORTS101184 | 26
B1.8 | Y |  |  | Air velocity sensor (VS)
B2.1 | N |  | West Air velocity sensor 1 | TUN:EC101 | WS01:SENSOR | VS | VS101618 | EC101_RTU | [9 empty] | &VS101618 | TUN_EC101_WS01_SENSOR_VS101618 |  |  | YES | TUNEC101WS01SENSORVS101618 | 26
B2.1 | N |  | East Air velocity sensor 1 | TUN:EC101 | ES01:SENSOR | VS | VS101094 | EC101_RTU | [9 empty] | &VS101094 | TUN_EC101_ES01_SENSOR_VS101094 |  |  | YES | TUNEC101ES01SENSORVS101094 | 26
B1.8 | Y |  |  | TVS Damper : Tunnel damper (TDP)
B2.1 | N |  | West Shaft Tunnel damper 1 | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | EC101_RTU | [9 empty] | &VT5-TDP01 | TUN_EC101_WS01_DAMPER_VT5-TDP01 |  |  | YES | TUNEC101WS01DAMPERVT5-TDP01 | 27
B2.1 | N |  | East Shaft Tunnel damper 2 | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | EC101_RTU | [9 empty] | &VT6-TDP01 | TUN_EC101_ES01_DAMPER_VT6-TDP01 |  |  | YES | TUNEC101ES01DAMPERVT6-TDP01 | 27
B1.8 | Y |  |  | TVS Damper : Isolation damper (IDP)
B2.1 | N |  | Isolation damper 1 | TUN:EC101 | WS01:DAMPER | IDP | VT1-IDP01 | EC101_RTU | [9 empty] | &VT1-IDP01 | TUN_EC101_WS01_DAMPER_VT1-IDP01 |  |  | YES | TUNEC101WS01DAMPERVT1-IDP01 | 27
B2.1 | N |  | Isolation damper 2 | TUN:EC101 | WS01:DAMPER | IDP | VT2-IDP01 | EC101_RTU | [9 empty] | &VT2-IDP01 | TUN_EC101_WS01_DAMPER_VT2-IDP01 |  |  | YES | TUNEC101WS01DAMPERVT2-IDP01 | 27
B2.1 | N |  | Isolation damper 3 | TUN:EC101 | ES01:DAMPER | IDP | VT3-IDP01 | EC101_RTU | [9 empty] | &VT3-IDP01 | TUN_EC101_ES01_DAMPER_VT3-IDP01 |  |  | YES | TUNEC101ES01DAMPERVT3-IDP01 | 27
B2.1 | N |  | Isolation damper 4 | TUN:EC101 | ES01:DAMPER | IDP | VT4-IDP01 | EC101_RTU | [9 empty] | &VT4-IDP01 | TUN_EC101_ES01_DAMPER_VT4-IDP01 |  |  | YES | TUNEC101ES01DAMPERVT4-IDP01 | 27
B1.8 | Y |  |  | TVS Damper : Bypass damper (BDP)
B2.1 | N |  | West Shaft Bypass damper 1 | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | EC101_RTU | [9 empty] | &FR1-BDP01 | TUN_EC101_WS01_DAMPER_FR1-BDP01 |  |  | YES | TUNEC101WS01DAMPERFR1-BDP01 | 27
B2.1 | N |  | East Shaft Bypass damper 2 | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | EC101_RTU | [9 empty] | &FR2-BDP01 | TUN_EC101_ES01_DAMPER_FR2-BDP01 |  |  | YES | TUNEC101ES01DAMPERFR2-BDP01 | 27
B1.8 | Y |  |  | MEP Damper : Tunnel Cooling damper (TCDP)
B2.1 | N |  | West Shaft Tunnel Cooling damper 1 | TUN:EC101 | WS01:DAMPER | MSFD | PLA-68 | EC101_RTU | [9 empty] | &PLA-68 | TUN_EC101_WS01_DAMPER_PLA-68 |  |  | YES | TUNEC101WS01DAMPERPLA-68 | 24
B2.1 | N |  | East Shaft Tunnel Cooling damper 2 | TUN:EC101 | ES01:DAMPER | MSFD | PLA-33 | EC101_RTU | [9 empty] | &PLA-33 | TUN_EC101_ES01_DAMPER_PLA-33 |  |  | YES | TUNEC101ES01DAMPERPLA-33 | 24
B1.8 | Y |  |  | MEP damper : Station to exhaust duct Damper (SEDD)
B2.1 | N |  | West Shaft Station to exhaust duct damper 1 | TUN:EC101 | WS01:DAMPER | MSFD | CON-80 | EC101_RTU | [9 empty] | &CON-80 | TUN_EC101_WS01_DAMPER_CON-80 |  |  | YES | TUNEC101WS01DAMPERCON-80 | 24
B2.1 | N |  | West Shaft Station to exhaust duct damper 2 | TUN:EC101 | WS01:DAMPER | MSFD | CON-72 | EC101_RTU | [9 empty] | &CON-72 | TUN_EC101_WS01_DAMPER_CON-72 |  |  | YES | TUNEC101WS01DAMPERCON-72 | 24
B2.1 | N |  | East Shaft Station to exhaust duct damper 3 | TUN:EC101 | ES01:DAMPER | MSFD | CON-25 | EC101_RTU | [9 empty] | &CON-25 | TUN_EC101_ES01_DAMPER_CON-25 |  |  | YES | TUNEC101ES01DAMPERCON-25 | 24
B2.1 | N |  | East Shaft Station to exhaust duct damper 4 | TUN:EC101 | ES01:DAMPER | MSFD | CON-26 | EC101_RTU | [9 empty] | &CON-26 | TUN_EC101_ES01_DAMPER_CON-26 |  |  | YES | TUNEC101ES01DAMPERCON-26 | 24
B1.8 | Y |  |  | MEP damper : Station Cooling damper (SCD)
B2.1 | N |  | West Shaft Station Cooling damper 1 | TUN:EC101 | WS01:DAMPER | MSFD | CON-79 | EC101_RTU | [9 empty] | &CON-79 | TUN_EC101_WS01_DAMPER_CON-79 |  |  | YES | TUNEC101WS01DAMPERCON-79 | 24
B2.1 | N |  | West Shaft Station Cooling damper 2 | TUN:EC101 | WS01:DAMPER | MSFD | CON-34 | EC101_RTU | [9 empty] | &CON-34 | TUN_EC101_WS01_DAMPER_CON-34 |  |  | YES | TUNEC101WS01DAMPERCON-34 | 24
B2.1 | N |  | East Shaft Station Cooling damper 3 | TUN:EC101 | ES01:DAMPER | MSFD | CON-24 | EC101_RTU | [9 empty] | &CON-24 | TUN_EC101_ES01_DAMPER_CON-24 |  |  | YES | TUNEC101ES01DAMPERCON-24 | 24
B2.1 | N |  | East Shaft Station Cooling damper 4 | TUN:EC101 | ES01:DAMPER | MSFD | CON-42 | EC101_RTU | [9 empty] | &CON-42 | TUN_EC101_ES01_DAMPER_CON-42 |  |  | YES | TUNEC101ES01DAMPERCON-42 | 24
B1.8 | Y |  |  | Tunnel AIR HANDLING UNIT
B2.1 | N |  | West ShaftTunnel Air Handling Unit 1 | TUN:EC101 | WS01:AHU | AHU | PLA-01 | EC101_RTU | [9 empty] | &PLA-01 | TUN_EC101_WS01_AHU_PLA-01 |  |  | YES | TUNEC101WS01AHUPLA-01 | 21
B2.1 | N |  | East ShaftTunnel Air Handling Unit 2 | TUN:EC101 | ES01:AHU | AHU | PLA-02 | EC101_RTU | [9 empty] | &PLA-02 | TUN_EC101_ES01_AHU_PLA-02 |  |  | YES | TUNEC101ES01AHUPLA-02 | 21
B1.8 | Y |  |  | MMS Equipment
B2.1 | N |  | Station PLC (MMS) | TUN:EC101 | MMS | SPLCMMS | SPLC01 | EC101_RTU | [9 empty] | &SPLC01 | TUN_EC101_MMS_SPLC01 |  |  | YES | TUNEC101MMSSPLC01 | 17
B1.8 | Y |  |  | Electrical Equipment
B2.1 | N |  | EC101-EL0-LBS01 | TUN:EC101 | MMS | ADS | EL0-LBS01 | EC101_RTU | [9 empty] | &EL0-LBS01 | TUN_EC101_MMS_EL0-LBS01 |  |  | YES | TUNEC101MMSEL0-LBS01 | 20
B2.1 | N |  | EC101-EL0-LBS02 | TUN:EC101 | MMS | ADS | EL0-LBS02 | EC101_RTU | [9 empty] | &EL0-LBS02 | TUN_EC101_MMS_EL0-LBS02 |  |  | YES | TUNEC101MMSEL0-LBS02 | 20
B2.1 | N |  | EC101-MV-TRF01 | TUN:EC101 | MMS | TRF | MV-TRF01 | EC101_RTU | [9 empty] | &MV-TRF01 | TUN_EC101_MMS_MV-TRF01 |  |  | YES | TUNEC101MMSMV-TRF01 | 19
B2.1 | N |  | EC101-MV-TRF02 | TUN:EC101 | MMS | TRF | MV-TRF02 | EC101_RTU | [9 empty] | &MV-TRF02 | TUN_EC101_MMS_MV-TRF02 |  |  | YES | TUNEC101MMSMV-TRF02 | 19
B2.1 | N |  | EC101-EL0-CBC01 | TUN:EC101 | MMS | ACB | EL0-CBC01 | EC101_RTU | [9 empty] | &EL0-CBC01 | TUN_EC101_MMS_EL0-CBC01 |  |  | YES | TUNEC101MMSEL0-CBC01 | 20
B2.1 | N |  | EC101-EL0-CBC02 | TUN:EC101 | MMS | ACB | EL0-CBC02 | EC101_RTU | [9 empty] | &EL0-CBC02 | TUN_EC101_MMS_EL0-CBC02 |  |  | YES | TUNEC101MMSEL0-CBC02 | 20
B2.1 | N |  | EC101-LPS-MDB01 | TUN:EC101 | MMS | MDB | LPS-MDB01 | EC101_RTU | [9 empty] | &LPS-MDB01 | TUN_EC101_MMS_LPS-MDB01 |  |  | YES | TUNEC101MMSLPS-MDB01 | 20
B2.1 | N |  | EC101-LPS-MDB02 | TUN:EC101 | MMS | MDB | LPS-MDB02 | EC101_RTU | [9 empty] | &LPS-MDB02 | TUN_EC101_MMS_LPS-MDB02 |  |  | YES | TUNEC101MMSLPS-MDB02 | 20
B1.8 | Y |  |  | Electrical Panel EL1 I/O 01
B2.1 | N |  | EC101-EL1-IO01 | TUN:EC101 | MMS | EL | EL1-IO01 | EC101_RTU | [9 empty] | &EL1-IO01 | TUN_EC101_MMS_EL1-IO01 |  |  | YES | TUNEC101MMSEL1-IO01 | 19
B2.1 | N |  | MCB EC101-EL0-LBS01 | TUN:EC101 | MMS | MCB | EL0-LBS01 | EC101_RTU | [9 empty] | &EL0-LBS01 | TUN_EC101_MMS_EL0-LBS01 |  |  | YES | TUNEC101MMSEL0-LBS01 | 20
B2.1 | N |  | MCB EC101-EL0-LBS02 | TUN:EC101 | MMS | MCB | EL0-LBS02 | EC101_RTU | [9 empty] | &EL0-LBS02 | TUN_EC101_MMS_EL0-LBS02 |  |  | YES | TUNEC101MMSEL0-LBS02 | 20
B2.1 | N |  | MCB EC101-EL0-CBC01 | TUN:EC101 | MMS | MCB | EL0-CBC01 | EC101_RTU | [9 empty] | &EL0-CBC01 | TUN_EC101_MMS_EL0-CBC01 |  |  | YES | TUNEC101MMSEL0-CBC01 | 20
B2.1 | N |  | MCB EC101-EL0-CBC02 | TUN:EC101 | MMS | MCB | EL0-CBC02 | EC101_RTU | [9 empty] | &EL0-CBC02 | TUN_EC101_MMS_EL0-CBC02 |  |  | YES | TUNEC101MMSEL0-CBC02 | 20
B2.1 | N |  | MCCB EC101-EL1-UPS | TUN:EC101 | MMS | MCCB | EL1-UPS | EC101_RTU | [9 empty] | &EL1-UPS | TUN_EC101_MMS_EL1-UPS |  |  | YES | TUNEC101MMSEL1-UPS | 18
B2.1 | N |  | MCB UPS EC101-EL0-LBS01 | TUN:EC101 | MMS | MCB | UPS_EL0-LBS01 | EC101_RTU | [9 empty] | &UPS-EL0-LBS01 | TUN_EC101_MMS_UPS_EL0-LBS01 |  |  | YES | TUNEC101MMSUPS_EL0-LBS01 | 24
B2.1 | N |  | MCB UPS EC101-EL0-LBS02 | TUN:EC101 | MMS | MCB | UPS_EL0-LBS02 | EC101_RTU | [9 empty] | &UPS-EL0-LBS02 | TUN_EC101_MMS_UPS_EL0-LBS02 |  |  | YES | TUNEC101MMSUPS_EL0-LBS02 | 24
B2.1 | N |  | MCB UPS EC101-EL0-CBC01 | TUN:EC101 | MMS | MCB | UPS_EL0-CBC01 | EC101_RTU | [9 empty] | &UPS-EL0-CBC01 | TUN_EC101_MMS_UPS_EL0-CBC01 |  |  | YES | TUNEC101MMSUPS_EL0-CBC01 | 24
B2.1 | N |  | MCB UPS EC101-EL0-CBC02 | TUN:EC101 | MMS | MCB | UPS_EL0-CBC02 | EC101_RTU | [9 empty] | &UPS-EL0-CBC02 | TUN_EC101_MMS_UPS_EL0-CBC02 |  |  | YES | TUNEC101MMSUPS_EL0-CBC02 | 24
B2.1 | N |  | MCB UPS EC101-EL1-VSD01 | TUN:EC101 | MMS | MCB | UPS_EL1-VSD01 | EC101_RTU | [9 empty] | &UPS-EL1-VSD01 | TUN_EC101_MMS_UPS_EL1-VSD01 |  |  | YES | TUNEC101MMSUPS_EL1-VSD01 | 24
B2.1 | N |  | MCB UPS EC101-EL1-VSD02 | TUN:EC101 | MMS | MCB | UPS_EL1-VSD02 | EC101_RTU | [9 empty] | &UPS-EL1-VSD02 | TUN_EC101_MMS_UPS_EL1-VSD02 |  |  | YES | TUNEC101MMSUPS_EL1-VSD02 | 24
B2.1 | N |  | MCB 3P EC101-VT3-IDP01 | TUN:EC101 | MMS | MCB | 3P-VT3-IDP01 | EC101_RTU | [9 empty] | &3P-VT3-IDP01 | TUN_EC101_MMS_3P-VT3-IDP01 |  |  | YES | TUNEC101MMS3P-VT3-IDP01 | 23
B2.1 | N |  | MCB 2P EC101-VT3-IDP01 | TUN:EC101 | MMS | MCB | 2P-VT3-IDP01 | EC101_RTU | [9 empty] | &2P-VT3-IDP01 | TUN_EC101_MMS_2P-VT3-IDP01 |  |  | YES | TUNEC101MMS2P-VT3-IDP01 | 23
B2.1 | N |  | MCB 3P EC101-VT4-IDP01 | TUN:EC101 | MMS | MCB | 3P-VT4-IDP01 | EC101_RTU | [9 empty] | &3P-VT4-IDP01 | TUN_EC101_MMS_3P-VT4-IDP01 |  |  | YES | TUNEC101MMS3P-VT4-IDP01 | 23
B2.1 | N |  | MCB 2P EC101-VT4-IDP01 | TUN:EC101 | MMS | MCB | 2P-VT4-IDP01 | EC101_RTU | [9 empty] | &2P-VT4-IDP01 | TUN_EC101_MMS_2P-VT4-IDP01 |  |  | YES | TUNEC101MMS2P-VT4-IDP01 | 23
B2.1 | N |  | MCB 3P EC101-VT6-TDP01-01 | TUN:EC101 | MMS | MCB | 3P-VT6-TDP01-01 | EC101_RTU | [9 empty] | &3P-VT6-TDP01-01 | TUN_EC101_MMS_3P-VT6-TDP01-01 |  |  | YES | TUNEC101MMS3P-VT6-TDP01-01 | 26
B2.1 | N |  | MCB 2P EC101-VT6-TDP01-01 | TUN:EC101 | MMS | MCB | 2P-VT6-TDP01-01 | EC101_RTU | [9 empty] | &2P-VT6-TDP01-01 | TUN_EC101_MMS_2P-VT6-TDP01-01 |  |  | YES | TUNEC101MMS2P-VT6-TDP01-01 | 26
B2.1 | N |  | MCB 3P EC101-VT6-TDP01-02 | TUN:EC101 | MMS | MCB | 3P-VT6-TDP01-02 | EC101_RTU | [9 empty] | &3P-VT6-TDP01-02 | TUN_EC101_MMS_3P-VT6-TDP01-02 |  |  | YES | TUNEC101MMS3P-VT6-TDP01-02 | 26
B2.1 | N |  | MCB 2P EC101-VT6-TDP01-02 | TUN:EC101 | MMS | MCB | 2P-VT6-TDP01-02 | EC101_RTU | [9 empty] | &2P-VT6-TDP01-02 | TUN_EC101_MMS_2P-VT6-TDP01-02 |  |  | YES | TUNEC101MMS2P-VT6-TDP01-02 | 26
B2.1 | N |  | MCB 3P EC101-VT6-TDP01-03 | TUN:EC101 | MMS | MCB | 3P-VT6-TDP01-03 | EC101_RTU | [9 empty] | &3P-VT6-TDP01-03 | TUN_EC101_MMS_3P-VT6-TDP01-03 |  |  | YES | TUNEC101MMS3P-VT6-TDP01-03 | 26
B2.1 | N |  | MCB 2P EC101-VT6-TDP01-03 | TUN:EC101 | MMS | MCB | 2P-VT6-TDP01-03 | EC101_RTU | [9 empty] | &2P-VT6-TDP01-03 | TUN_EC101_MMS_2P-VT6-TDP01-03 |  |  | YES | TUNEC101MMS2P-VT6-TDP01-03 | 26
B2.1 | N |  | MCB 3P EC101-FR2-BDP01-01 | TUN:EC101 | MMS | MCB | 3P--FR2-BDP01-01 | EC101_RTU | [9 empty] | &3P--FR2-BDP01-01 | TUN_EC101_MMS_3P--FR2-BDP01-01 |  |  | YES | TUNEC101MMS3P--FR2-BDP01-01 | 27
B2.1 | N |  | MCB 2P EC101-FR2-BDP01-01 | TUN:EC101 | MMS | MCB | 2P--FR2-BDP01-01 | EC101_RTU | [9 empty] | &2P--FR2-BDP01-01 | TUN_EC101_MMS_2P--FR2-BDP01-01 |  |  | YES | TUNEC101MMS2P--FR2-BDP01-01 | 27
B2.1 | N |  | MCB 3P EC101-FR2-BDP01-02 | TUN:EC101 | MMS | MCB | 3P--FR2-BDP01-02 | EC101_RTU | [9 empty] | &3P--FR2-BDP01-02 | TUN_EC101_MMS_3P--FR2-BDP01-02 |  |  | YES | TUNEC101MMS3P--FR2-BDP01-02 | 27
B2.1 | N |  | MCB 2P EC101-FR2-BDP01-02 | TUN:EC101 | MMS | MCB | 2P--FR2-BDP01-02 | EC101_RTU | [9 empty] | &2P--FR2-BDP01-02 | TUN_EC101_MMS_2P--FR2-BDP01-02 |  |  | YES | TUNEC101MMS2P--FR2-BDP01-02 | 27
B2.1 | N |  | MCB EC101-MSFD-CON-24 | TUN:EC101 | MMS | MCB | MSFD-CON-24 | EC101_RTU | [9 empty] | &MSFD-CON-24 | TUN_EC101_MMS_MSFD-CON-24 |  |  | YES | TUNEC101MMSMSFD-CON-24 | 22
B2.1 | N |  | MCB EC101-MSFD-CON-42 | TUN:EC101 | MMS | MCB | MSFD-CON-42 | EC101_RTU | [9 empty] | &MSFD-CON-42 | TUN_EC101_MMS_MSFD-CON-42 |  |  | YES | TUNEC101MMSMSFD-CON-42 | 22
B2.1 | N |  | MCB EC101-MSFD-CON-33 | TUN:EC101 | MMS | MCB | MSFD-CON-33 | EC101_RTU | [9 empty] | &MSFD-CON-33 | TUN_EC101_MMS_MSFD-CON-33 |  |  | YES | TUNEC101MMSMSFD-CON-33 | 22
B1.8 | Y |  |  | Electrical Panel EL2 I/O 01
B2.1 | N |  | EC101-EL2-IO01 | TUN:EC101 | MMS | EL | EL2-IO01 | EC101_RTU | [9 empty] | &EL2-IO01 | TUN_EC101_MMS_EL2-IO01 |  |  | YES | TUNEC101MMSEL2-IO01 | 19
B2.1 | N |  | MCCB EC101-EL2-UPS | TUN:EC101 | MMS | MCCB | EL2-UPS | EC101_RTU | [9 empty] | &EL2-UPS | TUN_EC101_MMS_EL2-UPS |  |  | YES | TUNEC101MMSEL2-UPS | 18
B2.1 | N |  | LBS EC101-EL2-UPS | TUN:EC101 | MMS | LBS | EL2-UPS | EC101_RTU | [9 empty] | &EL2-UPS | TUN_EC101_MMS_EL2-UPS |  |  | YES | TUNEC101MMSEL2-UPS | 18
B2.1 | N |  | MCB UPS EC101-EL2-VSD01 | TUN:EC101 | MMS | MCB | UPS_EL2-VSD01 | EC101_RTU | [9 empty] | &UPS-EL2-VSD01 | TUN_EC101_MMS_UPS_EL2-VSD01 |  |  | YES | TUNEC101MMSUPS_EL2-VSD01 | 24
B2.1 | N |  | MCB UPS EC101-EL2-VSD02 | TUN:EC101 | MMS | MCB | UPS_EL2-VSD02 | EC101_RTU | [9 empty] | &UPS-EL2-VSD02 | TUN_EC101_MMS_UPS_EL2-VSD02 |  |  | YES | TUNEC101MMSUPS_EL2-VSD02 | 24
B2.1 | N |  | MCB 3P EC101-VT1-IDP01 | TUN:EC101 | MMS | MCB | 3P-VT1-IDP01 | EC101_RTU | [9 empty] | &3P-VT1-IDP01 | TUN_EC101_MMS_3P-VT1-IDP01 |  |  | YES | TUNEC101MMS3P-VT1-IDP01 | 23
B2.1 | N |  | MCB 2P EC101-VT1-IDP01 | TUN:EC101 | MMS | MCB | 2P-VT1-IDP01 | EC101_RTU | [9 empty] | &2P-VT1-IDP01 | TUN_EC101_MMS_2P-VT1-IDP01 |  |  | YES | TUNEC101MMS2P-VT1-IDP01 | 23
B2.1 | N |  | MCB 3P EC101-VT2-IDP01 | TUN:EC101 | MMS | MCB | 3P-VT2-IDP01 | EC101_RTU | [9 empty] | &3P-VT2-IDP01 | TUN_EC101_MMS_3P-VT2-IDP01 |  |  | YES | TUNEC101MMS3P-VT2-IDP01 | 23
B2.1 | N |  | MCB 2P EC101-VT2-IDP01 | TUN:EC101 | MMS | MCB | 2P-VT2-IDP01 | EC101_RTU | [9 empty] | &2P-VT2-IDP01 | TUN_EC101_MMS_2P-VT2-IDP01 |  |  | YES | TUNEC101MMS2P-VT2-IDP01 | 23
B2.1 | N |  | MCB 3P EC101-VT5-IDP01-01 | TUN:EC101 | MMS | MCB | 3P-VT5-IDP01-01 | EC101_RTU | [9 empty] | &3P-VT5-IDP01-01 | TUN_EC101_MMS_3P-VT5-IDP01-01 |  |  | YES | TUNEC101MMS3P-VT5-IDP01-01 | 26
B2.1 | N |  | MCB 2P EC101-VT5-IDP01-01 | TUN:EC101 | MMS | MCB | 2P-VT5-IDP01-01 | EC101_RTU | [9 empty] | &2P-VT5-IDP01-01 | TUN_EC101_MMS_2P-VT5-IDP01-01 |  |  | YES | TUNEC101MMS2P-VT5-IDP01-01 | 26
B2.1 | N |  | MCB 3P EC101-VT5-IDP01-02 | TUN:EC101 | MMS | MCB | 3P-VT5-IDP01-02 | EC101_RTU | [9 empty] | &3P-VT5-IDP01-02 | TUN_EC101_MMS_3P-VT5-IDP01-02 |  |  | YES | TUNEC101MMS3P-VT5-IDP01-02 | 26
B2.1 | N |  | MCB 2P EC101-VT5-IDP01-02 | TUN:EC101 | MMS | MCB | 2P-VT5-IDP01-02 | EC101_RTU | [9 empty] | &2P-VT5-IDP01-02 | TUN_EC101_MMS_2P-VT5-IDP01-02 |  |  | YES | TUNEC101MMS2P-VT5-IDP01-02 | 26
B2.1 | N |  | MCB 3P EC101-VT5-IDP01-03 | TUN:EC101 | MMS | MCB | 3P-VT5-IDP01-03 | EC101_RTU | [9 empty] | &3P-VT5-IDP01-03 | TUN_EC101_MMS_3P-VT5-IDP01-03 |  |  | YES | TUNEC101MMS3P-VT5-IDP01-03 | 26
B2.1 | N |  | MCB 2P EC101-VT5-IDP01-03 | TUN:EC101 | MMS | MCB | 2P-VT5-IDP01-03 | EC101_RTU | [9 empty] | &2P-VT5-IDP01-03 | TUN_EC101_MMS_2P-VT5-IDP01-03 |  |  | YES | TUNEC101MMS2P-VT5-IDP01-03 | 26
B2.1 | N |  | MCB 3P EC101-FR1-BDP01-01 | TUN:EC101 | MMS | MCB | 3P-FR1-BDP01-01 | EC101_RTU | [9 empty] | &3P-FR1-BDP01-01 | TUN_EC101_MMS_3P-FR1-BDP01-01 |  |  | YES | TUNEC101MMS3P-FR1-BDP01-01 | 26
B2.1 | N |  | MCB 2P EC101-FR1-BDP01-01 | TUN:EC101 | MMS | MCB | 2P-FR1-BDP01-01 | EC101_RTU | [9 empty] | &2P-FR1-BDP01-01 | TUN_EC101_MMS_2P-FR1-BDP01-01 |  |  | YES | TUNEC101MMS2P-FR1-BDP01-01 | 26
B2.1 | N |  | MCB 3P EC101-FR1-BDP01-02 | TUN:EC101 | MMS | MCB | 3P-FR1-BDP01-02 | EC101_RTU | [9 empty] | &3P-FR1-BDP01-02 | TUN_EC101_MMS_3P-FR1-BDP01-02 |  |  | YES | TUNEC101MMS3P-FR1-BDP01-02 | 26
B2.1 | N |  | MCB 2P EC101-FR1-BDP01-02 | TUN:EC101 | MMS | MCB | 2P-FR1-BDP01-02 | EC101_RTU | [9 empty] | &2P-FR1-BDP01-02 | TUN_EC101_MMS_2P-FR1-BDP01-02 |  |  | YES | TUNEC101MMS2P-FR1-BDP01-02 | 26
B2.1 | N |  | MCB EC101-MSFD-CON-79 | TUN:EC101 | MMS | MCB | MSFD-CON-79 | EC101_RTU | [9 empty] | &MSFD-CON-79 | TUN_EC101_MMS_MSFD-CON-79 |  |  | YES | TUNEC101MMSMSFD-CON-79 | 22
B2.1 | N |  | MCB EC101-MSFD-CON-34 | TUN:EC101 | MMS | MCB | MSFD-CON-34 | EC101_RTU | [9 empty] | &MSFD-CON-34 | TUN_EC101_MMS_MSFD-CON-34 |  |  | YES | TUNEC101MMSMSFD-CON-34 | 22
B2.1 | N |  | MCB EC101-MSFD-CON-68 | TUN:EC101 | MMS | MCB | MSFD-CON-68 | EC101_RTU | [9 empty] | &MSFD-CON-68 | TUN_EC101_MMS_MSFD-CON-68 |  |  | YES | TUNEC101MMSMSFD-CON-68 | 22
B1.8 | Y |  |  | EC1-0A SHAFT
B1.8 | Y |  |  | LOCAL CONTROL PANEL (LCP) [STATION HMI]
B2.1 | N |  | Local control panel | TUN:EC10A | SCR | LCP | LCP01 | EC10A_RTU | [9 empty] | &LCP01 | TUN_EC10A_SCR_LCP01 |  |  | YES | TUNEC10ASCRLCP01 | 16
B1.8 | Y |  |  | FIRE MANUAL OVERRIDE PANEL (FMOP)
B2.1 | N |  | Fire control panel | TUN:EC10A | SCR | FMOP | FMOP01 | EC10A_RTU | [9 empty] | &FMOP01 | TUN_EC10A_SCR_FMOP01 |  |  | YES | TUNEC10ASCRFMOP01 | 17
B1.8 | Y |  |  | Station PLC (SPLC)
B2.1 | N |  | Station PLC | TUN:EC10A | TEL | SPLC | PLC01 | EC10A_RTU | [9 empty] | &PLC01 | TUN_EC10A_TEL_PLC01 |  |  | YES | TUNEC10ATELPLC01 | 16
B1.8 | Y |  |  | Switch (SWI)
B2.1 | N |  | Switch | TUN:EC10A | TEL | SWI | SWI01 | EC10A_RTU | [9 empty] | &SWI01 | TUN_EC10A_TEL_SWI01 |  |  | YES | TUNEC10ATELSWI01 | 16
B1.8 | Y |  |  | Outdoor temperature sensor (OTS)
B2.1 | N |  | Outdoor temperature sensor 1 | TUN:EC10A | OTS | OTS | OTS001 | EC10A_RTU | [9 empty] | &OTS001 | TUN_EC10A_OTS_OTS001 |  |  | YES | TUNEC10AOTSOTS001 | 17
B1.8 | Y |  |  | Tunnel temperature & humidity sensor (TTS)
B2.1 | N |  | Tunnel to QEC-01 temperature sensor 1 | TUN:EC10A | SENSOR | TTS | TS100421 | EC10A_RTU | [9 empty] | &TS100421 | TUN_EC10A_SENSOR_TS100421 |  |  | YES | TUNEC10ASENSORTS100421 | 22
B2.1 | N |  | Tunnel to QEC-01 temperature sensor 2 | TUN:EC10A | SENSOR | TTS | TS100521 | EC10A_RTU | [9 empty] | &TS100521 | TUN_EC10A_SENSOR_TS100521 |  |  | YES | TUNEC10ASENSORTS100521 | 22
B2.1 | N |  | Tunnel to EC1-01 temperature sensor 1 | TUN:EC10A | SENSOR | TTS | TS100767 | EC10A_RTU | [9 empty] | &TS100767 | TUN_EC10A_SENSOR_TS100767 |  |  | YES | TUNEC10ASENSORTS100767 | 22
B2.1 | N |  | Tunnel to EC1-01 temperature sensor 2 | TUN:EC10A | SENSOR | TTS | TS100906 | EC10A_RTU | [9 empty] | &TS100906 | TUN_EC10A_SENSOR_TS100906 |  |  | YES | TUNEC10ASENSORTS100906 | 22
B1.8 | Y |  |  | Air velocity sensor (VS)
B2.1 | N |  | Tunnel to QEC-01 Air velocity sensor | TUN:EC10A | SENSOR | VS | VS100456 | EC10A_RTU | [9 empty] | &VS100456 | TUN_EC10A_SENSOR_VS100456 |  |  | YES | TUNEC10ASENSORVS100456 | 22
B2.1 | N |  | Tunnel to EC1-01 Air velocity sensor | TUN:EC10A | SENSOR | VS | VS100862 | EC10A_RTU | [9 empty] | &VS100862 | TUN_EC10A_SENSOR_VS100862 |  |  | YES | TUNEC10ASENSORVS100862 | 22
B1.8 | Y |  |  | Tunnel ventilation fan (TVF)
B2.1 | N |  | Shaft Tunnel ventilation fan 1 | TUN:EC10A | TVF | TVF | VT1-TVF01 | EC10A_RTU | [9 empty] | &VT1-TVF01 | TUN_EC10A_TVF_VT1-TVF01 |  |  | YES | TUNEC10ATVFVT1-TVF01 | 20
B2.1 | N |  | Shaft Tunnel ventilation fan 2 | TUN:EC10A | TVF | TVF | VT2-TVF01 | EC10A_RTU | [9 empty] | &VT2-TVF01 | TUN_EC10A_TVF_VT2-TVF01 |  |  | YES | TUNEC10ATVFVT2-TVF01 | 20
B1.8 | Y |  |  | TVS Damper : Isolation damper (IDP)
B2.1 | N |  | Isolation damper 1 | TUN:EC10A | DAMPER | IDP | VT1-IDP01 | EC10A_RTU | [9 empty] | &VT1-IDP01 | TUN_EC10A_DAMPER_VT1-IDP01 |  |  | YES | TUNEC10ADAMPERVT1-IDP01 | 23
B2.1 | N |  | Isolation damper 2 | TUN:EC10A | DAMPER | IDP | VT2-IDP01 | EC10A_RTU | [9 empty] | &VT2-IDP01 | TUN_EC10A_DAMPER_VT2-IDP01 |  |  | YES | TUNEC10ADAMPERVT2-IDP01 | 23
B1.8 | Y |  |  | PRESSURIZATION FAN (PFA)
B2.1 | N |  | Pressurization fan Stair 1 Lobby | TUN:EC10A | PFA | PFA | LPF-01 | EC10A_RTU | [9 empty] | &LPF-01 | TUN_EC10A_PFA_LPF-01 |  |  | YES | TUNEC10APFALPF-01 | 17
B2.1 | N |  | Pressurization fan Escape Stair | TUN:EC10A | PFA | PFA | SPF-01 | EC10A_RTU | [9 empty] | &SPF-01 | TUN_EC10A_PFA_SPF-01 |  |  | YES | TUNEC10APFASPF-01 | 17
B1.8 | Y |  |  | MMS Equipment
B2.1 | N |  | Station PLC (MMS) | TUN:EC10A | MMS | SPLCMMS | SPLC01 | EC10A_RTU | [9 empty] | &SPLC01 | TUN_EC10A_MMS_SPLC01 |  |  | YES | TUNEC10AMMSSPLC01 | 17
B1.8 | Y |  |  | Electrical Equipment
B2.1 | N |  | EC10A-EL3-LBW01 | TUN:EC10A | MMS | ADS | EL3-LBW01 | EC10A_RTU | [9 empty] | &EL3-LBW01 | TUN_EC10A_MMS_EL3-LBW01 |  |  | YES | TUNEC10AMMSEL3-LBW01 | 20
B2.1 | N |  | EC10A-EL3-LBW02 | TUN:EC10A | MMS | ADS | EL3-LBW02 | EC10A_RTU | [9 empty] | &EL3-LBW02 | TUN_EC10A_MMS_EL3-LBW02 |  |  | YES | TUNEC10AMMSEL3-LBW02 | 20
B2.1 | N |  | EC10A-EL3-TRF01 | TUN:EC10A | MMS | TRF | EL3-TRF01 | EC10A_RTU | [9 empty] | &EL3-TRF01 | TUN_EC10A_MMS_EL3-TRF01 |  |  | YES | TUNEC10AMMSEL3-TRF01 | 20
B2.1 | N |  | EC10A-EL3-TRF02 | TUN:EC10A | MMS | TRF | EL3-TRF02 | EC10A_RTU | [9 empty] | &EL3-TRF02 | TUN_EC10A_MMS_EL3-TRF02 |  |  | YES | TUNEC10AMMSEL3-TRF02 | 20
B2.1 | N |  | EC10A-EL3-MDB01 | TUN:EC10A | MMS | MDB | EL3-MDB01 | EC10A_RTU | [9 empty] | &EL3-MDB01 | TUN_EC10A_MMS_EL3-MDB01 |  |  | YES | TUNEC10AMMSEL3-MDB01 | 20
B1.8 | Y |  |  | Electrical Panel EL3 PLC 01
B2.1 | N |  | EC10A-EL3-PLC01 | TUN:EC10A | MMS | EL | EL3-PLC01 | EC10A_RTU | [9 empty] | &EL3-PLC01 | TUN_EC10A_MMS_EL3-PLC01 |  |  | YES | TUNEC10AMMSEL3-PLC01 | 20
B2.1 | N |  | MCB EC10A-EL3-LBW01 | TUN:EC10A | MMS | MCB | EL3-LBW01 | EC10A_RTU | [9 empty] | &EL3-LBW01 | TUN_EC10A_MMS_EL3-LBW01 |  |  | YES | TUNEC10AMMSEL3-LBW01 | 20
B2.1 | N |  | MCB EC10A-EL3-LBW02 | TUN:EC10A | MMS | MCB | EL3-LBW02 | EC10A_RTU | [9 empty] | &EL3-LBW02 | TUN_EC10A_MMS_EL3-LBW02 |  |  | YES | TUNEC10AMMSEL3-LBW02 | 20
B2.1 | N |  | MCCB EC10A-EL3-UPS | TUN:EC10A | MMS | MCCB | EL3-UPS | EC10A_RTU | [9 empty] | &EL3-UPS | TUN_EC10A_MMS_EL3-UPS |  |  | YES | TUNEC10AMMSEL3-UPS | 18
B2.1 | N |  | LBS EC10A-EL3-UPS | TUN:EC10A | MMS | LBS | EL3-UPS | EC10A_RTU | [9 empty] | &EL3-UPS | TUN_EC10A_MMS_EL3-UPS |  |  | YES | TUNEC10AMMSEL3-UPS | 18
B2.1 | N |  | MCB UPS EC10A-EL3-VSD01 | TUN:EC10A | MMS | MCB | UPS_EL3-VSD01 | EC10A_RTU | [9 empty] | &UPS-EL3-VSD01 | TUN_EC10A_MMS_UPS_EL3-VSD01 |  |  | YES | TUNEC10AMMSUPS_EL3-VSD01 | 24
B2.1 | N |  | MCB UPS EC10A-EL3-VSD02 | TUN:EC10A | MMS | MCB | UPS_EL3-VSD02 | EC10A_RTU | [9 empty] | &UPS-EL3-VSD02 | TUN_EC10A_MMS_UPS_EL3-VSD02 |  |  | YES | TUNEC10AMMSUPS_EL3-VSD02 | 24
B2.1 | N |  | MCB UPS EC10A-EL3-LBW01 | TUN:EC10A | MMS | MCB | UPS_EL3-LBW01 | EC10A_RTU | [9 empty] | &UPS-EL3-LBW01 | TUN_EC10A_MMS_UPS_EL3-LBW01 |  |  | YES | TUNEC10AMMSUPS_EL3-LBW01 | 24
B2.1 | N |  | MCB UPS EC10A-EL3-LBW02 | TUN:EC10A | MMS | MCB | UPS_EL3-LBW02 | EC10A_RTU | [9 empty] | &UPS-EL3-LBW02 | TUN_EC10A_MMS_UPS_EL3-LBW02 |  |  | YES | TUNEC10AMMSUPS_EL3-LBW02 | 24
B2.1 | N |  | MCB UPS EC10A-EL3-MDB01 | TUN:EC10A | MMS | MCB | UPS_EL3-MDB01 | EC10A_RTU | [9 empty] | &UPS-EL3-MDB01 | TUN_EC10A_MMS_UPS_EL3-MDB01 |  |  | YES | TUNEC10AMMSUPS_EL3-MDB01 | 24
B2.1 | N |  | MCB 3P EC10A-VT1-IDP01 | TUN:EC10A | MMS | MCB | 3P-VT1-IDP01 | EC10A_RTU | [9 empty] | &3P-VT1-IDP01 | TUN_EC10A_MMS_3P-VT1-IDP01 |  |  | YES | TUNEC10AMMS3P-VT1-IDP01 | 23
B2.1 | N |  | MCB 2P EC10A-VT1-IDP01 | TUN:EC10A | MMS | MCB | 2P-VT1-IDP01 | EC10A_RTU | [9 empty] | &2P-VT1-IDP01 | TUN_EC10A_MMS_2P-VT1-IDP01 |  |  | YES | TUNEC10AMMS2P-VT1-IDP01 | 23
B2.1 | N |  | MCB 3P EC10A-VT2-IDP01 | TUN:EC10A | MMS | MCB | 3P-VT2-IDP01 | EC10A_RTU | [9 empty] | &3P-VT2-IDP01 | TUN_EC10A_MMS_3P-VT2-IDP01 |  |  | YES | TUNEC10AMMS3P-VT2-IDP01 | 23
B2.1 | N |  | MCB 2P EC10A-VT2-IDP01 | TUN:EC10A | MMS | MCB | 2P-VT2-IDP01 | EC10A_RTU | [9 empty] | &2P-VT2-IDP01 | TUN_EC10A_MMS_2P-VT2-IDP01 |  |  | YES | TUNEC10AMMS2P-VT2-IDP01 | 23
B1.8 | Y |  |  | QAP-01
B1.8 | Y |  |  | LOCAL CONTROL PANEL (LCP) [STATION HMI]
B2.1 | N |  | Local control panel | TUN:QAP01 | SCR | LCP | LCP01 | QAP01_RTU | [9 empty] | &LCP01 | TUN_QAP01_SCR_LCP01 |  |  | YES | TUNQAP01SCRLCP01 | 16
B1.8 | Y |  |  | FIRE MANUAL OVERRIDE PANEL (FMOP)
B2.1 | N |  | Fire control panel | TUN:QAP01 | SCR | FMOP | FMOP01 | QAP01_RTU | [9 empty] | &FMOP01 | TUN_QAP01_SCR_FMOP01 |  |  | YES | TUNQAP01SCRFMOP01 | 17
B1.8 | Y |  |  | Station PLC (SPLC)
B2.1 | N |  | Station PLC | TUN:QAP01 | TEL | SPLC | PLC01 | QAP01_RTU | [9 empty] | &PLC01 | TUN_QAP01_TEL_PLC01 |  |  | YES | TUNQAP01TELPLC01 | 16
B1.8 | Y |  |  | Switch (SWI)
B2.1 | N |  | Switch | TUN:QAP01 | TEL | SWI | SWI01 | QAP01_RTU | [9 empty] | &SWI01 | TUN_QAP01_TEL_SWI01 |  |  | YES | TUNQAP01TELSWI01 | 16
B1.8 | Y |  |  | PRESSURIZATION FAN (PFA)
B2.1 | N |  | Pressurization fan Lobby 1 | TUN:QAP01 | SS01:PFA | PFA | CON-03 | QAP01_RTU | [9 empty] | &CON-03 | TUN_QAP01_SS01_PFA_CON-03 |  |  | YES | TUNQAP01SS01PFACON-03 | 21
B2.1 | N |  | Pressurization fan Escape Stair 3 | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | QAP01_RTU | [9 empty] | &GRD-01 | TUN_QAP01_SS01_PFA_GRD-01 |  |  | YES | TUNQAP01SS01PFAGRD-01 | 21
B2.1 | N |  | Pressurization fan Lobby 2 | TUN:QAP01 | NS01:PFA | PFA | CON-02 | QAP01_RTU | [9 empty] | &CON-02 | TUN_QAP01_NS01_PFA_CON-02 |  |  | YES | TUNQAP01NS01PFACON-02 | 21
B2.1 | N |  | Pressurization fan Escape Stair 4 | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | QAP01_RTU | [9 empty] | &GRD-03 | TUN_QAP01_NS01_PFA_GRD-03 |  |  | YES | TUNQAP01NS01PFAGRD-03 | 21
B2.1 | N |  | Pressurization fan Stair 1 | TUN:QAP01 | NS01:PFA | PFA | CON-04 | QAP01_RTU | [9 empty] | &CON-04 | TUN_QAP01_NS01_PFA_CON-04 |  |  | YES | TUNQAP01NS01PFACON-04 | 21
B2.1 | N |  | Pressurization fan Corridor 6 | TUN:QAP01 | NS01:PFA | PFA | CON-05 | QAP01_RTU | [9 empty] | &CON-05 | TUN_QAP01_NS01_PFA_CON-05 |  |  | YES | TUNQAP01NS01PFACON-05 | 21
B1.8 | Y |  |  | SMOKE CURTAINS (SMC)
B2.1 | N |  | Smoke Curtains 1 | TUN:QAP01 | SMC | SMC | SMC01 | QAP01_RTU | [9 empty] | &SMC01 | TUN_QAP01_SMC_SMC01 |  |  | YES | TUNQAP01SMCSMC01 | 16
B2.1 | N |  | Smoke Curtains 2 | TUN:QAP01 | SMC | SMC | SMC02 | QAP01_RTU | [9 empty] | &SMC02 | TUN_QAP01_SMC_SMC02 |  |  | YES | TUNQAP01SMCSMC02 | 16
B2.1 | N |  | Smoke Curtains 3 | TUN:QAP01 | SMC | SMC | SMC03 | QAP01_RTU | [9 empty] | &SMC03 | TUN_QAP01_SMC_SMC03 |  |  | YES | TUNQAP01SMCSMC03 | 16
B2.1 | N |  | Smoke Curtains 4 | TUN:QAP01 | SMC | SMC | SMC04 | QAP01_RTU | [9 empty] | &SMC04 | TUN_QAP01_SMC_SMC04 |  |  | YES | TUNQAP01SMCSMC04 | 16
B2.1 | N |  | Smoke Curtains 5 | TUN:QAP01 | SMC | SMC | SMC05 | QAP01_RTU | [9 empty] | &SMC05 | TUN_QAP01_SMC_SMC05 |  |  | YES | TUNQAP01SMCSMC05 | 16
B2.1 | N |  | Smoke Curtains 6 | TUN:QAP01 | SMC | SMC | SMC06 | QAP01_RTU | [9 empty] | &SMC06 | TUN_QAP01_SMC_SMC06 |  |  | YES | TUNQAP01SMCSMC06 | 16
B2.1 | N |  | Smoke Curtains 7 | TUN:QAP01 | SMC | SMC | SMC07 | QAP01_RTU | [9 empty] | &SMC07 | TUN_QAP01_SMC_SMC07 |  |  | YES | TUNQAP01SMCSMC07 | 16
B2.1 | N |  | Smoke Curtains 8 | TUN:QAP01 | SMC | SMC | SMC08 | QAP01_RTU | [9 empty] | &SMC08 | TUN_QAP01_SMC_SMC08 |  |  | YES | TUNQAP01SMCSMC08 | 16
B2.1 | N |  | Smoke Curtains 9 | TUN:QAP01 | SMC | SMC | SMC09 | QAP01_RTU | [9 empty] | &SMC09 | TUN_QAP01_SMC_SMC09 |  |  | YES | TUNQAP01SMCSMC09 | 16
B2.1 | N |  | Smoke Curtains 10 | TUN:QAP01 | SMC | SMC | SMC10 | QAP01_RTU | [9 empty] | &SMC10 | TUN_QAP01_SMC_SMC10 |  |  | YES | TUNQAP01SMCSMC10 | 16
B1.8 | Y |  |  | STATION ENTRANCE DOOR (SED)
B2.1 | N |  | Station entrance door 1 | TUN:QAP01 | SED | SED | SED01 | QAP01_RTU | [9 empty] | &SED01 | TUN_QAP01_SED_SED01 |  |  | YES | TUNQAP01SEDSED01 | 16
B2.1 | N |  | Station entrance door 2 | TUN:QAP01 | SED | SED | SED02 | QAP01_RTU | [9 empty] | &SED02 | TUN_QAP01_SED_SED02 |  |  | YES | TUNQAP01SEDSED02 | 16
B2.1 | N |  | Station entrance door 3 | TUN:QAP01 | SED | SED | SED03 | QAP01_RTU | [9 empty] | &SED03 | TUN_QAP01_SED_SED03 |  |  | YES | TUNQAP01SEDSED03 | 16
B2.1 | N |  | Station entrance door 4 | TUN:QAP01 | SED | SED | SED04 | QAP01_RTU | [9 empty] | &SED04 | TUN_QAP01_SED_SED04 |  |  | YES | TUNQAP01SEDSED04 | 16
B1.8 | Y |  |  | Outdoor temperature sensor (OTS)
B2.1 | N |  | Outdoor temperature sensor 1 | TUN:QAP01 | OTS | OTS | OTS001 | QAP01_RTU | [9 empty] | &OTS001 | TUN_QAP01_OTS_OTS001 |  |  | YES | TUNQAP01OTSOTS001 | 17
B2.1 | N |  | Outdoor temperature sensor 2 | TUN:QAP01 | OTS | OTS | OTS002 | QAP01_RTU | [9 empty] | &OTS002 | TUN_QAP01_OTS_OTS002 |  |  | YES | TUNQAP01OTSOTS002 | 17
B1.8 | Y |  |  | Tunnel ventilation fan (TVF)
B2.1 | N |  | South ShaftTunnel ventilation fan 1 | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | QAP01_RTU | [9 empty] | &VT1-TVF01 | TUN_QAP01_SS01_TVF_VT1-TVF01 |  |  | YES | TUNQAP01SS01TVFVT1-TVF01 | 24
B2.1 | N |  | South ShaftTunnel ventilation fan 2 | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | QAP01_RTU | [9 empty] | &VT2-TVF01 | TUN_QAP01_SS01_TVF_VT2-TVF01 |  |  | YES | TUNQAP01SS01TVFVT2-TVF01 | 24
B2.1 | N |  | North ShaftTunnel ventilation fan 3 | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | QAP01_RTU | [9 empty] | &VT3-TVF01 | TUN_QAP01_NS01_TVF_VT3-TVF01 |  |  | YES | TUNQAP01NS01TVFVT3-TVF01 | 24
B2.1 | N |  | NorthShaftTunnel ventilation fan 4 | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | QAP01_RTU | [9 empty] | &VT4-TVF01 | TUN_QAP01_NS01_TVF_VT4-TVF01 |  |  | YES | TUNQAP01NS01TVFVT4-TVF01 | 24
B1.8 | Y |  |  | Tunnel temperature & humidity sensor (TTS)
B2.1 | N |  | Tunnel to EC1-01 temperature sensor 1 | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | QAP01_RTU | [9 empty] | &TS101733 | TUN_QAP01_SS01_SENSOR_TS101733 |  |  | YES | TUNQAP01SS01SENSORTS101733 | 26
B2.1 | N |  | Tunnel to EC1-01 temperature sensor 2 | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | QAP01_RTU | [9 empty] | &TS101817 | TUN_QAP01_SS01_SENSOR_TS101817 |  |  | YES | TUNQAP01SS01SENSORTS101817 | 26
B2.1 | N |  | Tunnel to QAP-1B temperature sensor 1 | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | QAP01_RTU | [9 empty] | &TS102057 | TUN_QAP01_NS01_SENSOR_TS102057 |  |  | YES | TUNQAP01NS01SENSORTS102057 | 26
B2.1 | N |  | Tunnel to QAP-1B temperature sensor 2 | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | QAP01_RTU | [9 empty] | &TS102121 | TUN_QAP01_NS01_SENSOR_TS102121 |  |  | YES | TUNQAP01NS01SENSORTS102121 | 26
B1.8 | Y |  |  | Air velocity sensor (VS)
B2.1 | N |  | Tunnel to EC1-01 Air velocity sensor | TUN:QAP01 | SS01:SENSOR | VS | VS101763 | QAP01_RTU | [9 empty] | &VS101763 | TUN_QAP01_SS01_SENSOR_VS101763 |  |  | YES | TUNQAP01SS01SENSORVS101763 | 26
B2.1 | N |  | Tunnel to QAP-1B Air velocity sensor | TUN:QAP01 | NS01:SENSOR | VS | VS102092 | QAP01_RTU | [9 empty] | &VS102092 | TUN_QAP01_NS01_SENSOR_VS102092 |  |  | YES | TUNQAP01NS01SENSORVS102092 | 26
B1.8 | Y |  |  | TVS Damper : Tunnel damper (TDP)
B2.1 | N |  | South Shaft Tunnel damper 1 | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | QAP01_RTU | [9 empty] | &VT5-TDP01 | TUN_QAP01_SS01_DAMPER_VT5-TDP01 |  |  | YES | TUNQAP01SS01DAMPERVT5-TDP01 | 27
B2.1 | N |  | North Shaft Tunnel damper 2 | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | QAP01_RTU | [9 empty] | &VT6-TDP01 | TUN_QAP01_NS01_DAMPER_VT6-TDP01 |  |  | YES | TUNQAP01NS01DAMPERVT6-TDP01 | 27
B1.8 | Y |  |  | TVS Damper : Isolation damper (IDP)
B2.1 | N |  | Isolation damper 1 | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | QAP01_RTU | [9 empty] | &VT1-IDP01 | TUN_QAP01_SS01_DAMPER_VT1-IDP01 |  |  | YES | TUNQAP01SS01DAMPERVT1-IDP01 | 27
B2.1 | N |  | Isolation damper 2 | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | QAP01_RTU | [9 empty] | &VT2-IDP01 | TUN_QAP01_SS01_DAMPER_VT2-IDP01 |  |  | YES | TUNQAP01SS01DAMPERVT2-IDP01 | 27
B2.1 | N |  | Isolation damper 3 | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | QAP01_RTU | [9 empty] | &VT3-IDP01 | TUN_QAP01_NS01_DAMPER_VT3-IDP01 |  |  | YES | TUNQAP01NS01DAMPERVT3-IDP01 | 27
B2.1 | N |  | Isolation damper 4 | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | QAP01_RTU | [9 empty] | &VT4-IDP01 | TUN_QAP01_NS01_DAMPER_VT4-IDP01 |  |  | YES | TUNQAP01NS01DAMPERVT4-IDP01 | 27
B1.8 | Y |  |  | TVS Damper : Bypass damper (BDP)
B2.1 | N |  | South Shaft Bypass damper 1 | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | QAP01_RTU | [9 empty] | &FR1-BDP01 | TUN_QAP01_SS01_DAMPER_FR1-BDP01 |  |  | YES | TUNQAP01SS01DAMPERFR1-BDP01 | 27
B2.1 | N |  | North Shaft Bypass damper 2 | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | QAP01_RTU | [9 empty] | &FR2-BDP01 | TUN_QAP01_NS01_DAMPER_FR2-BDP01 |  |  | YES | TUNQAP01NS01DAMPERFR2-BDP01 | 27
B1.8 | Y |  |  | MEP Damper : Tunnel Cooling damper (TCDP)
B2.1 | N |  | South Shaft Tunnel Cooling damper 1 | TUN:QAP01 | SS01:DAMPER | MSFD | CON-63 | QAP01_RTU | [9 empty] | &CON-63 | TUN_QAP01_SS01_DAMPER_CON-63 |  |  | YES | TUNQAP01SS01DAMPERCON-63 | 24
B2.1 | N |  | North Shaft Tunnel Cooling damper 2 | TUN:QAP01 | NS01:DAMPER | MSFD | CON-54 | QAP01_RTU | [9 empty] | &CON-54 | TUN_QAP01_NS01_DAMPER_CON-54 |  |  | YES | TUNQAP01NS01DAMPERCON-54 | 24
B1.8 | Y |  |  | MEP damper : Station to exhaust duct Damper (SEDD)
B2.1 | N |  | South Shaft Station to exhaust duct damper 1 | TUN:QAP01 | SS01:DAMPER | MSFD | CON-66 | QAP01_RTU | [9 empty] | &CON-66 | TUN_QAP01_SS01_DAMPER_CON-66 |  |  | YES | TUNQAP01SS01DAMPERCON-66 | 24
B2.1 | N |  | South Shaft Station to exhaust duct damper 2 | TUN:QAP01 | SS01:DAMPER | MSFD | CON-61 | QAP01_RTU | [9 empty] | &CON-61 | TUN_QAP01_SS01_DAMPER_CON-61 |  |  | YES | TUNQAP01SS01DAMPERCON-61 | 24
B2.1 | N |  | North Shaft Station to exhaust duct damper 3 | TUN:QAP01 | NS01:DAMPER | MSFD | CON-56 | QAP01_RTU | [9 empty] | &CON-56 | TUN_QAP01_NS01_DAMPER_CON-56 |  |  | YES | TUNQAP01NS01DAMPERCON-56 | 24
B2.1 | N |  | North Shaft Station to exhaust duct damper 4 | TUN:QAP01 | NS01:DAMPER | MSFD | CON-51 | QAP01_RTU | [9 empty] | &CON-51 | TUN_QAP01_NS01_DAMPER_CON-51 |  |  | YES | TUNQAP01NS01DAMPERCON-51 | 24
B1.8 | Y |  |  | MEP damper : Station Cooling damper (SCD)
B2.1 | N |  | South Shaft Station Cooling damper 1 | TUN:QAP01 | SS01:DAMPER | MSFD | CON-67 | QAP01_RTU | [9 empty] | &CON-67 | TUN_QAP01_SS01_DAMPER_CON-67 |  |  | YES | TUNQAP01SS01DAMPERCON-67 | 24
B2.1 | N |  | South Shaft Station Cooling damper 2 | TUN:QAP01 | SS01:DAMPER | MSFD | CON-59 | QAP01_RTU | [9 empty] | &CON-59 | TUN_QAP01_SS01_DAMPER_CON-59 |  |  | YES | TUNQAP01SS01DAMPERCON-59 | 24
B2.1 | N |  | North Shaft Station Cooling damper 3 | TUN:QAP01 | NS01:DAMPER | MSFD | CON-58 | QAP01_RTU | [9 empty] | &CON-58 | TUN_QAP01_NS01_DAMPER_CON-58 |  |  | YES | TUNQAP01NS01DAMPERCON-58 | 24
B2.1 | N |  | North Shaft Station Cooling damper 4 | TUN:QAP01 | NS01:DAMPER | MSFD | CON-52 | QAP01_RTU | [9 empty] | &CON-52 | TUN_QAP01_NS01_DAMPER_CON-52 |  |  | YES | TUNQAP01NS01DAMPERCON-52 | 24
B1.8 | Y |  |  | Tunnel AIR HANDLING UNIT
B2.1 | N |  | South ShaftTunnel Air Handling Unit 1 (AHU room 3) | TUN:QAP01 | SS01:AHU | AHU | CON-08 | QAP01_RTU | [9 empty] | &CON-08 | TUN_QAP01_SS01_AHU_CON-08 |  |  | YES | TUNQAP01SS01AHUCON-08 | 21
B2.1 | N |  | South ShaftTunnel Air Handling Unit 2 (AHU room 2) | TUN:QAP01 | SS01:AHU | AHU | CON-07 | QAP01_RTU | [9 empty] | &CON-07 | TUN_QAP01_SS01_AHU_CON-07 |  |  | YES | TUNQAP01SS01AHUCON-07 | 21
B2.1 | N |  | North ShaftTunnel Air Handling Unit 1 (AHU room 4) | TUN:QAP01 | NS01:AHU | AHU | CON-06 | QAP01_RTU | [9 empty] | &CON-06 | TUN_QAP01_NS01_AHU_CON-06 |  |  | YES | TUNQAP01NS01AHUCON-06 | 21
B2.1 | N |  | North ShaftTunnel Air Handling Unit 2 (AHU room 1) | TUN:QAP01 | NS01:AHU | AHU | CON-05 | QAP01_RTU | [9 empty] | &CON-05 | TUN_QAP01_NS01_AHU_CON-05 |  |  | YES | TUNQAP01NS01AHUCON-05 | 21
B1.8 | Y |  |  | MMS Equipment
B2.1 | N |  | Station PLC (MMS) | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | QAP01_RTU | [9 empty] | &SPLC01 | TUN_QAP01_MMS_SPLC01 |  |  | YES | TUNQAP01MMSSPLC01 | 17
B1.8 | Y |  |  | Electrical Equipment
B2.1 | N |  | QAP01-LPS-MDB01 | TUN:QAP01 | MMS | MDB | LPS-MDB01 | QAP01_RTU | [9 empty] | &LPS-MDB01 | TUN_QAP01_MMS_LPS-MDB01 |  |  | YES | TUNQAP01MMSLPS-MDB01 | 20
B2.1 | N |  | QAP01-LPS-MDB02 | TUN:QAP01 | MMS | MDB | LPS-MDB02 | QAP01_RTU | [9 empty] | &LPS-MDB02 | TUN_QAP01_MMS_LPS-MDB02 |  |  | YES | TUNQAP01MMSLPS-MDB02 | 20
B1.8 | Y |  |  | Electrical Panel EL1 I/O 01
B2.1 | N |  | QAP01-EL1-IO01 | TUN:QAP01 | MMS | EL | EL1-IO01 | QAP01_RTU | [9 empty] | &EL1-IO01 | TUN_QAP01_MMS_EL1-IO01 |  |  | YES | TUNQAP01MMSEL1-IO01 | 19
B2.1 | N |  | MCCB QAP01-EL1-UPS | TUN:QAP01 | MMS | MCCB | EL1-UPS | QAP01_RTU | [9 empty] | &EL1-UPS | TUN_QAP01_MMS_EL1-UPS |  |  | YES | TUNQAP01MMSEL1-UPS | 18
B2.1 | N |  | LBS QAP01-EL1-UPS | TUN:QAP01 | MMS | LBS | EL1-UPS | QAP01_RTU | [9 empty] | &EL1-UPS | TUN_QAP01_MMS_EL1-UPS |  |  | YES | TUNQAP01MMSEL1-UPS | 18
B2.1 | N |  | MCB UPS QAP01-EL1-VSD01 | TUN:QAP01 | MMS | MCB | UPS_EL1-VSD01 | QAP01_RTU | [9 empty] | &UPS-EL1-VSD01 | TUN_QAP01_MMS_UPS_EL1-VSD01 |  |  | YES | TUNQAP01MMSUPS_EL1-VSD01 | 24
B2.1 | N |  | MCB UPS QAP01-EL1-VSD02 | TUN:QAP01 | MMS | MCB | UPS_EL1-VSD02 | QAP01_RTU | [9 empty] | &UPS-EL1-VSD02 | TUN_QAP01_MMS_UPS_EL1-VSD02 |  |  | YES | TUNQAP01MMSUPS_EL1-VSD02 | 24
B2.1 | N |  | MCB 3P QAP01-VT3-IDP01 | TUN:QAP01 | MMS | MCB | 3P-VT3-IDP01 | QAP01_RTU | [9 empty] | &3P-VT3-IDP01 | TUN_QAP01_MMS_3P-VT3-IDP01 |  |  | YES | TUNQAP01MMS3P-VT3-IDP01 | 23
B2.1 | N |  | MCB 2P QAP01-VT3-IDP01 | TUN:QAP01 | MMS | MCB | 2P-VT3-IDP01 | QAP01_RTU | [9 empty] | &2P-VT3-IDP01 | TUN_QAP01_MMS_2P-VT3-IDP01 |  |  | YES | TUNQAP01MMS2P-VT3-IDP01 | 23
B2.1 | N |  | MCB 3P QAP01-VT4-IDP01 | TUN:QAP01 | MMS | MCB | 3P-VT4-IDP01 | QAP01_RTU | [9 empty] | &3P-VT4-IDP01 | TUN_QAP01_MMS_3P-VT4-IDP01 |  |  | YES | TUNQAP01MMS3P-VT4-IDP01 | 23
B2.1 | N |  | MCB 2P QAP01-VT4-IDP01 | TUN:QAP01 | MMS | MCB | 2P-VT4-IDP01 | QAP01_RTU | [9 empty] | &2P-VT4-IDP01 | TUN_QAP01_MMS_2P-VT4-IDP01 |  |  | YES | TUNQAP01MMS2P-VT4-IDP01 | 23
B2.1 | N |  | MCB 3P QAP01-VT6-TDP01-01 | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-01 | QAP01_RTU | [9 empty] | &3P-VT6-TDP01-01 | TUN_QAP01_MMS_3P-VT6-TDP01-01 |  |  | YES | TUNQAP01MMS3P-VT6-TDP01-01 | 26
B2.1 | N |  | MCB 2P QAP01-VT6-TDP01-01 | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-01 | QAP01_RTU | [9 empty] | &2P-VT6-TDP01-01 | TUN_QAP01_MMS_2P-VT6-TDP01-01 |  |  | YES | TUNQAP01MMS2P-VT6-TDP01-01 | 26
B2.1 | N |  | MCB 3P QAP01-VT6-TDP01-02 | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-02 | QAP01_RTU | [9 empty] | &3P-VT6-TDP01-02 | TUN_QAP01_MMS_3P-VT6-TDP01-02 |  |  | YES | TUNQAP01MMS3P-VT6-TDP01-02 | 26
B2.1 | N |  | MCB 2P QAP01-VT6-TDP01-02 | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-02 | QAP01_RTU | [9 empty] | &2P-VT6-TDP01-02 | TUN_QAP01_MMS_2P-VT6-TDP01-02 |  |  | YES | TUNQAP01MMS2P-VT6-TDP01-02 | 26
B2.1 | N |  | MCB 3P QAP01-VT6-TDP01-03 | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-03 | QAP01_RTU | [9 empty] | &3P-VT6-TDP01-03 | TUN_QAP01_MMS_3P-VT6-TDP01-03 |  |  | YES | TUNQAP01MMS3P-VT6-TDP01-03 | 26
B2.1 | N |  | MCB 2P QAP01-VT6-TDP01-03 | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-03 | QAP01_RTU | [9 empty] | &2P-VT6-TDP01-03 | TUN_QAP01_MMS_2P-VT6-TDP01-03 |  |  | YES | TUNQAP01MMS2P-VT6-TDP01-03 | 26
B2.1 | N |  | MCB 3P QAP01-FR2-BDP01-01 | TUN:QAP01 | MMS | MCB | 3P--FR2-BDP01-01 | QAP01_RTU | [9 empty] | &3P--FR2-BDP01-01 | TUN_QAP01_MMS_3P--FR2-BDP01-01 |  |  | YES | TUNQAP01MMS3P--FR2-BDP01-01 | 27
B2.1 | N |  | MCB 2P QAP01-FR2-BDP01-01 | TUN:QAP01 | MMS | MCB | 2P--FR2-BDP01-01 | QAP01_RTU | [9 empty] | &2P--FR2-BDP01-01 | TUN_QAP01_MMS_2P--FR2-BDP01-01 |  |  | YES | TUNQAP01MMS2P--FR2-BDP01-01 | 27
B2.1 | N |  | MCB 3P QAP01-FR2-BDP01-02 | TUN:QAP01 | MMS | MCB | 3P--FR2-BDP01-02 | QAP01_RTU | [9 empty] | &3P--FR2-BDP01-02 | TUN_QAP01_MMS_3P--FR2-BDP01-02 |  |  | YES | TUNQAP01MMS3P--FR2-BDP01-02 | 27
B2.1 | N |  | MCB 2P QAP01-FR2-BDP01-02 | TUN:QAP01 | MMS | MCB | 2P--FR2-BDP01-02 | QAP01_RTU | [9 empty] | &2P--FR2-BDP01-02 | TUN_QAP01_MMS_2P--FR2-BDP01-02 |  |  | YES | TUNQAP01MMS2P--FR2-BDP01-02 | 27
B2.1 | N |  | MCB QAP01-MSFD-CON-54 | TUN:QAP01 | MMS | MCB | MSFD-CON-54 | QAP01_RTU | [9 empty] | &MSFD-CON-54 | TUN_QAP01_MMS_MSFD-CON-54 |  |  | YES | TUNQAP01MMSMSFD-CON-54 | 22
B2.1 | N |  | MCB QAP01-MSFD-CON-52 | TUN:QAP01 | MMS | MCB | MSFD-CON-52 | QAP01_RTU | [9 empty] | &MSFD-CON-52 | TUN_QAP01_MMS_MSFD-CON-52 |  |  | YES | TUNQAP01MMSMSFD-CON-52 | 22
B2.1 | N |  | MCB QAP01-MSFD-CON-58 | TUN:QAP01 | MMS | MCB | MSFD-CON-58 | QAP01_RTU | [9 empty] | &MSFD-CON-58 | TUN_QAP01_MMS_MSFD-CON-58 |  |  | YES | TUNQAP01MMSMSFD-CON-58 | 22
B1.8 | Y |  |  | Electrical Panel EL2 I/O 01
B2.1 | N |  | QAP01-EL2-IO01 | TUN:QAP01 | MMS | EL | EL2-IO01 | QAP01_RTU | [9 empty] | &EL2-IO01 | TUN_QAP01_MMS_EL2-IO01 |  |  | YES | TUNQAP01MMSEL2-IO01 | 19
B2.1 | N |  | MCCB QAP01-EL2-UPS | TUN:QAP01 | MMS | MCCB | EL2-UPS | QAP01_RTU | [9 empty] | &EL2-UPS | TUN_QAP01_MMS_EL2-UPS |  |  | YES | TUNQAP01MMSEL2-UPS | 18
B2.1 | N |  | LBS QAP01-EL2-UPS | TUN:QAP01 | MMS | LBS | EL2-UPS | QAP01_RTU | [9 empty] | &EL2-UPS | TUN_QAP01_MMS_EL2-UPS |  |  | YES | TUNQAP01MMSEL2-UPS | 18
B2.1 | N |  | MCB UPS QAP01-EL2-VSD01 | TUN:QAP01 | MMS | MCB | UPS_EL2-VSD01 | QAP01_RTU | [9 empty] | &UPS-EL2-VSD01 | TUN_QAP01_MMS_UPS_EL2-VSD01 |  |  | YES | TUNQAP01MMSUPS_EL2-VSD01 | 24
B2.1 | N |  | MCB UPS QAP01-EL2-VSD02 | TUN:QAP01 | MMS | MCB | UPS_EL2-VSD02 | QAP01_RTU | [9 empty] | &UPS-EL2-VSD02 | TUN_QAP01_MMS_UPS_EL2-VSD02 |  |  | YES | TUNQAP01MMSUPS_EL2-VSD02 | 24
B2.1 | N |  | MCB 3P QAP01-VT1-IDP01 | TUN:QAP01 | MMS | MCB | 3P-VT1-IDP01 | QAP01_RTU | [9 empty] | &3P-VT1-IDP01 | TUN_QAP01_MMS_3P-VT1-IDP01 |  |  | YES | TUNQAP01MMS3P-VT1-IDP01 | 23
B2.1 | N |  | MCB 2P QAP01-VT1-IDP01 | TUN:QAP01 | MMS | MCB | 2P-VT1-IDP01 | QAP01_RTU | [9 empty] | &2P-VT1-IDP01 | TUN_QAP01_MMS_2P-VT1-IDP01 |  |  | YES | TUNQAP01MMS2P-VT1-IDP01 | 23
B2.1 | N |  | MCB 3P QAP01-VT2-IDP01 | TUN:QAP01 | MMS | MCB | 3P-VT2-IDP01 | QAP01_RTU | [9 empty] | &3P-VT2-IDP01 | TUN_QAP01_MMS_3P-VT2-IDP01 |  |  | YES | TUNQAP01MMS3P-VT2-IDP01 | 23
B2.1 | N |  | MCB 2P QAP01-VT2-IDP01 | TUN:QAP01 | MMS | MCB | 2P-VT2-IDP01 | QAP01_RTU | [9 empty] | &2P-VT2-IDP01 | TUN_QAP01_MMS_2P-VT2-IDP01 |  |  | YES | TUNQAP01MMS2P-VT2-IDP01 | 23
B2.1 | N |  | MCB 3P QAP01-VT5-TDP01-01 | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-01 | QAP01_RTU | [9 empty] | &3P-VT5-TDP01-01 | TUN_QAP01_MMS_3P-VT5-TDP01-01 |  |  | YES | TUNQAP01MMS3P-VT5-TDP01-01 | 26
B2.1 | N |  | MCB 2P QAP01-VT5-TDP01-01 | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-01 | QAP01_RTU | [9 empty] | &2P-VT5-TDP01-01 | TUN_QAP01_MMS_2P-VT5-TDP01-01 |  |  | YES | TUNQAP01MMS2P-VT5-TDP01-01 | 26
B2.1 | N |  | MCB 3P QAP01-VT5-TDP01-02 | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-02 | QAP01_RTU | [9 empty] | &3P-VT5-TDP01-02 | TUN_QAP01_MMS_3P-VT5-TDP01-02 |  |  | YES | TUNQAP01MMS3P-VT5-TDP01-02 | 26
B2.1 | N |  | MCB 2P QAP01-VT5-TDP01-02 | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-02 | QAP01_RTU | [9 empty] | &2P-VT5-TDP01-02 | TUN_QAP01_MMS_2P-VT5-TDP01-02 |  |  | YES | TUNQAP01MMS2P-VT5-TDP01-02 | 26
B2.1 | N |  | MCB 3P QAP01-VT5-TDP01-03 | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-03 | QAP01_RTU | [9 empty] | &3P-VT5-TDP01-03 | TUN_QAP01_MMS_3P-VT5-TDP01-03 |  |  | YES | TUNQAP01MMS3P-VT5-TDP01-03 | 26
B2.1 | N |  | MCB 2P QAP01-VT5-TDP01-03 | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-03 | QAP01_RTU | [9 empty] | &2P-VT5-TDP01-03 | TUN_QAP01_MMS_2P-VT5-TDP01-03 |  |  | YES | TUNQAP01MMS2P-VT5-TDP01-03 | 26
B2.1 | N |  | MCB 3P QAP01-FR1-BDP01-01 | TUN:QAP01 | MMS | MCB | 3P-FR1-BDP01-01 | QAP01_RTU | [9 empty] | &3P-FR1-BDP01-01 | TUN_QAP01_MMS_3P-FR1-BDP01-01 |  |  | YES | TUNQAP01MMS3P-FR1-BDP01-01 | 26
B2.1 | N |  | MCB 2P QAP01-FR1-BDP01-01 | TUN:QAP01 | MMS | MCB | 2P-FR1-BDP01-01 | QAP01_RTU | [9 empty] | &2P-FR1-BDP01-01 | TUN_QAP01_MMS_2P-FR1-BDP01-01 |  |  | YES | TUNQAP01MMS2P-FR1-BDP01-01 | 26
B2.1 | N |  | MCB 3P QAP01-FR1-BDP01-02 | TUN:QAP01 | MMS | MCB | 3P-FR1-BDP01-02 | QAP01_RTU | [9 empty] | &3P-FR1-BDP01-02 | TUN_QAP01_MMS_3P-FR1-BDP01-02 |  |  | YES | TUNQAP01MMS3P-FR1-BDP01-02 | 26
B2.1 | N |  | MCB 2P QAP01-FR1-BDP01-02 | TUN:QAP01 | MMS | MCB | 2P-FR1-BDP01-02 | QAP01_RTU | [9 empty] | &2P-FR1-BDP01-02 | TUN_QAP01_MMS_2P-FR1-BDP01-02 |  |  | YES | TUNQAP01MMS2P-FR1-BDP01-02 | 26
B2.1 | N |  | MCB QAP01-MSFD-CON-63 | TUN:QAP01 | MMS | MCB | MSFD-CON-63 | QAP01_RTU | [9 empty] | &MSFD-CON-63 | TUN_QAP01_MMS_MSFD-CON-63 |  |  | YES | TUNQAP01MMSMSFD-CON-63 | 22
B2.1 | N |  | MCB QAP01-MSFD-CON-59 | TUN:QAP01 | MMS | MCB | MSFD-CON-59 | QAP01_RTU | [9 empty] | &MSFD-CON-59 | TUN_QAP01_MMS_MSFD-CON-59 |  |  | YES | TUNQAP01MMSMSFD-CON-59 | 22
B2.1 | N |  | MCB QAP01-MSFD-CON-67 | TUN:QAP01 | MMS | MCB | MSFD-CON-67 | QAP01_RTU | [9 empty] | &MSFD-CON-67 | TUN_QAP01_MMS_MSFD-CON-67 |  |  | YES | TUNQAP01MMSMSFD-CON-67 | 22
B1.8 | Y |  |  | QEC-01
B1.8 | Y |  |  | LOCAL CONTROL PANEL (LCP) [STATION HMI]
B2.1 | N |  | Local control panel | TUN:QEC01 | SCR | LCP | LCP01 | QEC01_RTU | [9 empty] | &LCP01 | TUN_QEC01_SCR_LCP01 |  |  | YES | TUNQEC01SCRLCP01 | 16
B1.8 | Y |  |  | FIRE MANUAL OVERRIDE PANEL (FMOP)
B2.1 | N |  | Fire control panel | TUN:QEC01 | SCR | FMOP | FMOP01 | QEC01_RTU | [9 empty] | &FMOP01 | TUN_QEC01_SCR_FMOP01 |  |  | YES | TUNQEC01SCRFMOP01 | 17
B1.8 | Y |  |  | Station PLC (SPLC)
B2.1 | N |  | Station PLC | TUN:QEC01 | TEL | SPLC | PLC01 | QEC01_RTU | [9 empty] | &PLC01 | TUN_QEC01_TEL_PLC01 |  |  | YES | TUNQEC01TELPLC01 | 16
B1.8 | Y |  |  | Switch (SWI)
B2.1 | N |  | Switch | TUN:QEC01 | TEL | SWI | SWI01 | QEC01_RTU | [9 empty] | &SWI01 | TUN_QEC01_TEL_SWI01 |  |  | YES | TUNQEC01TELSWI01 | 16
B1.8 | Y |  |  | PRESSURIZATION FAN (PFA)
B2.1 | N |  | Pressurization fan Lobby 1 | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | QEC01_RTU | [9 empty] | &PLA-01 | TUN_QEC01_SS01_PFA_PLA-01 |  |  | YES | TUNQEC01SS01PFAPLA-01 | 21
B2.1 | N |  | Pressurization fan Escape Stair 1 | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | QEC01_RTU | [9 empty] | &GRD-01 | TUN_QEC01_SS01_PFA_GRD-01 |  |  | YES | TUNQEC01SS01PFAGRD-01 | 21
B2.1 | N |  | Pressurization fan Lobby 2 | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | QEC01_RTU | [9 empty] | &PLA-02 | TUN_QEC01_NS01_PFA_PLA-02 |  |  | YES | TUNQEC01NS01PFAPLA-02 | 21
B2.1 | N |  | Pressurization fan Stair 4 | TUN:QEC01 | NS01:PFA | PFA | CON-04 | QEC01_RTU | [9 empty] | &CON-04 | TUN_QEC01_NS01_PFA_CON-04 |  |  | YES | TUNQEC01NS01PFACON-04 | 21
B2.1 | N |  | Pressurization fan Lobby 3 & Corridor 4 | TUN:QEC01 | NS01:PFA | PFA | CON-03 | QEC01_RTU | [9 empty] | &CON-03 | TUN_QEC01_NS01_PFA_CON-03 |  |  | YES | TUNQEC01NS01PFACON-03 | 21
B2.1 | N |  | Pressurization fan Escape Stair 3 | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | QEC01_RTU | [9 empty] | &GRD-03 | TUN_QEC01_NS01_PFA_GRD-03 |  |  | YES | TUNQEC01NS01PFAGRD-03 | 21
B1.8 | Y |  |  | SMOKE CURTAINS (SMC)
B2.1 | N |  | Smoke Curtains 1 | TUN:QEC01 | SMC | SMC | SMC01 | QEC01_RTU | [9 empty] | &SMC01 | TUN_QEC01_SMC_SMC01 |  |  | YES | TUNQEC01SMCSMC01 | 16
B2.1 | N |  | Smoke Curtains 2 | TUN:QEC01 | SMC | SMC | SMC02 | QEC01_RTU | [9 empty] | &SMC02 | TUN_QEC01_SMC_SMC02 |  |  | YES | TUNQEC01SMCSMC02 | 16
B2.1 | N |  | Smoke Curtains 3 | TUN:QEC01 | SMC | SMC | SMC03 | QEC01_RTU | [9 empty] | &SMC03 | TUN_QEC01_SMC_SMC03 |  |  | YES | TUNQEC01SMCSMC03 | 16
B2.1 | N |  | Smoke Curtains 4 | TUN:QEC01 | SMC | SMC | SMC04 | QEC01_RTU | [9 empty] | &SMC04 | TUN_QEC01_SMC_SMC04 |  |  | YES | TUNQEC01SMCSMC04 | 16
B2.1 | N |  | Smoke Curtains 5 | TUN:QEC01 | SMC | SMC | SMC05 | QEC01_RTU | [9 empty] | &SMC05 | TUN_QEC01_SMC_SMC05 |  |  | YES | TUNQEC01SMCSMC05 | 16
B2.1 | N |  | Smoke Curtains 6 | TUN:QEC01 | SMC | SMC | SMC06 | QEC01_RTU | [9 empty] | &SMC06 | TUN_QEC01_SMC_SMC06 |  |  | YES | TUNQEC01SMCSMC06 | 16
B2.1 | N |  | Smoke Curtains 7 | TUN:QEC01 | SMC | SMC | SMC07 | QEC01_RTU | [9 empty] | &SMC07 | TUN_QEC01_SMC_SMC07 |  |  | YES | TUNQEC01SMCSMC07 | 16
B2.1 | N |  | Smoke Curtains 8 | TUN:QEC01 | SMC | SMC | SMC08 | QEC01_RTU | [9 empty] | &SMC08 | TUN_QEC01_SMC_SMC08 |  |  | YES | TUNQEC01SMCSMC08 | 16
B2.1 | N |  | Smoke Curtains 9 | TUN:QEC01 | SMC | SMC | SMC09 | QEC01_RTU | [9 empty] | &SMC09 | TUN_QEC01_SMC_SMC09 |  |  | YES | TUNQEC01SMCSMC09 | 16
B2.1 | N |  | Smoke Curtains 10 | TUN:QEC01 | SMC | SMC | SMC10 | QEC01_RTU | [9 empty] | &SMC10 | TUN_QEC01_SMC_SMC10 |  |  | YES | TUNQEC01SMCSMC10 | 16
B1.8 | Y |  |  | STATION ENTRANCE DOOR (SED)
B2.1 | N |  | Station entrance door 1 | TUN:QEC01 | SED | SED | SED01 | QEC01_RTU | [9 empty] | &SED01 | TUN_QEC01_SED_SED01 |  |  | YES | TUNQEC01SEDSED01 | 16
B2.1 | N |  | Station entrance door 2 | TUN:QEC01 | SED | SED | SED02 | QEC01_RTU | [9 empty] | &SED02 | TUN_QEC01_SED_SED02 |  |  | YES | TUNQEC01SEDSED02 | 16
B2.1 | N |  | Station entrance door 3 | TUN:QEC01 | SED | SED | SED03 | QEC01_RTU | [9 empty] | &SED03 | TUN_QEC01_SED_SED03 |  |  | YES | TUNQEC01SEDSED03 | 16
B2.1 | N |  | Station entrance door 4 | TUN:QEC01 | SED | SED | SED04 | QEC01_RTU | [9 empty] | &SED04 | TUN_QEC01_SED_SED04 |  |  | YES | TUNQEC01SEDSED04 | 16
B1.8 | Y |  |  | Outdoor temperature sensor (OTS)
B2.1 | N |  | Outdoor temperature sensor 1 | TUN:QEC01 | OTS | OTS | OTS001 | QEC01_RTU | [9 empty] | &OTS001 | TUN_QEC01_OTS_OTS001 |  |  | YES | TUNQEC01OTSOTS001 | 17
B2.1 | N |  | Outdoor temperature sensor 2 | TUN:QEC01 | OTS | OTS | OTS002 | QEC01_RTU | [9 empty] | &OTS002 | TUN_QEC01_OTS_OTS002 |  |  | YES | TUNQEC01OTSOTS002 | 17
B1.8 | Y |  |  | Tunnel ventilation fan (TVF)
B2.1 | N |  | South ShaftTunnel ventilation fan 1 | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | QEC01_RTU | [9 empty] | &VT1-TVF01 | TUN_QEC01_SS01_TVF_VT1-TVF01 |  |  | YES | TUNQEC01SS01TVFVT1-TVF01 | 24
B2.1 | N |  | South ShaftTunnel ventilation fan 2 | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | QEC01_RTU | [9 empty] | &VT2-TVF01 | TUN_QEC01_SS01_TVF_VT2-TVF01 |  |  | YES | TUNQEC01SS01TVFVT2-TVF01 | 24
B2.1 | N |  | North ShaftTunnel ventilation fan 3 | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | QEC01_RTU | [9 empty] | &VT3-TVF01 | TUN_QEC01_NS01_TVF_VT3-TVF01 |  |  | YES | TUNQEC01NS01TVFVT3-TVF01 | 24
B2.1 | N |  | NorthShaftTunnel ventilation fan 4 | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | QEC01_RTU | [9 empty] | &VT4-TVF01 | TUN_QEC01_NS01_TVF_VT4-TVF01 |  |  | YES | TUNQEC01NS01TVFVT4-TVF01 | 24
B1.8 | Y |  |  | Tunnel temperature & humidity sensor (TTS)
B2.1 | N |  | Tunnel to MAR-04 temperature sensor 1 | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | QEC01_RTU | [9 empty] | &TS101871 | TUN_QEC01_SS01_SENSOR_TS101871 |  |  | YES | TUNQEC01SS01SENSORTS101871 | 26
B2.1 | N |  | Tunnel to MAR-04 temperature sensor 2 | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | QEC01_RTU | [9 empty] | &TS101984 | TUN_QEC01_SS01_SENSOR_TS101984 |  |  | YES | TUNQEC01SS01SENSORTS101984 | 26
B2.1 | N |  | Tunnel to QEC-1A Niche temperature sensor 1 | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | QEC01_RTU | [9 empty] | &TS102441 | TUN_QEC01_NS01_SENSOR_TS102441 |  |  | YES | TUNQEC01NS01SENSORTS102441 | 26
B2.1 | N |  | Tunnel to QEC-1A Niche temperature sensor 2 | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | QEC01_RTU | [9 empty] | &TS102499 | TUN_QEC01_NS01_SENSOR_TS102499 |  |  | YES | TUNQEC01NS01SENSORTS102499 | 26
B2.1 | N |  | Tunnel to QEC-1B Niche temperature sensor 1 | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | QEC01_RTU | [9 empty] | &TS102261 | TUN_QEC01_NS01_SENSOR_TS102261 |  |  | YES | TUNQEC01NS01SENSORTS102261 | 26
B2.1 | N |  | Tunnel to QEC-1B Niche temperature sensor 2 | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | QEC01_RTU | [9 empty] | &TS100023 | TUN_QEC01_NS01_SENSOR_TS100023 |  |  | YES | TUNQEC01NS01SENSORTS100023 | 26
B2.1 | N |  | Tunnel to QEC-1B Niche temperature sensor 3 | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | QEC01_RTU | [9 empty] | &TS100062 | TUN_QEC01_NS01_SENSOR_TS100062 |  |  | YES | TUNQEC01NS01SENSORTS100062 | 26
B2.1 | N |  | Tunnel to QEC-1B Niche temperature sensor 4 | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | QEC01_RTU | [9 empty] | &TS100108 | TUN_QEC01_NS01_SENSOR_TS100108 |  |  | YES | TUNQEC01NS01SENSORTS100108 | 26
B2.1 | N |  | Tunnel to QEC-1B Niche temperature sensor 5 | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | QEC01_RTU | [9 empty] | &TS100230 | TUN_QEC01_NS01_SENSOR_TS100230 |  |  | YES | TUNQEC01NS01SENSORTS100230 | 26
B2.1 | N |  | Tunnel to QEC-1B Niche temperature sensor 6 | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | QEC01_RTU | [9 empty] | &TS100335 | TUN_QEC01_NS01_SENSOR_TS100335 |  |  | YES | TUNQEC01NS01SENSORTS100335 | 26
B1.8 | Y |  |  | Air velocity sensor (VS)
B2.1 | N |  | Tunnel to MAR-04 Air velocity sensor | TUN:QEC01 | SS01:SENSOR | VS | VS101909 | QEC01_RTU | [9 empty] | &VS101909 | TUN_QEC01_SS01_SENSOR_VS101909 |  |  | YES | TUNQEC01SS01SENSORVS101909 | 26
B2.1 | N |  | Tunnel to QEC-1A Niche Air velocity sensor 1 | TUN:QEC01 | NS01:SENSOR | VS | VS102357 | QEC01_RTU | [9 empty] | &VS102357 | TUN_QEC01_NS01_SENSOR_VS102357 |  |  | YES | TUNQEC01NS01SENSORVS102357 | 26
B2.1 | N |  | Tunnel to QEC-1A Niche Air velocity sensor 2 | TUN:QEC01 | NS01:SENSOR | VS | VS102467 | QEC01_RTU | [9 empty] | &VS102467 | TUN_QEC01_NS01_SENSOR_VS102467 |  |  | YES | TUNQEC01NS01SENSORVS102467 | 26
B2.1 | N |  | Tunnel to QEC-1B Niche Air velocity sensor 1 | TUN:QEC01 | NS01:SENSOR | VS | VS102276 | QEC01_RTU | [9 empty] | &VS102276 | TUN_QEC01_NS01_SENSOR_VS102276 |  |  | YES | TUNQEC01NS01SENSORVS102276 | 26
B2.1 | N |  | Tunnel to QEC-1B Niche Air velocity sensor 2 | TUN:QEC01 | NS01:SENSOR | VS | VS100080 | QEC01_RTU | [9 empty] | &VS100080 | TUN_QEC01_NS01_SENSOR_VS100080 |  |  | YES | TUNQEC01NS01SENSORVS100080 | 26
B2.1 | N |  | Tunnel to QEC-1B Niche Air velocity sensor 3 | TUN:QEC01 | NS01:SENSOR | VS | VS100285 | QEC01_RTU | [9 empty] | &VS100285 | TUN_QEC01_NS01_SENSOR_VS100285 |  |  | YES | TUNQEC01NS01SENSORVS100285 | 26
B1.8 | Y |  |  | TVS Damper : Tunnel damper (TDP)
B2.1 | N |  | South Shaft Tunnel damper 1 | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | QEC01_RTU | [9 empty] | &VT5-TDP01 | TUN_QEC01_SS01_DAMPER_VT5-TDP01 |  |  | YES | TUNQEC01SS01DAMPERVT5-TDP01 | 27
B2.1 | N |  | North Shaft Tunnel damper 2 | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | QEC01_RTU | [9 empty] | &VT6-TDP01 | TUN_QEC01_NS01_DAMPER_VT6-TDP01 |  |  | YES | TUNQEC01NS01DAMPERVT6-TDP01 | 27
B1.8 | Y |  |  | TVS Damper : Isolation damper (IDP)
B2.1 | N |  | Isolation damper 1 | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | QEC01_RTU | [9 empty] | &VT1-IDP01 | TUN_QEC01_SS01_DAMPER_VT1-IDP01 |  |  | YES | TUNQEC01SS01DAMPERVT1-IDP01 | 27
B2.1 | N |  | Isolation damper 2 | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | QEC01_RTU | [9 empty] | &VT2-IDP01 | TUN_QEC01_SS01_DAMPER_VT2-IDP01 |  |  | YES | TUNQEC01SS01DAMPERVT2-IDP01 | 27
B2.1 | N |  | Isolation damper 3 | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | QEC01_RTU | [9 empty] | &VT3-IDP01 | TUN_QEC01_NS01_DAMPER_VT3-IDP01 |  |  | YES | TUNQEC01NS01DAMPERVT3-IDP01 | 27
B2.1 | N |  | Isolation damper 4 | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | QEC01_RTU | [9 empty] | &VT4-IDP01 | TUN_QEC01_NS01_DAMPER_VT4-IDP01 |  |  | YES | TUNQEC01NS01DAMPERVT4-IDP01 | 27
B1.8 | Y |  |  | TVS Damper : Bypass damper (BDP)
B2.1 | N |  | South Shaft Bypass damper 1 | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | QEC01_RTU | [9 empty] | &FR1-BDP01 | TUN_QEC01_SS01_DAMPER_FR1-BDP01 |  |  | YES | TUNQEC01SS01DAMPERFR1-BDP01 | 27
B2.1 | N |  | North Shaft Bypass damper 2 | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | QEC01_RTU | [9 empty] | &FR2-BDP01 | TUN_QEC01_NS01_DAMPER_FR2-BDP01 |  |  | YES | TUNQEC01NS01DAMPERFR2-BDP01 | 27
B1.8 | Y |  |  | MEP Damper : Tunnel Cooling damper (TCDP)
B2.1 | N |  | South Shaft Tunnel Cooling damper 1 | TUN:QEC01 | SS01:DAMPER | MSFD | CON-95 | QEC01_RTU | [9 empty] | &CON-95 | TUN_QEC01_SS01_DAMPER_CON-95 |  |  | YES | TUNQEC01SS01DAMPERCON-95 | 24
B2.1 | N |  | North Shaft Tunnel Cooling damper 2 | TUN:QEC01 | NS01:DAMPER | MSFD | CON-94 | QEC01_RTU | [9 empty] | &CON-94 | TUN_QEC01_NS01_DAMPER_CON-94 |  |  | YES | TUNQEC01NS01DAMPERCON-94 | 24
B1.8 | Y |  |  | MEP damper : Station to exhaust duct Damper (SEDD)
B2.1 | N |  | South Shaft Station to exhaust duct damper 1 | TUN:QEC01 | SS01:DAMPER | MSFD | CON-51 | QEC01_RTU | [9 empty] | &CON-51 | TUN_QEC01_SS01_DAMPER_CON-51 |  |  | YES | TUNQEC01SS01DAMPERCON-51 | 24
B2.1 | N |  | South Shaft Station to exhaust duct damper 2 | TUN:QEC01 | SS01:DAMPER | MSFD | CON-49 | QEC01_RTU | [9 empty] | &CON-49 | TUN_QEC01_SS01_DAMPER_CON-49 |  |  | YES | TUNQEC01SS01DAMPERCON-49 | 24
B2.1 | N |  | North Shaft Station to exhaust duct damper 3 | TUN:QEC01 | NS01:DAMPER | MSFD | CON-34 | QEC01_RTU | [9 empty] | &CON-34 | TUN_QEC01_NS01_DAMPER_CON-34 |  |  | YES | TUNQEC01NS01DAMPERCON-34 | 24
B2.1 | N |  | North Shaft Station to exhaust duct damper 4 | TUN:QEC01 | NS01:DAMPER | MSFD | CON-53 | QEC01_RTU | [9 empty] | &CON-53 | TUN_QEC01_NS01_DAMPER_CON-53 |  |  | YES | TUNQEC01NS01DAMPERCON-53 | 24
B1.8 | Y |  |  | MEP damper : Station Cooling damper (SCD)
B2.1 | N |  | South Shaft Station Cooling damper 1 | TUN:QEC01 | SS01:DAMPER | MSFD | CON-52 | QEC01_RTU | [9 empty] | &CON-52 | TUN_QEC01_SS01_DAMPER_CON-52 |  |  | YES | TUNQEC01SS01DAMPERCON-52 | 24
B2.1 | N |  | South Shaft Station Cooling damper 2 | TUN:QEC01 | SS01:DAMPER | MSFD | CON-50 | QEC01_RTU | [9 empty] | &CON-50 | TUN_QEC01_SS01_DAMPER_CON-50 |  |  | YES | TUNQEC01SS01DAMPERCON-50 | 24
B2.1 | N |  | North Shaft Station Cooling damper 3 | TUN:QEC01 | NS01:DAMPER | MSFD | CON-88 | QEC01_RTU | [9 empty] | &CON-88 | TUN_QEC01_NS01_DAMPER_CON-88 |  |  | YES | TUNQEC01NS01DAMPERCON-88 | 24
B2.1 | N |  | North Shaft Station Cooling damper 4 | TUN:QEC01 | NS01:DAMPER | MSFD | CON-58 | QEC01_RTU | [9 empty] | &CON-58 | TUN_QEC01_NS01_DAMPER_CON-58 |  |  | YES | TUNQEC01NS01DAMPERCON-58 | 24
B1.8 | Y |  |  | Tunnel AIR HANDLING UNIT
B2.1 | N |  | South ShaftTunnel Air Handling Unit 1 (AHU room 3) | TUN:QEC01 | SS01:AHU | AHU | CON-02 | QEC01_RTU | [9 empty] | &CON-02 | TUN_QEC01_SS01_AHU_CON-02 |  |  | YES | TUNQEC01SS01AHUCON-02 | 21
B2.1 | N |  | North ShaftTunnel Air Handling Unit 2 (AHU room 1) | TUN:QEC01 | NS01:AHU | AHU | PLA-02 | QEC01_RTU | [9 empty] | &PLA-02 | TUN_QEC01_NS01_AHU_PLA-02 |  |  | YES | TUNQEC01NS01AHUPLA-02 | 21
B1.8 | Y |  |  | JET FANS equipment
B2.1 | N |  | QEC01 Jet Fans PLC | TUN:QEC01 | SCR | SPLC | JETPLC01 | QEC01_RTU | [9 empty] | &JETPLC01 | TUN_QEC01_SCR_JETPLC01 |  |  | YES | TUNQEC01SCRJETPLC01 | 19
B1.8 | Y |  |  | Jet Fan Niche QEC-1A
B2.1 | N |  | Jet Fan 100132 in tunnel between QEC-01 and EC1-0A (QEC-1B) | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | QEC01_RTU | [9 empty] | &QEC1B-JET100132 | TUN_QEC01_QEC1B_JET_QEC1B-JET100132 |  |  | YES | TUNQEC01QEC1BJETQEC1B-JET100132 | 31
B2.1 | N |  | Jet Fan 100133 in tunnel between QEC-01 and EC1-0A (QEC-1B) | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | QEC01_RTU | [9 empty] | &QEC1B-JET100133 | TUN_QEC01_QEC1B_JET_QEC1B-JET100133 |  |  | YES | TUNQEC01QEC1BJETQEC1B-JET100133 | 31
B2.1 | N |  | Jet Fan 100134 in tunnel between QEC-01 and EC1-0A (QEC-1B) | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | QEC01_RTU | [9 empty] | &QEC1B-JET100134 | TUN_QEC01_QEC1B_JET_QEC1B-JET100134 |  |  | YES | TUNQEC01QEC1BJETQEC1B-JET100134 | 31
B1.8 | Y |  |  | Jet Fan Niche QEC-1B
B2.1 | N |  | Jet Fan 102392 in tunnel between QEC-01 and QEC-02 (QEC-1A) | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | QEC01_RTU | [9 empty] | &QEC1A-JET102392 | TUN_QEC01_QEC1A_JET_QEC1A-JET102392 |  |  | YES | TUNQEC01QEC1AJETQEC1A-JET102392 | 31
B2.1 | N |  | Jet Fan 102393 in tunnel between QEC-01 and QEC-02 (QEC-1A) | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | QEC01_RTU | [9 empty] | &QEC1A-JET102393 | TUN_QEC01_QEC1A_JET_QEC1A-JET102393 |  |  | YES | TUNQEC01QEC1AJETQEC1A-JET102393 | 31
B2.1 | N |  | Jet Fan 102394 in tunnel between QEC-01 and QEC-02 (QEC-1A) | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | QEC01_RTU | [9 empty] | &QEC1A-JET102394 | TUN_QEC01_QEC1A_JET_QEC1A-JET102394 |  |  | YES | TUNQEC01QEC1AJETQEC1A-JET102394 | 31
B1.8 | Y |  |  | MMS Equipment
B2.1 | N |  | Station PLC (MMS) | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | QEC01_RTU | [9 empty] | &SPLC01 | TUN_QEC01_MMS_SPLC01 |  |  | YES | TUNQEC01MMSSPLC01 | 17
B1.8 | Y |  |  | Electrical Equipment
B2.1 | N |  | QEC01-LPS-MDB01 | TUN:QEC01 | MMS | MDB | LPS-MDB01 | QEC01_RTU | [9 empty] | &LPS-MDB01 | TUN_QEC01_MMS_LPS-MDB01 |  |  | YES | TUNQEC01MMSLPS-MDB01 | 20
B2.1 | N |  | QEC01-LPS-MDB02 | TUN:QEC01 | MMS | MDB | LPS-MDB02 | QEC01_RTU | [9 empty] | &LPS-MDB02 | TUN_QEC01_MMS_LPS-MDB02 |  |  | YES | TUNQEC01MMSLPS-MDB02 | 20
B1.8 | Y |  |  | Electrical Panel EL1 I/O 01
B2.1 | N |  | QEC01-EL1-IO01 | TUN:QEC01 | MMS | EL | EL1-IO01 | QEC01_RTU | [9 empty] | &EL1-IO01 | TUN_QEC01_MMS_EL1-IO01 |  |  | YES | TUNQEC01MMSEL1-IO01 | 19
B2.1 | N |  | MCCB QEC01-EL1-UPS | TUN:QEC01 | MMS | MCCB | EL1-UPS | QEC01_RTU | [9 empty] | &EL1-UPS | TUN_QEC01_MMS_EL1-UPS |  |  | YES | TUNQEC01MMSEL1-UPS | 18
B2.1 | N |  | LBS QEC01-EL1-UPS | TUN:QEC01 | MMS | LBS | EL1-UPS | QEC01_RTU | [9 empty] | &EL1-UPS | TUN_QEC01_MMS_EL1-UPS |  |  | YES | TUNQEC01MMSEL1-UPS | 18
B2.1 | N |  | MCB UPS QEC01-EL1-VSD01 | TUN:QEC01 | MMS | MCB | UPS_EL1-VSD01 | QEC01_RTU | [9 empty] | &UPS-EL1-VSD01 | TUN_QEC01_MMS_UPS_EL1-VSD01 |  |  | YES | TUNQEC01MMSUPS_EL1-VSD01 | 24
B2.1 | N |  | MCB UPS QEC01-EL1-VSD02 | TUN:QEC01 | MMS | MCB | UPS_EL1-VSD02 | QEC01_RTU | [9 empty] | &UPS-EL1-VSD02 | TUN_QEC01_MMS_UPS_EL1-VSD02 |  |  | YES | TUNQEC01MMSUPS_EL1-VSD02 | 24
B2.1 | N |  | MCB 3P QEC01-VT3-IDP01 | TUN:QEC01 | MMS | MCB | 3P-VT3-IDP01 | QEC01_RTU | [9 empty] | &3P-VT3-IDP01 | TUN_QEC01_MMS_3P-VT3-IDP01 |  |  | YES | TUNQEC01MMS3P-VT3-IDP01 | 23
B2.1 | N |  | MCB 2P QEC01-VT3-IDP01 | TUN:QEC01 | MMS | MCB | 2P-VT3-IDP01 | QEC01_RTU | [9 empty] | &2P-VT3-IDP01 | TUN_QEC01_MMS_2P-VT3-IDP01 |  |  | YES | TUNQEC01MMS2P-VT3-IDP01 | 23
B2.1 | N |  | MCB 3P QEC01-VT4-IDP01 | TUN:QEC01 | MMS | MCB | 3P-VT4-IDP01 | QEC01_RTU | [9 empty] | &3P-VT4-IDP01 | TUN_QEC01_MMS_3P-VT4-IDP01 |  |  | YES | TUNQEC01MMS3P-VT4-IDP01 | 23
B2.1 | N |  | MCB 2P QEC01-VT4-IDP01 | TUN:QEC01 | MMS | MCB | 2P-VT4-IDP01 | QEC01_RTU | [9 empty] | &2P-VT4-IDP01 | TUN_QEC01_MMS_2P-VT4-IDP01 |  |  | YES | TUNQEC01MMS2P-VT4-IDP01 | 23
B2.1 | N |  | MCB 3P QEC01-VT6-TDP01-01 | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-01 | QEC01_RTU | [9 empty] | &3P-VT6-TDP01-01 | TUN_QEC01_MMS_3P-VT6-TDP01-01 |  |  | YES | TUNQEC01MMS3P-VT6-TDP01-01 | 26
B2.1 | N |  | MCB 2P QEC01-VT6-TDP01-01 | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-01 | QEC01_RTU | [9 empty] | &2P-VT6-TDP01-01 | TUN_QEC01_MMS_2P-VT6-TDP01-01 |  |  | YES | TUNQEC01MMS2P-VT6-TDP01-01 | 26
B2.1 | N |  | MCB 3P QEC01-VT6-TDP01-02 | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-02 | QEC01_RTU | [9 empty] | &3P-VT6-TDP01-02 | TUN_QEC01_MMS_3P-VT6-TDP01-02 |  |  | YES | TUNQEC01MMS3P-VT6-TDP01-02 | 26
B2.1 | N |  | MCB 2P QEC01-VT6-TDP01-02 | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-02 | QEC01_RTU | [9 empty] | &2P-VT6-TDP01-02 | TUN_QEC01_MMS_2P-VT6-TDP01-02 |  |  | YES | TUNQEC01MMS2P-VT6-TDP01-02 | 26
B2.1 | N |  | MCB 3P QEC01-VT6-TDP01-03 | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-03 | QEC01_RTU | [9 empty] | &3P-VT6-TDP01-03 | TUN_QEC01_MMS_3P-VT6-TDP01-03 |  |  | YES | TUNQEC01MMS3P-VT6-TDP01-03 | 26
B2.1 | N |  | MCB 2P QEC01-VT6-TDP01-03 | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-03 | QEC01_RTU | [9 empty] | &2P-VT6-TDP01-03 | TUN_QEC01_MMS_2P-VT6-TDP01-03 |  |  | YES | TUNQEC01MMS2P-VT6-TDP01-03 | 26
B2.1 | N |  | MCB 3P QEC01-FR2-BDP01-01 | TUN:QEC01 | MMS | MCB | 3P--FR2-BDP01-01 | QEC01_RTU | [9 empty] | &3P--FR2-BDP01-01 | TUN_QEC01_MMS_3P--FR2-BDP01-01 |  |  | YES | TUNQEC01MMS3P--FR2-BDP01-01 | 27
B2.1 | N |  | MCB 2P QEC01-FR2-BDP01-01 | TUN:QEC01 | MMS | MCB | 2P--FR2-BDP01-01 | QEC01_RTU | [9 empty] | &2P--FR2-BDP01-01 | TUN_QEC01_MMS_2P--FR2-BDP01-01 |  |  | YES | TUNQEC01MMS2P--FR2-BDP01-01 | 27
B2.1 | N |  | MCB 3P QEC01-FR2-BDP01-02 | TUN:QEC01 | MMS | MCB | 3P--FR2-BDP01-02 | QEC01_RTU | [9 empty] | &3P--FR2-BDP01-02 | TUN_QEC01_MMS_3P--FR2-BDP01-02 |  |  | YES | TUNQEC01MMS3P--FR2-BDP01-02 | 27
B2.1 | N |  | MCB 2P QEC01-FR2-BDP01-02 | TUN:QEC01 | MMS | MCB | 2P--FR2-BDP01-02 | QEC01_RTU | [9 empty] | &2P--FR2-BDP01-02 | TUN_QEC01_MMS_2P--FR2-BDP01-02 |  |  | YES | TUNQEC01MMS2P--FR2-BDP01-02 | 27
B2.1 | N |  | MCB QEC01-MSFD-CON-94 | TUN:QEC01 | MMS | MCB | MSFD-CON-94 | QEC01_RTU | [9 empty] | &MSFD-CON-94 | TUN_QEC01_MMS_MSFD-CON-94 |  |  | YES | TUNQEC01MMSMSFD-CON-94 | 22
B2.1 | N |  | MCB QEC01-MSFD-CON-58 | TUN:QEC01 | MMS | MCB | MSFD-CON-58 | QEC01_RTU | [9 empty] | &MSFD-CON-58 | TUN_QEC01_MMS_MSFD-CON-58 |  |  | YES | TUNQEC01MMSMSFD-CON-58 | 22
B2.1 | N |  | MCB QEC01-MSFD-CON-88 | TUN:QEC01 | MMS | MCB | MSFD-CON-88 | QEC01_RTU | [9 empty] | &MSFD-CON-88 | TUN_QEC01_MMS_MSFD-CON-88 |  |  | YES | TUNQEC01MMSMSFD-CON-88 | 22
B1.8 | Y |  |  | Electrical Panel EL2 I/O 01
B2.1 | N |  | QEC01-EL2-IO01 | TUN:QEC01 | MMS | EL | EL2-IO01 | QEC01_RTU | [9 empty] | &EL2-IO01 | TUN_QEC01_MMS_EL2-IO01 |  |  | YES | TUNQEC01MMSEL2-IO01 | 19
B2.1 | N |  | MCCB QEC01-EL2-UPS | TUN:QEC01 | MMS | MCCB | EL2-UPS | QEC01_RTU | [9 empty] | &EL2-UPS | TUN_QEC01_MMS_EL2-UPS |  |  | YES | TUNQEC01MMSEL2-UPS | 18
B2.1 | N |  | LBS QEC01-EL2-UPS | TUN:QEC01 | MMS | LBS | EL2-UPS | QEC01_RTU | [9 empty] | &EL2-UPS | TUN_QEC01_MMS_EL2-UPS |  |  | YES | TUNQEC01MMSEL2-UPS | 18
B2.1 | N |  | MCB UPS QEC01-EL2-VSD01 | TUN:QEC01 | MMS | MCB | UPS_EL2-VSD01 | QEC01_RTU | [9 empty] | &UPS-EL2-VSD01 | TUN_QEC01_MMS_UPS_EL2-VSD01 |  |  | YES | TUNQEC01MMSUPS_EL2-VSD01 | 24
B2.1 | N |  | MCB UPS QEC01-EL2-VSD02 | TUN:QEC01 | MMS | MCB | UPS_EL2-VSD02 | QEC01_RTU | [9 empty] | &UPS-EL2-VSD02 | TUN_QEC01_MMS_UPS_EL2-VSD02 |  |  | YES | TUNQEC01MMSUPS_EL2-VSD02 | 24
B2.1 | N |  | MCB 3P QEC01-VT1-IDP01 | TUN:QEC01 | MMS | MCB | 3P-VT1-IDP01 | QEC01_RTU | [9 empty] | &3P-VT1-IDP01 | TUN_QEC01_MMS_3P-VT1-IDP01 |  |  | YES | TUNQEC01MMS3P-VT1-IDP01 | 23
B2.1 | N |  | MCB 2P QEC01-VT1-IDP01 | TUN:QEC01 | MMS | MCB | 2P-VT1-IDP01 | QEC01_RTU | [9 empty] | &2P-VT1-IDP01 | TUN_QEC01_MMS_2P-VT1-IDP01 |  |  | YES | TUNQEC01MMS2P-VT1-IDP01 | 23
B2.1 | N |  | MCB 3P QEC01-VT2-IDP01 | TUN:QEC01 | MMS | MCB | 3P-VT2-IDP01 | QEC01_RTU | [9 empty] | &3P-VT2-IDP01 | TUN_QEC01_MMS_3P-VT2-IDP01 |  |  | YES | TUNQEC01MMS3P-VT2-IDP01 | 23
B2.1 | N |  | MCB 2P QEC01-VT2-IDP01 | TUN:QEC01 | MMS | MCB | 2P-VT2-IDP01 | QEC01_RTU | [9 empty] | &2P-VT2-IDP01 | TUN_QEC01_MMS_2P-VT2-IDP01 |  |  | YES | TUNQEC01MMS2P-VT2-IDP01 | 23
B2.1 | N |  | MCB 3P QEC01-VT5-TDP01-01 | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-01 | QEC01_RTU | [9 empty] | &3P-VT5-TDP01-01 | TUN_QEC01_MMS_3P-VT5-TDP01-01 |  |  | YES | TUNQEC01MMS3P-VT5-TDP01-01 | 26
B2.1 | N |  | MCB 2P QEC01-VT5-TDP01-01 | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-01 | QEC01_RTU | [9 empty] | &2P-VT5-TDP01-01 | TUN_QEC01_MMS_2P-VT5-TDP01-01 |  |  | YES | TUNQEC01MMS2P-VT5-TDP01-01 | 26
B2.1 | N |  | MCB 3P QEC01-VT5-TDP01-02 | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-02 | QEC01_RTU | [9 empty] | &3P-VT5-TDP01-02 | TUN_QEC01_MMS_3P-VT5-TDP01-02 |  |  | YES | TUNQEC01MMS3P-VT5-TDP01-02 | 26
B2.1 | N |  | MCB 2P QEC01-VT5-TDP01-02 | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-02 | QEC01_RTU | [9 empty] | &2P-VT5-TDP01-02 | TUN_QEC01_MMS_2P-VT5-TDP01-02 |  |  | YES | TUNQEC01MMS2P-VT5-TDP01-02 | 26
B2.1 | N |  | MCB 3P QEC01-VT5-TDP01-03 | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-03 | QEC01_RTU | [9 empty] | &3P-VT5-TDP01-03 | TUN_QEC01_MMS_3P-VT5-TDP01-03 |  |  | YES | TUNQEC01MMS3P-VT5-TDP01-03 | 26
B2.1 | N |  | MCB 2P QEC01-VT5-TDP01-03 | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-03 | QEC01_RTU | [9 empty] | &2P-VT5-TDP01-03 | TUN_QEC01_MMS_2P-VT5-TDP01-03 |  |  | YES | TUNQEC01MMS2P-VT5-TDP01-03 | 26
B2.1 | N |  | MCB 3P QEC01-FR1-BDP01-01 | TUN:QEC01 | MMS | MCB | 3P-FR1-BDP01-01 | QEC01_RTU | [9 empty] | &3P-FR1-BDP01-01 | TUN_QEC01_MMS_3P-FR1-BDP01-01 |  |  | YES | TUNQEC01MMS3P-FR1-BDP01-01 | 26
B2.1 | N |  | MCB 2P QEC01-FR1-BDP01-01 | TUN:QEC01 | MMS | MCB | 2P-FR1-BDP01-01 | QEC01_RTU | [9 empty] | &2P-FR1-BDP01-01 | TUN_QEC01_MMS_2P-FR1-BDP01-01 |  |  | YES | TUNQEC01MMS2P-FR1-BDP01-01 | 26
B2.1 | N |  | MCB 3P QEC01-FR1-BDP01-02 | TUN:QEC01 | MMS | MCB | 3P-FR1-BDP01-02 | QEC01_RTU | [9 empty] | &3P-FR1-BDP01-02 | TUN_QEC01_MMS_3P-FR1-BDP01-02 |  |  | YES | TUNQEC01MMS3P-FR1-BDP01-02 | 26
B2.1 | N |  | MCB 2P QEC01-FR1-BDP01-02 | TUN:QEC01 | MMS | MCB | 2P-FR1-BDP01-02 | QEC01_RTU | [9 empty] | &2P-FR1-BDP01-02 | TUN_QEC01_MMS_2P-FR1-BDP01-02 |  |  | YES | TUNQEC01MMS2P-FR1-BDP01-02 | 26
B2.1 | N |  | MCB QEC01-MSFD-CON-50 | TUN:QEC01 | MMS | MCB | MSFD-CON-50 | QEC01_RTU | [9 empty] | &MSFD-CON-50 | TUN_QEC01_MMS_MSFD-CON-50 |  |  | YES | TUNQEC01MMSMSFD-CON-50 | 22
B2.1 | N |  | MCB QEC01-MSFD-CON-52 | TUN:QEC01 | MMS | MCB | MSFD-CON-52 | QEC01_RTU | [9 empty] | &MSFD-CON-52 | TUN_QEC01_MMS_MSFD-CON-52 |  |  | YES | TUNQEC01MMSMSFD-CON-52 | 22
B2.1 | N |  | MCB QEC01-MSFD-CON-95 | TUN:QEC01 | MMS | MCB | MSFD-CON-95 | QEC01_RTU | [9 empty] | &MSFD-CON-95 | TUN_QEC01_MMS_MSFD-CON-95 |  |  | YES | TUNQEC01MMSMSFD-CON-95 | 22

## 3-Class Mapping
Class name | Prototype | Aggregate name | Object type | isAComment
MPLC | LusailHK:LusTvsMplc

## 4-External Variables
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
MPLC | dciMPLC-Point1:dac | DEIV | Point1 | Zone status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point2:dac | DEIV | Point2 | Operational status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point3:dac | DEIV | Point3 | Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point4:dac | DEIV | Point4 | Operational status Normal/Alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point5:dac | DEIV | Point5 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point6:dac | DEIV | Point6 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point7:dac | DEIV | Point7 | Operational status Normal/Alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point8:dac | DEIV | Point8 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point9:dac | DEIV | Point9 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point10:dac | DEIV | Point10 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point11:dac | DEIV | Point11 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point12:dac | DEIV | Point12 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point13:dac | DEIV | Point13 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point14:dac | DEIV | Point14 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point15:dac | DEIV | Point15 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point16:dac | DEIV | Point16 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point17:dac | DEIV | Point17 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point18:dac | DEIV | Point18 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point19:dac | DEIV | Point19 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point20:dac | DEIV | Point20 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point21:dac | DEIV | Point21 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point22:dac | DEIV | Point22 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point23:dac | DEIV | Point23 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point24:dac | DEIV | Point24 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point25:dac | DEIV | Point25 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N

## 4-External Variables - SIL0
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
MPLC | dciMPLC-Point1:dac | DEIV | Point1 | Zone status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point2:dac | DEIV | Point2 | Operational status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point3:dac | DEIV | Point3 | Status | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point4:dac | DEIV | Point4 | Operational status Normal/Alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point5:dac | DEIV | Point5 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point6:dac | DEIV | Point6 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point7:dac | DEIV | Point7 | Operational status Normal/Alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point8:dac | DEIV | Point8 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point9:dac | DEIV | Point9 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point10:dac | DEIV | Point10 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point11:dac | DEIV | Point11 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point12:dac | DEIV | Point12 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point13:dac | DEIV | Point13 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point14:dac | DEIV | Point14 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point15:dac | DEIV | Point15 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point16:dac | DEIV | Point16 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point17:dac | DEIV | Point17 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point18:dac | DEIV | Point18 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point19:dac | DEIV | Point19 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point20:dac | DEIV | Point20 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point21:dac | DEIV | Point21 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point22:dac | DEIV | Point22 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point23:dac | DEIV | Point23 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point24:dac | DEIV | Point24 | status Healthy/fault | $VOID | VEE | 0 |  |  |  | 4 |  |  | N
MPLC | dciMPLC-Point25:dac | DEIV | Point25 | General alarm | $VOID | VEE | 0 |  |  |  | 4 |  |  | N

## 4-External Variables - SIL2MON
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment

## 4-External Variables - SIL2CON
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment

## 10-PLC Points
row_id | concentrator | location | sub_location | class_name | eqp_name | instance_id | attribute_code | sil_channel | operation_type | point_address | start_bit | nb_bits | Warning | Error | PRTU Name | SWC Name | Daccom Source File | Daccom Variable Type | FC Code / ASDU Type | Daccom Type Num | Protocol Address | Start Bit | Nb Bits | Daccom External Variable Name | field1 | field2 | field3 | field4 | field5 | External Var Comment
1 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B OFFLINE
2 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC RUNNING.
3 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B : PRIMARY MODE ACTIVE
4 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: SECONDARY MODE ACTIVE (STANDBY)
5 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #APPLICATIONS ARE DIFFERENT ON THE TWO PLCS
6 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: POWER SUPPLY FAULT
7 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CPU MODULE FAULT
8 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CRP MODULE FAULT
9 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (SCADA COMMUNICATION)
10 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
11 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH SCADA
12 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH STATION PEA-01 PLC
13 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH STATION MAR-01 PLC
14 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH STATION MAR-02 PLC
15 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH STATION MAR-03 PLC
16 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH STATION MAR-04 PLC
17 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH STATION QEC-01 PLC
18 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH STATION EC1-01 PLC
19 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH STATION QAP-01 PLC
20 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH STATION FXH-02 PLC
21 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH SHAFT PEA-0A PLC
22 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH SHAFT PEA-1B PLC
23 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH SHAFT MAR-0A PLC
24 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH SHAFT EC1-0A PLC
25 | BOCC_RTU | TUN:BOCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH SHAFT QAP-1B PLC
26 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY DISCONNECTING SWITCH - OPEN
27 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY VOLTAGE PRESENCE
28 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER OPEN
29 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER FAULT
30 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN
31 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT
32 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKER OPEN
33 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKER FAULT
34 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER OPEN
35 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER FAULT
36 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN
37 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT
38 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 ABSENCE OF VOLTAGE
39 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN
40 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT
41 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 ABSENCE OF VOLTAGE
42 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH 1 CIRCUIT BREAKER OPEN
43 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH 1 CIRCUIT BREAKER FAULT
44 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH 2 CIRCUIT BREAKER OPEN
45 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH 2 CIRCUIT BREAKER FAULT
46 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A CIRCUIT BREAKER OPEN
47 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A CIRCUIT BREAKER FAULT
48 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC B CIRCUIT BREAKER OPEN
49 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC B CIRCUIT BREAKER FAULT
50 | BOCC_RTU | TUN:BOCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SURGE ARRESTER TRIGGERED
51 | BOCC_RTU | TUN:BOCC | WTDG | WTDG | WTDG01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | BOCC-SIL2_Monitoring |  | BOCC_RTU_S2M_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNBOCCWTDGWTDG01TODO | 4 |  |  | 0 | $ComStatus , , | #Watchdog Counter for each TVS Master PLC
52 | BOCC_RTU | TUN:BOCC | SWI | SWI | SWI01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCSWISWI01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH FAULT
53 | BOCC_RTU | TUN:BOCC | SWI | SWI | SWI02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | BOCC-SIL0 |  | BOCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNBOCCSWISWI02TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH FAULT
54 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B OFFLINE
55 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC RUNNING.
56 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B : PRIMARY MODE ACTIVE
57 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: SECONDARY MODE ACTIVE (STANDBY)
58 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #APPLICATIONS ARE DIFFERENT ON THE TWO PLCS
59 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: POWER SUPPLY FAULT
60 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CPU MODULE FAULT
61 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CRP MODULE FAULT
62 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (SCADA COMMUNICATION)
63 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
64 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH SCADA
65 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH STATION PEA-01 PLC
66 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH STATION MAR-01 PLC
67 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH STATION MAR-02 PLC
68 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH STATION MAR-03 PLC
69 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH STATION MAR-04 PLC
70 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH STATION QEC-01 PLC
71 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH STATION EC1-01 PLC
72 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH STATION QAP-01 PLC
73 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH STATION FXH-02 PLC
74 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH SHAFT PEA-0A PLC
75 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH SHAFT PEA-1B PLC
76 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH SHAFT MAR-0A PLC
77 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH SHAFT EC1-0A PLC
78 | OCC_RTU | TUN:OCC | MPLC | MPLC | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMPLCMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: COMMUNICATION FAULT WITH SHAFT QAP-1B PLC
79 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY DISCONNECTING SWITCH - OPEN
80 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY VOLTAGE PRESENCE
81 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER OPEN
82 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER FAULT
83 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN
84 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT
85 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKER OPEN
86 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKER FAULT
87 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER OPEN
88 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER FAULT
89 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN
90 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT
91 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 ABSENCE OF VOLTAGE
92 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN
93 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT
94 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 ABSENCE OF VOLTAGE
95 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH 1 CIRCUIT BREAKER OPEN
96 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH 1 CIRCUIT BREAKER FAULT
97 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH 2 CIRCUIT BREAKER OPEN
98 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH 2 CIRCUIT BREAKER FAULT
99 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A CIRCUIT BREAKER OPEN
100 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A CIRCUIT BREAKER FAULT
101 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC B CIRCUIT BREAKER OPEN
102 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC B CIRCUIT BREAKER FAULT
103 | OCC_RTU | TUN:OCC | MMS | MPLCMMS | MPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMMSMPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SURGE ARRESTER TRIGGERED
104 | OCC_RTU | TUN:OCC | WTDG | WTDG | WTDG01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNOCCWTDGWTDG01TODO | 4 |  |  | 0 | $ComStatus , , | #Watchdog Counter for each TVS Master PLC
105 | OCC_RTU | TUN:OCC | SWI | SWI | SWI01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCSWISWI01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH FAULT
106 | OCC_RTU | TUN:OCC | SWI | SWI | SWI02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCSWISWI02TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH FAULT
107 | OCC_RTU | TUN:MUL | TEMP | MUL | MUL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MUL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMULTEMPMUL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TUNNEL TEMPERATURE ZONE 1
108 | OCC_RTU | TUN:MUL | TEMP | MUL | MUL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MUL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMULTEMPMUL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TUNNEL TEMPERATURE ZONE 2
109 | OCC_RTU | TUN:MUL | TEMP | MUL | MUL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MUL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMULTEMPMUL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TUNNEL TEMPERATURE ZONE 3
110 | OCC_RTU | TUN:MUL | TEMP | MUL | MUL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MUL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMULTEMPMUL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TUNNEL TEMPERATURE ZONE 4
111 | OCC_RTU | TUN:MUL | TEMP | MUL | MUL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MUL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMULTEMPMUL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TUNNEL TEMPERATURE ZONE 5
112 | OCC_RTU | TUN:MUL | TEMP | MUL | MUL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MUL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMULTEMPMUL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TUNNEL TEMPERATURE ZONE 6
113 | OCC_RTU | TUN:MUL | TEMP | MUL | MUL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MUL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMULTEMPMUL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TUNNEL TEMPERATURE ZONE 7
114 | OCC_RTU | TUN:MUL | TEMP | MUL | MUL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MUL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMULTEMPMUL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TUNNEL TEMPERATURE ZONE 8
115 | OCC_RTU | TUN:MUL | TEMP | MUL | MUL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MUL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMULTEMPMUL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TUNNEL TEMPERATURE ZONE 9
116 | OCC_RTU | TUN:MUL | TEMP | MUL | MUL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MUL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMULTEMPMUL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TUNNEL TEMPERATURE ZONE 10
117 | OCC_RTU | TUN:MUL | TEMP | MUL | MUL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MUL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMULTEMPMUL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TUNNEL TEMPERATURE ZONE 11
118 | OCC_RTU | TUN:MUL | TEMP | MUL | MUL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MUL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMULTEMPMUL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TUNNEL TEMPERATURE ZONE 12
119 | OCC_RTU | TUN:MUL | TEMP | MUL | MUL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MUL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMULTEMPMUL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TUNNEL TEMPERATURE ZONE 13
120 | OCC_RTU | TUN:MUL | TEMP | MUL | MUL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MUL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMULTEMPMUL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TUNNEL TEMPERATURE ZONE 14
121 | OCC_RTU | TUN:MUL | TEMP | MUL | MUL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MUL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMULTEMPMUL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TUNNEL TEMPERATURE ZONE 15
122 | OCC_RTU | TUN:MUL | TEMP | MUL | MUL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MUL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMULTEMPMUL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE OUTDOOR TEMPERATURE
123 | OCC_RTU | TUN:FXL | TEMP | FXL | FXL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | FXL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNFXLTEMPFXL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TUNNEL TEMPERATURE ZONE 16
124 | OCC_RTU | TUN:FXL | TEMP | FXL | FXL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | FXL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNFXLTEMPFXL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TUNNEL TEMPERATURE ZONE 17
125 | OCC_RTU | TUN:FXL | TEMP | FXL | FXL01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | FXL-SIL0 |  | OCC_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNFXLTEMPFXL01TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE OUTDOOR TEMPERATURE
126 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
127 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
128 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL0 |  | OCC_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
129 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
130 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
131 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
132 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
133 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
134 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
135 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
136 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
137 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
138 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
139 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
140 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
141 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
142 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
143 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
144 | OCC_RTU | TUN:OCC | MODES | VENTILATION | VENTILATION | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCMODESVENTILATIONTODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
145 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1011 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1011TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
146 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1011 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1011TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
147 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1011 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1011TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
148 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1011 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1011TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
149 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1011 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1011TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
150 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1011 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1011TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
151 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1012 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1012TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
152 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1012 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1012TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
153 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1012 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1012TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
154 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1012 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1012TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
155 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1012 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1012TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
156 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1012 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1012TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
157 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1021 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1021TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
158 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1021 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1021TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
159 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1021 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1021TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
160 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1021 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1021TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
161 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1021 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1021TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
162 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1021 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1021TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
163 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1022 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1022TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
164 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1022 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1022TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
165 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1022 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1022TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
166 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1022 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1022TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
167 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1022 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1022TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
168 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1022 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1022TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
169 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1031 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1031TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
170 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1031 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1031TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
171 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1031 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1031TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
172 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1031 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1031TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
173 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1031 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1031TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
174 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1031 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1031TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
175 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1032 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1032TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
176 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1032 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1032TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
177 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1032 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1032TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
178 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1032 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1032TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
179 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1032 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1032TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
180 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1032 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1032TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
181 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1041 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1041TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
182 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1041 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1041TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
183 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1041 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1041TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
184 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1041 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1041TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
185 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1041 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1041TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
186 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1041 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1041TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
187 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1042 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1042TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
188 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1042 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1042TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
189 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1042 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1042TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
190 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1042 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1042TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
191 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1042 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1042TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
192 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1042 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1042TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
193 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1051 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1051TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
194 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1051 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1051TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
195 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1051 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1051TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
196 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1051 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1051TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
197 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1051 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1051TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
198 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1051 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1051TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
199 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1052 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1052TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
200 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1052 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1052TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
201 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1052 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1052TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
202 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1052 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1052TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
203 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1052 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1052TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
204 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1052 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1052TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
205 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1061 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1061TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
206 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1061 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1061TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
207 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1061 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1061TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
208 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1061 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1061TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
209 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1061 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1061TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
210 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1061 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1061TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
211 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1062 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1062TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
212 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1062 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1062TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
213 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1062 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1062TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
214 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1062 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1062TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
215 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1062 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1062TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
216 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1062 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1062TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
217 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1071 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1071TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
218 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1071 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1071TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
219 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1071 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1071TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
220 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1071 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1071TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
221 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1071 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1071TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
222 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1071 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1071TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
223 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1072 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1072TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
224 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1072 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1072TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
225 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1072 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1072TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
226 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1072 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1072TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
227 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1072 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1072TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
228 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1072 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1072TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
229 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1081 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1081TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
230 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1081 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1081TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
231 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1081 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1081TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
232 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1081 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1081TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
233 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1081 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1081TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
234 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1081 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1081TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
235 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1082 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1082TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
236 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1082 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1082TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
237 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1082 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1082TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
238 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1082 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1082TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
239 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1082 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1082TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
240 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1082 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1082TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
241 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1091 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1091TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
242 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1091 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1091TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
243 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1091 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1091TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
244 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1091 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1091TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
245 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1091 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1091TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
246 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1091 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1091TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
247 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1092 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1092TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
248 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1092 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1092TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
249 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1092 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1092TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
250 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1092 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1092TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
251 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1092 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1092TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
252 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1092 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1092TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
253 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1101 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1101TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
254 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1101 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1101TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
255 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1101 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1101TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
256 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1101 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1101TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
257 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1101 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1101TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
258 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1101 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1101TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
259 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1102 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1102TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
260 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1102 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1102TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
261 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1102 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1102TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
262 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1102 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1102TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
263 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1102 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1102TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
264 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1102 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1102TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
265 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1111 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1111TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
266 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1111 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1111TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
267 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1111 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1111TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
268 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1111 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1111TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
269 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1111 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1111TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
270 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1111 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1111TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
271 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1112 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1112TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
272 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1112 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1112TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
273 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1112 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1112TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
274 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1112 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1112TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
275 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1112 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1112TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
276 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1112 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1112TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
277 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1121 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1121TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
278 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1121 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1121TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
279 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1121 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1121TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
280 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1121 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1121TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
281 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1121 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1121TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
282 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1121 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1121TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
283 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1122 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1122TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
284 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1122 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1122TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
285 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1122 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1122TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
286 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1122 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1122TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
287 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1122 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1122TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
288 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1122 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1122TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
289 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1131 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1131TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
290 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1131 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1131TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
291 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1131 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1131TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
292 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1131 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1131TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
293 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1131 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1131TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
294 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1131 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1131TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
295 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1132 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1132TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
296 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1132 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1132TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
297 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1132 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1132TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
298 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1132 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1132TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
299 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1132 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1132TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
300 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1132 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1132TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
301 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1141 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1141TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
302 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1141 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1141TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
303 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1141 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1141TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
304 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1141 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1141TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
305 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1141 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1141TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
306 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1141 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1141TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
307 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1142 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1142TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
308 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1142 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1142TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
309 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1142 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1142TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
310 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1142 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1142TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
311 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1142 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1142TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
312 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1142 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1142TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
313 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1151 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1151TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
314 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1151 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1151TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
315 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1151 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1151TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
316 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1151 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1151TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
317 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1151 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1151TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
318 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1151 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1151TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
319 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1152 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1152TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
320 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1152 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1152TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
321 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1152 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1152TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
322 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1152 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1152TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
323 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1152 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1152TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
324 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1152 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1152TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
325 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1161 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1161TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
326 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1161 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1161TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
327 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1161 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1161TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
328 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1161 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1161TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
329 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1161 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1161TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
330 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1161 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1161TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
331 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1162 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1162TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
332 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1162 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1162TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
333 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1162 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1162TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
334 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1162 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1162TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
335 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1162 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1162TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
336 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1162 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1162TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
337 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1171 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1171TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
338 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1171 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1171TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
339 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1171 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1171TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
340 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1171 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1171TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
341 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1171 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1171TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
342 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1171 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1171TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
343 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1172 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1172TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
344 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1172 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO1172TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
345 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1172 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1172TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
346 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1172 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1172TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
347 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1172 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO1172TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
348 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1172 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO1172TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
349 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2510 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO2510TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
350 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2510 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO2510TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
351 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2510 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO2510TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
352 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2510 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO2510TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
353 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2510 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO2510TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
354 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2510 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO2510TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
355 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2520 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO2520TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
356 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2520 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO2520TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
357 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2520 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO2520TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
358 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2520 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO2520TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
359 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2520 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO2520TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
360 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2520 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO2520TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
361 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2530 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO2530TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
362 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2530 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO2530TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
363 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2530 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO2530TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
364 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2530 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO2530TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
365 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2530 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO2530TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
366 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2530 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO2530TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
367 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2540 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO2540TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
368 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2540 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO2540TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
369 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2540 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO2540TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
370 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2540 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO2540TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
371 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2540 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO2540TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
372 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2540 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO2540TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
373 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2550 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO2550TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
374 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2550 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO2550TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
375 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2550 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO2550TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
376 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2550 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO2550TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
377 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2550 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO2550TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
378 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2550 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO2550TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
379 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2560 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO2560TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
380 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2560 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO2560TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
381 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2560 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO2560TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
382 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2560 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO2560TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
383 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2560 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO2560TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
384 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2560 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO2560TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
385 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2570 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO2570TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
386 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2570 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO2570TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
387 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2570 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO2570TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
388 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2570 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO2570TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
389 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2570 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO2570TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
390 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2570 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO2570TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
391 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2580 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO2580TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
392 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2580 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Monitoring |  | OCC_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNOCCEMERGENCYSCENARIO2580TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
393 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2580 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO2580TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
394 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2580 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO2580TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
395 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2580 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNOCCEMERGENCYSCENARIO2580TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
396 | OCC_RTU | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2580 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | OCC-SIL2_Control |  | OCC_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNOCCEMERGENCYSCENARIO2580TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
397 | MAR01_RTU | TUN:MAR01 | SCR | LCP | LCP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SCRLCP01TODO | 4 |  |  | 0 | $ComStatus , , | #COMMUNICATION FAULT WITH PLC
398 | MAR01_RTU | TUN:MAR01 | SCR | LCP | LCP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SCRLCP01TODO | 4 |  |  | 0 | $ComStatus , , | #LOCAL / REMOTE STATUS
399 | MAR01_RTU | TUN:MAR01 | SCR | FMOP | FMOP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SCRFMOP01TODO | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
400 | MAR01_RTU | TUN:MAR01 | SCR | FMOP | FMOP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SCRFMOP01TODO | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
401 | MAR01_RTU | TUN:MAR01 | SCR | FMOP | FMOP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SCRFMOP01TODO | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
402 | MAR01_RTU | TUN:MAR01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B OFFLINE
403 | MAR01_RTU | TUN:MAR01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC RUNNING.
404 | MAR01_RTU | TUN:MAR01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: POWER SUPPLY FAULT
405 | MAR01_RTU | TUN:MAR01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CPU MODULE FAULT
406 | MAR01_RTU | TUN:MAR01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CRP MODULE FAULT
407 | MAR01_RTU | TUN:MAR01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
408 | MAR01_RTU | TUN:MAR01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
409 | MAR01_RTU | TUN:MAR01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
410 | MAR01_RTU | TUN:MAR01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
411 | MAR01_RTU | TUN:MAR01 | TEL | SWI | SWI01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01TELSWI01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH FAULT
412 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
413 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
414 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
415 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
416 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
417 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
418 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
419 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
420 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
421 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
422 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
423 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
424 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
425 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
426 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
427 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
428 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
429 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
430 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
431 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
432 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
433 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
434 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
435 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
436 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
437 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
438 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
439 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
440 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
441 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
442 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
443 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
444 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
445 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
446 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
447 | MAR01_RTU | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
448 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
449 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
450 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
451 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
452 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
453 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
454 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
455 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
456 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
457 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
458 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
459 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
460 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
461 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
462 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
463 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
464 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
465 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
466 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
467 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
468 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
469 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
470 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
471 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
472 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
473 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
474 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
475 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
476 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
477 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
478 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
479 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
480 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
481 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
482 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
483 | MAR01_RTU | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
484 | MAR01_RTU | TUN:MAR01 | SMC | SMC | SMC01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SMCSMC01TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
485 | MAR01_RTU | TUN:MAR01 | SMC | SMC | SMC02 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SMCSMC02TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
486 | MAR01_RTU | TUN:MAR01 | SMC | SMC | SMC03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SMCSMC03TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
487 | MAR01_RTU | TUN:MAR01 | SMC | SMC | SMC04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SMCSMC04TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
488 | MAR01_RTU | TUN:MAR01 | SMC | SMC | SMC05 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SMCSMC05TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
489 | MAR01_RTU | TUN:MAR01 | SMC | SMC | SMC06 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SMCSMC06TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
490 | MAR01_RTU | TUN:MAR01 | SMC | SMC | SMC07 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SMCSMC07TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
491 | MAR01_RTU | TUN:MAR01 | SMC | SMC | SMC08 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SMCSMC08TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
492 | MAR01_RTU | TUN:MAR01 | SED | SED | SED01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SEDSED01TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
493 | MAR01_RTU | TUN:MAR01 | SED | SED | SED01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SEDSED01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
494 | MAR01_RTU | TUN:MAR01 | SED | SED | SED02 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SEDSED02TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
495 | MAR01_RTU | TUN:MAR01 | SED | SED | SED02 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SEDSED02TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
496 | MAR01_RTU | TUN:MAR01 | SED | SED | SED03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SEDSED03TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
497 | MAR01_RTU | TUN:MAR01 | SED | SED | SED03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SEDSED03TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
498 | MAR01_RTU | TUN:MAR01 | SED | SED | SED04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SEDSED04TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
499 | MAR01_RTU | TUN:MAR01 | SED | SED | SED04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SEDSED04TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
500 | MAR01_RTU | TUN:MAR01 | OTS | OTS | OTS001 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01OTSOTS001TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
501 | MAR01_RTU | TUN:MAR01 | OTS | OTS | OTS001 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01OTSOTS001TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
502 | MAR01_RTU | TUN:MAR01 | OTS | OTS | OTS001 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR01OTSOTS001TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
503 | MAR01_RTU | TUN:MAR01 | OTS | OTS | OTS002 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01OTSOTS002TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
504 | MAR01_RTU | TUN:MAR01 | OTS | OTS | OTS002 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01OTSOTS002TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
505 | MAR01_RTU | TUN:MAR01 | OTS | OTS | OTS002 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR01OTSOTS002TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
506 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
507 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
508 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
509 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
510 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
511 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
512 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
513 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
514 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
515 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
516 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
517 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
518 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
519 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
520 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
521 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
522 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
523 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
524 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
525 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
526 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
527 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
528 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
529 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
530 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
531 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
532 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
533 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
534 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
535 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
536 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
537 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
538 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
539 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
540 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
541 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
542 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
543 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
544 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
545 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNMAR01NS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
546 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
547 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
548 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
549 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
550 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
551 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
552 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
553 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
554 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
555 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
556 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
557 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
558 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
559 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
560 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
561 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
562 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
563 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
564 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
565 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
566 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
567 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
568 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
569 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
570 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
571 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
572 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
573 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
574 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
575 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
576 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
577 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
578 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
579 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
580 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
581 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
582 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
583 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
584 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
585 | MAR01_RTU | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNMAR01NS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
586 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
587 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
588 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
589 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
590 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
591 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
592 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
593 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
594 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
595 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
596 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
597 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
598 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
599 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
600 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
601 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
602 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
603 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
604 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
605 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
606 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
607 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
608 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
609 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
610 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
611 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
612 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
613 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
614 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
615 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
616 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
617 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
618 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
619 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
620 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
621 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
622 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
623 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
624 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
625 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNMAR01SS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
626 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
627 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
628 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
629 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
630 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
631 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
632 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
633 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
634 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
635 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
636 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
637 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
638 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
639 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
640 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
641 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
642 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
643 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
644 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
645 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
646 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
647 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
648 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
649 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
650 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
651 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
652 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
653 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
654 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
655 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
656 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
657 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
658 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
659 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
660 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
661 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
662 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
663 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
664 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
665 | MAR01_RTU | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNMAR01SS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
666 | MAR01_RTU | TUN:MAR01 | NS01:SENSOR | TTS | TS100269 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01SENSORTS100269TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
667 | MAR01_RTU | TUN:MAR01 | NS01:SENSOR | TTS | TS100269 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01SENSORTS100269TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
668 | MAR01_RTU | TUN:MAR01 | NS01:SENSOR | TTS | TS100269 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01SENSORTS100269TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
669 | MAR01_RTU | TUN:MAR01 | NS01:SENSOR | TTS | TS100269 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01SENSORTS100269TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
670 | MAR01_RTU | TUN:MAR01 | NS01:SENSOR | TTS | TS100269 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR01NS01SENSORTS100269TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
671 | MAR01_RTU | TUN:MAR01 | NS01:SENSOR | TTS | TS100269 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR01NS01SENSORTS100269TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
672 | MAR01_RTU | TUN:MAR01 | NS01:SENSOR | TTS | TS100222 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01SENSORTS100222TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
673 | MAR01_RTU | TUN:MAR01 | NS01:SENSOR | TTS | TS100222 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01SENSORTS100222TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
674 | MAR01_RTU | TUN:MAR01 | NS01:SENSOR | TTS | TS100222 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01SENSORTS100222TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
675 | MAR01_RTU | TUN:MAR01 | NS01:SENSOR | TTS | TS100222 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01SENSORTS100222TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
676 | MAR01_RTU | TUN:MAR01 | NS01:SENSOR | TTS | TS100222 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR01NS01SENSORTS100222TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
677 | MAR01_RTU | TUN:MAR01 | NS01:SENSOR | TTS | TS100222 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR01NS01SENSORTS100222TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
678 | MAR01_RTU | TUN:MAR01 | SS01:SENSOR | TTS | TS099914 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01SENSORTS099914TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
679 | MAR01_RTU | TUN:MAR01 | SS01:SENSOR | TTS | TS099914 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01SENSORTS099914TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
680 | MAR01_RTU | TUN:MAR01 | SS01:SENSOR | TTS | TS099914 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01SENSORTS099914TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
681 | MAR01_RTU | TUN:MAR01 | SS01:SENSOR | TTS | TS099914 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01SENSORTS099914TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
682 | MAR01_RTU | TUN:MAR01 | SS01:SENSOR | TTS | TS099914 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR01SS01SENSORTS099914TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
683 | MAR01_RTU | TUN:MAR01 | SS01:SENSOR | TTS | TS099914 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR01SS01SENSORTS099914TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
684 | MAR01_RTU | TUN:MAR01 | SS01:SENSOR | TTS | TS099816 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01SENSORTS099816TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
685 | MAR01_RTU | TUN:MAR01 | SS01:SENSOR | TTS | TS099816 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01SENSORTS099816TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
686 | MAR01_RTU | TUN:MAR01 | SS01:SENSOR | TTS | TS099816 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01SENSORTS099816TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
687 | MAR01_RTU | TUN:MAR01 | SS01:SENSOR | TTS | TS099816 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01SENSORTS099816TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
688 | MAR01_RTU | TUN:MAR01 | SS01:SENSOR | TTS | TS099816 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR01SS01SENSORTS099816TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
689 | MAR01_RTU | TUN:MAR01 | SS01:SENSOR | TTS | TS099816 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR01SS01SENSORTS099816TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
690 | MAR01_RTU | TUN:MAR01 | NS01:SENSOR | VS | VS100253 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01SENSORVS100253TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
691 | MAR01_RTU | TUN:MAR01 | NS01:SENSOR | VS | VS100253 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR01NS01SENSORVS100253TODO | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
692 | MAR01_RTU | TUN:MAR01 | SS01:SENSOR | VS | VS099848 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01SENSORVS099848TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
693 | MAR01_RTU | TUN:MAR01 | SS01:SENSOR | VS | VS099848 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR01SS01SENSORVS099848TODO | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
694 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
695 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
696 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
697 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
698 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
699 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
700 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
701 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
702 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
703 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
704 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
705 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
706 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
707 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
708 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
709 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
710 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
711 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
712 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
713 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
714 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
715 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
716 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
717 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
718 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
719 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
720 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
721 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
722 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
723 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
724 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
725 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
726 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
727 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
728 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
729 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
730 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
731 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
732 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
733 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
734 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
735 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
736 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
737 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
738 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
739 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
740 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
741 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
742 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
743 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
744 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
745 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
746 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
747 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
748 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
749 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
750 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
751 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
752 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
753 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
754 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
755 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
756 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
757 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
758 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
759 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
760 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
761 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
762 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
763 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
764 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
765 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
766 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
767 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
768 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
769 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
770 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
771 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
772 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
773 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
774 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
775 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
776 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
777 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
778 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
779 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
780 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
781 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
782 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
783 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
784 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
785 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
786 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
787 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
788 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
789 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
790 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
791 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
792 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
793 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Control |  | MAR01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
794 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
795 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
796 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
797 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
798 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-54 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERCON-54TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
799 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-54 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERCON-54TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
800 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-54 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERCON-54TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
801 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-54 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERCON-54TODO | 4 |  |  | 0 | $ComStatus , , | #
802 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-63 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERCON-63TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
803 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-63 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERCON-63TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
804 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-63 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERCON-63TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
805 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-63 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERCON-63TODO | 4 |  |  | 0 | $ComStatus , , | #
806 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-51 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERCON-51TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
807 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-51 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERCON-51TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
808 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-51 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERCON-51TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
809 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-51 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERCON-51TODO | 4 |  |  | 0 | $ComStatus , , | #
810 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-56 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERCON-56TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
811 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-56 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERCON-56TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
812 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-56 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERCON-56TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
813 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-56 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERCON-56TODO | 4 |  |  | 0 | $ComStatus , , | #
814 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-61 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERCON-61TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
815 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-61 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERCON-61TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
816 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-61 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERCON-61TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
817 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-61 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERCON-61TODO | 4 |  |  | 0 | $ComStatus , , | #
818 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-66 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERCON-66TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
819 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-66 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERCON-66TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
820 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-66 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERCON-66TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
821 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-66 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERCON-66TODO | 4 |  |  | 0 | $ComStatus , , | #
822 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-52 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERCON-52TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
823 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-52 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERCON-52TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
824 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-52 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERCON-52TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
825 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-52 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERCON-52TODO | 4 |  |  | 0 | $ComStatus , , | #
826 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-58 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01NS01DAMPERCON-58TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
827 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-58 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERCON-58TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
828 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-58 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERCON-58TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
829 | MAR01_RTU | TUN:MAR01 | NS01:DAMPER | MSFD | CON-58 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01DAMPERCON-58TODO | 4 |  |  | 0 | $ComStatus , , | #
830 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-59 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERCON-59TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
831 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-59 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERCON-59TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
832 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-59 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERCON-59TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
833 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-59 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERCON-59TODO | 4 |  |  | 0 | $ComStatus , , | #
834 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-67 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR01-SIL2_Monitoring |  | MAR01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR01SS01DAMPERCON-67TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
835 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-67 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERCON-67TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
836 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-67 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERCON-67TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
837 | MAR01_RTU | TUN:MAR01 | SS01:DAMPER | MSFD | CON-67 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01DAMPERCON-67TODO | 4 |  |  | 0 | $ComStatus , , | #
838 | MAR01_RTU | TUN:MAR01 | NS01:AHU | AHU | CON-05 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01AHUCON-05TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
839 | MAR01_RTU | TUN:MAR01 | NS01:AHU | AHU | CON-05 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01AHUCON-05TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
840 | MAR01_RTU | TUN:MAR01 | NS01:AHU | AHU | CON-06 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01AHUCON-06TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
841 | MAR01_RTU | TUN:MAR01 | NS01:AHU | AHU | CON-06 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01NS01AHUCON-06TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
842 | MAR01_RTU | TUN:MAR01 | SS01:AHU | AHU | CON-07 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01AHUCON-07TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
843 | MAR01_RTU | TUN:MAR01 | SS01:AHU | AHU | CON-07 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01AHUCON-07TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
844 | MAR01_RTU | TUN:MAR01 | SS01:AHU | AHU | CON-08 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01AHUCON-08TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
845 | MAR01_RTU | TUN:MAR01 | SS01:AHU | AHU | CON-08 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01SS01AHUCON-08TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
846 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY DISCONNECTING SWITCH - OPEN
847 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY VOLTAGE PRESENCE
848 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER OPEN
849 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER FAULT
850 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN
851 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT
852 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS OPEN
853 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS FAULT
854 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER OPEN
855 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER FAULT
856 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER OPEN
857 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER FAULT
858 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS DISCONNECTING SWITCH OPEN
859 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS FAULT
860 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN
861 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT
862 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 ABSENCE OF VOLTAGE
863 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN
864 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT
865 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 ABSENCE OF VOLTAGE
866 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER OPEN
867 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER FAULT
868 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER OPEN
869 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER FAULT
870 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER OPEN
871 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER FAULT
872 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER OPEN
873 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER FAULT
874 | MAR01_RTU | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SURGE ARRESTER TRIGGERED
875 | MAR01_RTU | TUN:MAR01 | MMS | ADS | EL2-LBS01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-LBS01TODO | 4 |  |  | 0 | $ComStatus , , | #
876 | MAR01_RTU | TUN:MAR01 | MMS | ADS | EL2-LBS01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-LBS01TODO | 4 |  |  | 0 | $ComStatus , , | #
877 | MAR01_RTU | TUN:MAR01 | MMS | ADS | EL2-LBS02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-LBS02TODO | 4 |  |  | 0 | $ComStatus , , | #
878 | MAR01_RTU | TUN:MAR01 | MMS | ADS | EL2-LBS02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-LBS02TODO | 4 |  |  | 0 | $ComStatus , , | #
879 | MAR01_RTU | TUN:MAR01 | MMS | TRF | MV-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMV-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
880 | MAR01_RTU | TUN:MAR01 | MMS | TRF | MV-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMV-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
881 | MAR01_RTU | TUN:MAR01 | MMS | TRF | MV-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMV-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
882 | MAR01_RTU | TUN:MAR01 | MMS | TRF | MV-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMV-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
883 | MAR01_RTU | TUN:MAR01 | MMS | TRF | MV-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMV-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
884 | MAR01_RTU | TUN:MAR01 | MMS | TRF | MV-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMV-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
885 | MAR01_RTU | TUN:MAR01 | MMS | TRF | MV-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMV-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
886 | MAR01_RTU | TUN:MAR01 | MMS | TRF | MV-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMV-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
887 | MAR01_RTU | TUN:MAR01 | MMS | TRF | MV-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMV-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
888 | MAR01_RTU | TUN:MAR01 | MMS | TRF | MV-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMV-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
889 | MAR01_RTU | TUN:MAR01 | MMS | ACB | EL2-CBC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-CBC01TODO | 4 |  |  | 0 | $ComStatus , , | #
890 | MAR01_RTU | TUN:MAR01 | MMS | ACB | EL2-CBC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-CBC01TODO | 4 |  |  | 0 | $ComStatus , , | #
891 | MAR01_RTU | TUN:MAR01 | MMS | ACB | EL2-CBC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-CBC01TODO | 4 |  |  | 0 | $ComStatus , , | #
892 | MAR01_RTU | TUN:MAR01 | MMS | ACB | EL2-CBC02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-CBC02TODO | 4 |  |  | 0 | $ComStatus , , | #
893 | MAR01_RTU | TUN:MAR01 | MMS | ACB | EL2-CBC02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-CBC02TODO | 4 |  |  | 0 | $ComStatus , , | #
894 | MAR01_RTU | TUN:MAR01 | MMS | ACB | EL2-CBC02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-CBC02TODO | 4 |  |  | 0 | $ComStatus , , | #
895 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
896 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
897 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
898 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
899 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
900 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
901 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
902 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
903 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
904 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
905 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
906 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
907 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
908 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
909 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
910 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
911 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
912 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
913 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
914 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
915 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
916 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
917 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
918 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
919 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
920 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
921 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
922 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
923 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
924 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
925 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
926 | MAR01_RTU | TUN:MAR01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
927 | MAR01_RTU | TUN:MAR01 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
928 | MAR01_RTU | TUN:MAR01 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
929 | MAR01_RTU | TUN:MAR01 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
930 | MAR01_RTU | TUN:MAR01 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
931 | MAR01_RTU | TUN:MAR01 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
932 | MAR01_RTU | TUN:MAR01 | MMS | MCCB | EL1-VSD0102 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL1-VSD0102TODO | 4 |  |  | 0 | $ComStatus , , | #
933 | MAR01_RTU | TUN:MAR01 | MMS | MCCB | EL1-VSD0102 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL1-VSD0102TODO | 4 |  |  | 0 | $ComStatus , , | #
934 | MAR01_RTU | TUN:MAR01 | MMS | LBS | EL1-VSD0102 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL1-VSD0102TODO | 4 |  |  | 0 | $ComStatus , , | #
935 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL1-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL1-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
936 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL1-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL1-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
937 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL1-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL1-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
938 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL1-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL1-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
939 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
940 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
941 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
942 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
943 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
944 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
945 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
946 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
947 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT6-IDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT6-IDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
948 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT6-IDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT6-IDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
949 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT6-IDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT6-IDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
950 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT6-IDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT6-IDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
951 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT6-IDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT6-IDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
952 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT6-IDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT6-IDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
953 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT6-IDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT6-IDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
954 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT6-IDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT6-IDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
955 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT6-IDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT6-IDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
956 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT6-IDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT6-IDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
957 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT6-IDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT6-IDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
958 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT6-IDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT6-IDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
959 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-FR2-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-FR2-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
960 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-FR2-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-FR2-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
961 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-FR2-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-FR2-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
962 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-FR2-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-FR2-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
963 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-FR2-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-FR2-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
964 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-FR2-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-FR2-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
965 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-FR2-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-FR2-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
966 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-FR2-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-FR2-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
967 | MAR01_RTU | TUN:MAR01 | MMS | MCB | MSFD-CON-63 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMSFD-CON-63TODO | 4 |  |  | 0 | $ComStatus , , | #
968 | MAR01_RTU | TUN:MAR01 | MMS | MCB | MSFD-CON-63 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMSFD-CON-63TODO | 4 |  |  | 0 | $ComStatus , , | #
969 | MAR01_RTU | TUN:MAR01 | MMS | MCB | MSFD-CON-59 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMSFD-CON-59TODO | 4 |  |  | 0 | $ComStatus , , | #
970 | MAR01_RTU | TUN:MAR01 | MMS | MCB | MSFD-CON-59 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMSFD-CON-59TODO | 4 |  |  | 0 | $ComStatus , , | #
971 | MAR01_RTU | TUN:MAR01 | MMS | MCB | MSFD-CON-67 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMSFD-CON-67TODO | 4 |  |  | 0 | $ComStatus , , | #
972 | MAR01_RTU | TUN:MAR01 | MMS | MCB | MSFD-CON-67 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMSFD-CON-67TODO | 4 |  |  | 0 | $ComStatus , , | #
973 | MAR01_RTU | TUN:MAR01 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
974 | MAR01_RTU | TUN:MAR01 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
975 | MAR01_RTU | TUN:MAR01 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
976 | MAR01_RTU | TUN:MAR01 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
977 | MAR01_RTU | TUN:MAR01 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
978 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-LBS01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-LBS01TODO | 4 |  |  | 0 | $ComStatus , , | #
979 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-LBS01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-LBS01TODO | 4 |  |  | 0 | $ComStatus , , | #
980 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-LBS02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-LBS02TODO | 4 |  |  | 0 | $ComStatus , , | #
981 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-LBS02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-LBS02TODO | 4 |  |  | 0 | $ComStatus , , | #
982 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-CBC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-CBC01TODO | 4 |  |  | 0 | $ComStatus , , | #
983 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-CBC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-CBC01TODO | 4 |  |  | 0 | $ComStatus , , | #
984 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-CBC02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-CBC02TODO | 4 |  |  | 0 | $ComStatus , , | #
985 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-CBC02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-CBC02TODO | 4 |  |  | 0 | $ComStatus , , | #
986 | MAR01_RTU | TUN:MAR01 | MMS | MCCB | EL2-2P | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-2PTODO | 4 |  |  | 0 | $ComStatus , , | #
987 | MAR01_RTU | TUN:MAR01 | MMS | MCCB | EL2-2P | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-2PTODO | 4 |  |  | 0 | $ComStatus , , | #
988 | MAR01_RTU | TUN:MAR01 | MMS | LBS | EL2-2P | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-2PTODO | 4 |  |  | 0 | $ComStatus , , | #
989 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-CBC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-CBC01TODO | 4 |  |  | 0 | $ComStatus , , | #
990 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-CBC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-CBC01TODO | 4 |  |  | 0 | $ComStatus , , | #
991 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-CBC02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-CBC02TODO | 4 |  |  | 0 | $ComStatus , , | #
992 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-CBC02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-CBC02TODO | 4 |  |  | 0 | $ComStatus , , | #
993 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
994 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
995 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
996 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
997 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-LBS01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-LBS01TODO | 4 |  |  | 0 | $ComStatus , , | #
998 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-LBS01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-LBS01TODO | 4 |  |  | 0 | $ComStatus , , | #
999 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-LBS02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-LBS02TODO | 4 |  |  | 0 | $ComStatus , , | #
1000 | MAR01_RTU | TUN:MAR01 | MMS | MCB | EL2-LBS02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSEL2-LBS02TODO | 4 |  |  | 0 | $ComStatus , , | #
1001 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1002 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1003 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1004 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1005 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1006 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1007 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1008 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1009 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT5-IDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT5-IDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1010 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT5-IDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT5-IDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1011 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT5-IDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT5-IDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1012 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT5-IDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT5-IDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1013 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT5-IDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT5-IDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1014 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT5-IDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT5-IDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1015 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT5-IDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT5-IDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1016 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT5-IDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT5-IDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1017 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT5-IDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT5-IDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
1018 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-VT5-IDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-VT5-IDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
1019 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT5-IDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT5-IDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
1020 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-VT5-IDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-VT5-IDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
1021 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-FR1-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-FR1-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1022 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-FR1-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-FR1-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1023 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-FR1-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-FR1-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1024 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-FR1-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-FR1-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1025 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-FR1-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-FR1-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1026 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 3P-FR1-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS3P-FR1-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1027 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-FR1-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-FR1-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1028 | MAR01_RTU | TUN:MAR01 | MMS | MCB | 2P-FR1-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMS2P-FR1-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1029 | MAR01_RTU | TUN:MAR01 | MMS | MCB | MSFD-CON-54 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMSFD-CON-54TODO | 4 |  |  | 0 | $ComStatus , , | #
1030 | MAR01_RTU | TUN:MAR01 | MMS | MCB | MSFD-CON-54 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMSFD-CON-54TODO | 4 |  |  | 0 | $ComStatus , , | #
1031 | MAR01_RTU | TUN:MAR01 | MMS | MCB | MSFD-CON-52 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMSFD-CON-52TODO | 4 |  |  | 0 | $ComStatus , , | #
1032 | MAR01_RTU | TUN:MAR01 | MMS | MCB | MSFD-CON-52 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMSFD-CON-52TODO | 4 |  |  | 0 | $ComStatus , , | #
1033 | MAR01_RTU | TUN:MAR01 | MMS | MCB | MSFD-CON-58 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMSFD-CON-58TODO | 4 |  |  | 0 | $ComStatus , , | #
1034 | MAR01_RTU | TUN:MAR01 | MMS | MCB | MSFD-CON-58 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR01-SIL0 |  | MAR01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR01MMSMSFD-CON-58TODO | 4 |  |  | 0 | $ComStatus , , | #
1035 | MAR0A_RTU | TUN:MAR0A | SCR | LCP | LCP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASCRLCP01TODO | 4 |  |  | 0 | $ComStatus , , | #COMMUNICATION FAULT WITH PLC
1036 | MAR0A_RTU | TUN:MAR0A | SCR | LCP | LCP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASCRLCP01TODO | 4 |  |  | 0 | $ComStatus , , | #LOCAL / REMOTE STATUS
1037 | MAR0A_RTU | TUN:MAR0A | SCR | FMOP | FMOP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Monitoring |  | MAR0A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASCRFMOP01TODO | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
1038 | MAR0A_RTU | TUN:MAR0A | SCR | FMOP | FMOP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Monitoring |  | MAR0A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASCRFMOP01TODO | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
1039 | MAR0A_RTU | TUN:MAR0A | SCR | FMOP | FMOP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Monitoring |  | MAR0A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASCRFMOP01TODO | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
1040 | MAR0A_RTU | TUN:MAR0A | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B OFFLINE
1041 | MAR0A_RTU | TUN:MAR0A | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC RUNNING.
1042 | MAR0A_RTU | TUN:MAR0A | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: POWER SUPPLY FAULT
1043 | MAR0A_RTU | TUN:MAR0A | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CPU MODULE FAULT
1044 | MAR0A_RTU | TUN:MAR0A | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CRP MODULE FAULT
1045 | MAR0A_RTU | TUN:MAR0A | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
1046 | MAR0A_RTU | TUN:MAR0A | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
1047 | MAR0A_RTU | TUN:MAR0A | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
1048 | MAR0A_RTU | TUN:MAR0A | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
1049 | MAR0A_RTU | TUN:MAR0A | TEL | SWI | SWI01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATELSWI01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH FAULT
1050 | MAR0A_RTU | TUN:MAR0A | OTS | OTS | OTS001 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AOTSOTS001TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1051 | MAR0A_RTU | TUN:MAR0A | OTS | OTS | OTS001 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AOTSOTS001TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1052 | MAR0A_RTU | TUN:MAR0A | OTS | OTS | OTS001 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR0AOTSOTS001TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1053 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099152 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASENSORTS099152TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1054 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099152 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASENSORTS099152TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1055 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099152 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASENSORTS099152TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1056 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099152 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASENSORTS099152TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1057 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099152 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR0ASENSORTS099152TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1058 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099152 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR0ASENSORTS099152TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1059 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099343 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASENSORTS099343TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1060 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099343 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASENSORTS099343TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1061 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099343 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASENSORTS099343TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1062 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099343 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASENSORTS099343TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1063 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099343 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR0ASENSORTS099343TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1064 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099343 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR0ASENSORTS099343TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1065 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099620 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASENSORTS099620TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1066 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099620 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASENSORTS099620TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1067 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099620 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASENSORTS099620TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1068 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099620 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASENSORTS099620TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1069 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099620 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR0ASENSORTS099620TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1070 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099620 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR0ASENSORTS099620TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1071 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099718 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASENSORTS099718TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1072 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099718 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASENSORTS099718TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1073 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099718 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASENSORTS099718TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1074 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099718 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASENSORTS099718TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1075 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099718 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR0ASENSORTS099718TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1076 | MAR0A_RTU | TUN:MAR0A | SENSOR | TTS | TS099718 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR0ASENSORTS099718TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1077 | MAR0A_RTU | TUN:MAR0A | SENSOR | VS | VS099216 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASENSORVS099216TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1078 | MAR0A_RTU | TUN:MAR0A | SENSOR | VS | VS099216 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR0ASENSORVS099216TODO | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
1079 | MAR0A_RTU | TUN:MAR0A | SENSOR | VS | VS099685 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ASENSORVS099685TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1080 | MAR0A_RTU | TUN:MAR0A | SENSOR | VS | VS099685 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR0ASENSORVS099685TODO | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
1081 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Monitoring |  | MAR0A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1082 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Monitoring |  | MAR0A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1083 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Monitoring |  | MAR0A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
1084 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1085 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1086 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1087 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1088 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1089 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
1090 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
1091 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
1092 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
1093 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
1094 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1095 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1096 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1097 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1098 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
1099 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
1100 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
1101 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
1102 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
1103 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
1104 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
1105 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
1106 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
1107 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
1108 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
1109 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
1110 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
1111 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
1112 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
1113 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
1114 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
1115 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
1116 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
1117 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
1118 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
1119 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
1120 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNMAR0ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
1121 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Monitoring |  | MAR0A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1122 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Monitoring |  | MAR0A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1123 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Monitoring |  | MAR0A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
1124 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1125 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1126 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1127 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1128 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1129 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
1130 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
1131 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
1132 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
1133 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
1134 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1135 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1136 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1137 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1138 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
1139 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
1140 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
1141 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
1142 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
1143 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
1144 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
1145 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
1146 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
1147 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
1148 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
1149 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
1150 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
1151 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
1152 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
1153 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
1154 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
1155 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
1156 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
1157 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
1158 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
1159 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
1160 | MAR0A_RTU | TUN:MAR0A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNMAR0ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
1161 | MAR0A_RTU | TUN:MAR0A | DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Monitoring |  | MAR0A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ADAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1162 | MAR0A_RTU | TUN:MAR0A | DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Monitoring |  | MAR0A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ADAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1163 | MAR0A_RTU | TUN:MAR0A | DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ADAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
1164 | MAR0A_RTU | TUN:MAR0A | DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ADAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
1165 | MAR0A_RTU | TUN:MAR0A | DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ADAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1166 | MAR0A_RTU | TUN:MAR0A | DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ADAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1167 | MAR0A_RTU | TUN:MAR0A | DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Monitoring |  | MAR0A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ADAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1168 | MAR0A_RTU | TUN:MAR0A | DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Monitoring |  | MAR0A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0ADAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1169 | MAR0A_RTU | TUN:MAR0A | DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ADAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
1170 | MAR0A_RTU | TUN:MAR0A | DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ADAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
1171 | MAR0A_RTU | TUN:MAR0A | DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ADAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1172 | MAR0A_RTU | TUN:MAR0A | DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0ADAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1173 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Monitoring |  | MAR0A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0APFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1174 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Monitoring |  | MAR0A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0APFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1175 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0APFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
1176 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0APFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1177 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0APFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1178 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0APFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1179 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0APFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1180 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0APFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1181 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0APFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
1182 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0APFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
1183 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0APFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
1184 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0APFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
1185 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0APFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1186 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0APFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1187 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0APFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1188 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0APFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1189 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0APFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
1190 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0APFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
1191 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-02 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Monitoring |  | MAR0A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0APFAGRD-02TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1192 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-02 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Monitoring |  | MAR0A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0APFAGRD-02TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1193 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0APFAGRD-02TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
1194 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-02 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0APFAGRD-02TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1195 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-02 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0APFAGRD-02TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1196 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-02 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0APFAGRD-02TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1197 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-02 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0APFAGRD-02TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1198 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-02 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0APFAGRD-02TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1199 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-02 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0APFAGRD-02TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
1200 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-02 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0APFAGRD-02TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
1201 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-02 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0APFAGRD-02TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
1202 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-02 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0APFAGRD-02TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
1203 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-02 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0APFAGRD-02TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1204 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-02 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0APFAGRD-02TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1205 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-02 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNMAR0APFAGRD-02TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1206 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-02 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | MAR0A-SIL2_Control |  | MAR0A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNMAR0APFAGRD-02TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1207 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0APFAGRD-02TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
1208 | MAR0A_RTU | TUN:MAR0A | PFA | PFA | GRD-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0APFAGRD-02TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
1209 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY DISCONNECTING SWITCH - OPEN
1210 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY VOLTAGE PRESENCE
1211 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER OPEN
1212 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER FAULT
1213 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN
1214 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT
1215 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS OPEN
1216 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS FAULT
1217 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER OPEN
1218 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER FAULT
1219 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER OPEN
1220 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER FAULT
1221 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS DISCONNECTING SWITCH OPEN
1222 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS FAULT
1223 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN
1224 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT
1225 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 ABSENCE OF VOLTAGE
1226 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN
1227 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT
1228 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 ABSENCE OF VOLTAGE
1229 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER OPEN
1230 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER FAULT
1231 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER OPEN
1232 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER FAULT
1233 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER OPEN
1234 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER FAULT
1235 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER OPEN
1236 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER FAULT
1237 | MAR0A_RTU | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SURGE ARRESTER TRIGGERED
1238 | MAR0A_RTU | TUN:MAR0A | MMS | ADS | EL3-LBW01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-LBW01TODO | 4 |  |  | 0 | $ComStatus , , | #
1239 | MAR0A_RTU | TUN:MAR0A | MMS | ADS | EL3-LBW01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-LBW01TODO | 4 |  |  | 0 | $ComStatus , , | #
1240 | MAR0A_RTU | TUN:MAR0A | MMS | ADS | EL3-LBW02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-LBW02TODO | 4 |  |  | 0 | $ComStatus , , | #
1241 | MAR0A_RTU | TUN:MAR0A | MMS | ADS | EL3-LBW02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-LBW02TODO | 4 |  |  | 0 | $ComStatus , , | #
1242 | MAR0A_RTU | TUN:MAR0A | MMS | TRF | EL3-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
1243 | MAR0A_RTU | TUN:MAR0A | MMS | TRF | EL3-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
1244 | MAR0A_RTU | TUN:MAR0A | MMS | TRF | EL3-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
1245 | MAR0A_RTU | TUN:MAR0A | MMS | TRF | EL3-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
1246 | MAR0A_RTU | TUN:MAR0A | MMS | TRF | EL3-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
1247 | MAR0A_RTU | TUN:MAR0A | MMS | TRF | EL3-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
1248 | MAR0A_RTU | TUN:MAR0A | MMS | TRF | EL3-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
1249 | MAR0A_RTU | TUN:MAR0A | MMS | TRF | EL3-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
1250 | MAR0A_RTU | TUN:MAR0A | MMS | TRF | EL3-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
1251 | MAR0A_RTU | TUN:MAR0A | MMS | TRF | EL3-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
1252 | MAR0A_RTU | TUN:MAR0A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1253 | MAR0A_RTU | TUN:MAR0A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1254 | MAR0A_RTU | TUN:MAR0A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1255 | MAR0A_RTU | TUN:MAR0A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1256 | MAR0A_RTU | TUN:MAR0A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1257 | MAR0A_RTU | TUN:MAR0A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1258 | MAR0A_RTU | TUN:MAR0A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1259 | MAR0A_RTU | TUN:MAR0A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1260 | MAR0A_RTU | TUN:MAR0A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1261 | MAR0A_RTU | TUN:MAR0A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1262 | MAR0A_RTU | TUN:MAR0A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1263 | MAR0A_RTU | TUN:MAR0A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1264 | MAR0A_RTU | TUN:MAR0A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1265 | MAR0A_RTU | TUN:MAR0A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1266 | MAR0A_RTU | TUN:MAR0A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1267 | MAR0A_RTU | TUN:MAR0A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1268 | MAR0A_RTU | TUN:MAR0A | MMS | EL | EL3-PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-PLC01TODO | 4 |  |  | 0 | $ComStatus , , | #
1269 | MAR0A_RTU | TUN:MAR0A | MMS | EL | EL3-PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-PLC01TODO | 4 |  |  | 0 | $ComStatus , , | #
1270 | MAR0A_RTU | TUN:MAR0A | MMS | EL | EL3-PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-PLC01TODO | 4 |  |  | 0 | $ComStatus , , | #
1271 | MAR0A_RTU | TUN:MAR0A | MMS | EL | EL3-PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-PLC01TODO | 4 |  |  | 0 | $ComStatus , , | #
1272 | MAR0A_RTU | TUN:MAR0A | MMS | EL | EL3-PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-PLC01TODO | 4 |  |  | 0 | $ComStatus , , | #
1273 | MAR0A_RTU | TUN:MAR0A | MMS | LBS | EL3-4P | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-4PTODO | 4 |  |  | 0 | $ComStatus , , | #
1274 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | EL3-LBW01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-LBW01TODO | 4 |  |  | 0 | $ComStatus , , | #
1275 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | EL3-LBW01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-LBW01TODO | 4 |  |  | 0 | $ComStatus , , | #
1276 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | EL3-LBW02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-LBW02TODO | 4 |  |  | 0 | $ComStatus , , | #
1277 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | EL3-LBW02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-LBW02TODO | 4 |  |  | 0 | $ComStatus , , | #
1278 | MAR0A_RTU | TUN:MAR0A | MMS | MCCB | EL3-2P | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-2PTODO | 4 |  |  | 0 | $ComStatus , , | #
1279 | MAR0A_RTU | TUN:MAR0A | MMS | MCCB | EL3-2P | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-2PTODO | 4 |  |  | 0 | $ComStatus , , | #
1280 | MAR0A_RTU | TUN:MAR0A | MMS | LBS | EL3-2P | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-2PTODO | 4 |  |  | 0 | $ComStatus , , | #
1281 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | EL3-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
1282 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | EL3-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
1283 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | EL3-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
1284 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | EL3-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
1285 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | EL3-LBW01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-LBW01TODO | 4 |  |  | 0 | $ComStatus , , | #
1286 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | EL3-LBW01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-LBW01TODO | 4 |  |  | 0 | $ComStatus , , | #
1287 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | EL3-LBW02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-LBW02TODO | 4 |  |  | 0 | $ComStatus , , | #
1288 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | EL3-LBW02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-LBW02TODO | 4 |  |  | 0 | $ComStatus , , | #
1289 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1290 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1291 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | 3P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMS3P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1292 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | 3P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMS3P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1293 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | 2P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMS2P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1294 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | 2P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMS2P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1295 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | 3P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMS3P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1296 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | 3P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMS3P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1297 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | 2P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMS2P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1298 | MAR0A_RTU | TUN:MAR0A | MMS | MCB | 2P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | MAR0A-SIL0 |  | MAR0A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNMAR0AMMS2P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1299 | EC101_RTU | TUN:EC101 | SCR | LCP | LCP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SCRLCP01TODO | 4 |  |  | 0 | $ComStatus , , | #COMMUNICATION FAULT WITH PLC
1300 | EC101_RTU | TUN:EC101 | SCR | LCP | LCP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SCRLCP01TODO | 4 |  |  | 0 | $ComStatus , , | #LOCAL / REMOTE STATUS
1301 | EC101_RTU | TUN:EC101 | SCR | FMOP | FMOP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SCRFMOP01TODO | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
1302 | EC101_RTU | TUN:EC101 | SCR | FMOP | FMOP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SCRFMOP01TODO | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
1303 | EC101_RTU | TUN:EC101 | SCR | FMOP | FMOP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SCRFMOP01TODO | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
1304 | EC101_RTU | TUN:EC101 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B OFFLINE
1305 | EC101_RTU | TUN:EC101 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC RUNNING.
1306 | EC101_RTU | TUN:EC101 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: POWER SUPPLY FAULT
1307 | EC101_RTU | TUN:EC101 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CPU MODULE FAULT
1308 | EC101_RTU | TUN:EC101 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CRP MODULE FAULT
1309 | EC101_RTU | TUN:EC101 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
1310 | EC101_RTU | TUN:EC101 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
1311 | EC101_RTU | TUN:EC101 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
1312 | EC101_RTU | TUN:EC101 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
1313 | EC101_RTU | TUN:EC101 | TEL | SWI | SWI01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101TELSWI01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH FAULT
1314 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFACON-06TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1315 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFACON-06TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1316 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFACON-06TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
1317 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFACON-06TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1318 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFACON-06TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1319 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFACON-06TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1320 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFACON-06TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1321 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFACON-06TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1322 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFACON-06TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
1323 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFACON-06TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
1324 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFACON-06TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
1325 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFACON-06TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
1326 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFACON-06TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1327 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFACON-06TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1328 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFACON-06TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1329 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFACON-06TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1330 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFACON-06TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
1331 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFACON-06TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
1332 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1333 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1334 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
1335 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1336 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1337 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1338 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1339 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1340 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
1341 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
1342 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
1343 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
1344 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1345 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1346 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1347 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1348 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
1349 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
1350 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1351 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1352 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
1353 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1354 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1355 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1356 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1357 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1358 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
1359 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
1360 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
1361 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
1362 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1363 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1364 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1365 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1366 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
1367 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
1368 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1369 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1370 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
1371 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1372 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1373 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1374 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1375 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1376 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
1377 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
1378 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
1379 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
1380 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1381 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1382 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1383 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1384 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
1385 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
1386 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFACON-07TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1387 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFACON-07TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1388 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFACON-07TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
1389 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFACON-07TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1390 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFACON-07TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1391 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFACON-07TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1392 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFACON-07TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1393 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFACON-07TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1394 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFACON-07TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
1395 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFACON-07TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
1396 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFACON-07TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
1397 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFACON-07TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
1398 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFACON-07TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1399 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFACON-07TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1400 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFACON-07TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1401 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFACON-07TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1402 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFACON-07TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
1403 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFACON-07TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
1404 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1405 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1406 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
1407 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1408 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1409 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1410 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1411 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1412 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
1413 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
1414 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
1415 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
1416 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1417 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1418 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1419 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1420 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
1421 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
1422 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SMCSMC01TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
1423 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC02 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SMCSMC02TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
1424 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SMCSMC03TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
1425 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SMCSMC04TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
1426 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC05 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SMCSMC05TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
1427 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC06 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SMCSMC06TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
1428 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC07 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SMCSMC07TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
1429 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC08 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SMCSMC08TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
1430 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC09 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SMCSMC09TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
1431 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC10 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SMCSMC10TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
1432 | EC101_RTU | TUN:EC101 | SED | SED | SED01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SEDSED01TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
1433 | EC101_RTU | TUN:EC101 | SED | SED | SED01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SEDSED01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
1434 | EC101_RTU | TUN:EC101 | SED | SED | SED02 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SEDSED02TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
1435 | EC101_RTU | TUN:EC101 | SED | SED | SED02 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SEDSED02TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
1436 | EC101_RTU | TUN:EC101 | SED | SED | SED03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SEDSED03TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
1437 | EC101_RTU | TUN:EC101 | SED | SED | SED03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SEDSED03TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
1438 | EC101_RTU | TUN:EC101 | SED | SED | SED04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SEDSED04TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
1439 | EC101_RTU | TUN:EC101 | SED | SED | SED04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101SEDSED04TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
1440 | EC101_RTU | TUN:EC101 | OTS | OTS | OTS001 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101OTSOTS001TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1441 | EC101_RTU | TUN:EC101 | OTS | OTS | OTS001 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101OTSOTS001TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1442 | EC101_RTU | TUN:EC101 | OTS | OTS | OTS001 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC101OTSOTS001TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1443 | EC101_RTU | TUN:EC101 | OTS | OTS | OTS002 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101OTSOTS002TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1444 | EC101_RTU | TUN:EC101 | OTS | OTS | OTS002 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101OTSOTS002TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1445 | EC101_RTU | TUN:EC101 | OTS | OTS | OTS002 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC101OTSOTS002TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1446 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1447 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1448 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
1449 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1450 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1451 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1452 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1453 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1454 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
1455 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
1456 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
1457 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
1458 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
1459 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1460 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1461 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1462 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1463 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
1464 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
1465 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
1466 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
1467 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
1468 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
1469 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
1470 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
1471 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
1472 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
1473 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
1474 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
1475 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
1476 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
1477 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
1478 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
1479 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
1480 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
1481 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
1482 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
1483 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
1484 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
1485 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNEC101WS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
1486 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1487 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1488 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
1489 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1490 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1491 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1492 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1493 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1494 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
1495 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
1496 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
1497 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
1498 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
1499 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1500 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1501 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1502 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1503 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
1504 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
1505 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
1506 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
1507 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
1508 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
1509 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
1510 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
1511 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
1512 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
1513 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
1514 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
1515 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
1516 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
1517 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
1518 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
1519 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
1520 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
1521 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
1522 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
1523 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
1524 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
1525 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNEC101WS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
1526 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1527 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1528 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
1529 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1530 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1531 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1532 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1533 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1534 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
1535 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
1536 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
1537 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
1538 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
1539 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1540 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1541 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1542 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1543 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
1544 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
1545 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
1546 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
1547 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
1548 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
1549 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
1550 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
1551 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
1552 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
1553 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
1554 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
1555 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
1556 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
1557 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
1558 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
1559 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
1560 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
1561 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
1562 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
1563 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
1564 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
1565 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNEC101ES01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
1566 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1567 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1568 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
1569 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1570 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1571 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1572 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1573 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1574 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
1575 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
1576 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
1577 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
1578 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
1579 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1580 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1581 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1582 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1583 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
1584 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
1585 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
1586 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
1587 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
1588 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
1589 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
1590 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
1591 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
1592 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
1593 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
1594 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
1595 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
1596 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
1597 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
1598 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
1599 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
1600 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
1601 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
1602 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
1603 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
1604 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
1605 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNEC101ES01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
1606 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101561 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01SENSORTS101561TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1607 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101561 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01SENSORTS101561TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1608 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101561 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01SENSORTS101561TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1609 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101561 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01SENSORTS101561TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1610 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101561 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC101WS01SENSORTS101561TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1611 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101561 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC101WS01SENSORTS101561TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1612 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101647 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01SENSORTS101647TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1613 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101647 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01SENSORTS101647TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1614 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101647 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01SENSORTS101647TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1615 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101647 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01SENSORTS101647TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1616 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101647 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC101WS01SENSORTS101647TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1617 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101647 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC101WS01SENSORTS101647TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1618 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101045 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01SENSORTS101045TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1619 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101045 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01SENSORTS101045TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1620 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101045 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01SENSORTS101045TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1621 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101045 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01SENSORTS101045TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1622 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101045 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC101ES01SENSORTS101045TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1623 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101045 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC101ES01SENSORTS101045TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1624 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101184 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01SENSORTS101184TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1625 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101184 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01SENSORTS101184TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1626 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101184 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01SENSORTS101184TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1627 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101184 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01SENSORTS101184TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1628 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101184 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC101ES01SENSORTS101184TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1629 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101184 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC101ES01SENSORTS101184TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1630 | EC101_RTU | TUN:EC101 | WS01:SENSOR | VS | VS101618 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01SENSORVS101618TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1631 | EC101_RTU | TUN:EC101 | WS01:SENSOR | VS | VS101618 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC101WS01SENSORVS101618TODO | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
1632 | EC101_RTU | TUN:EC101 | ES01:SENSOR | VS | VS101094 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01SENSORVS101094TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1633 | EC101_RTU | TUN:EC101 | ES01:SENSOR | VS | VS101094 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC101ES01SENSORVS101094TODO | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
1634 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1635 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1636 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1637 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1638 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1639 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1640 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1641 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1642 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
1643 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
1644 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
1645 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
1646 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
1647 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
1648 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
1649 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
1650 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
1651 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
1652 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1653 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1654 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1655 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1656 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1657 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1658 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1659 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1660 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1661 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1662 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
1663 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
1664 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
1665 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
1666 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
1667 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
1668 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
1669 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
1670 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
1671 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
1672 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1673 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1674 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1675 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1676 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
1677 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
1678 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1679 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1680 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1681 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1682 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
1683 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
1684 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1685 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1686 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1687 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1688 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
1689 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
1690 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1691 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1692 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1693 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1694 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
1695 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
1696 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1697 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1698 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1699 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1700 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1701 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1702 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1703 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1704 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1705 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1706 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
1707 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
1708 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
1709 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
1710 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
1711 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
1712 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
1713 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
1714 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
1715 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
1716 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1717 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1718 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1719 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1720 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1721 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1722 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1723 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1724 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1725 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1726 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
1727 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
1728 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
1729 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
1730 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
1731 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
1732 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
1733 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
1734 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
1735 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
1736 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1737 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1738 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | PLA-68 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERPLA-68TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1739 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | PLA-68 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERPLA-68TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1740 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | PLA-68 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERPLA-68TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1741 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | PLA-68 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERPLA-68TODO | 4 |  |  | 0 | $ComStatus , , | #
1742 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | PLA-33 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERPLA-33TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1743 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | PLA-33 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERPLA-33TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1744 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | PLA-33 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERPLA-33TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1745 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | PLA-33 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERPLA-33TODO | 4 |  |  | 0 | $ComStatus , , | #
1746 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-80 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERCON-80TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1747 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-80 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERCON-80TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1748 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-80 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERCON-80TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1749 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-80 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERCON-80TODO | 4 |  |  | 0 | $ComStatus , , | #
1750 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-72 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERCON-72TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1751 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-72 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERCON-72TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1752 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-72 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERCON-72TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1753 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-72 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERCON-72TODO | 4 |  |  | 0 | $ComStatus , , | #
1754 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-25 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERCON-25TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1755 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-25 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERCON-25TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1756 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-25 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERCON-25TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1757 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-25 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERCON-25TODO | 4 |  |  | 0 | $ComStatus , , | #
1758 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-26 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERCON-26TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1759 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-26 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERCON-26TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1760 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-26 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERCON-26TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1761 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-26 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERCON-26TODO | 4 |  |  | 0 | $ComStatus , , | #
1762 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-79 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERCON-79TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1763 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-79 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERCON-79TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1764 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-79 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERCON-79TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1765 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-79 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERCON-79TODO | 4 |  |  | 0 | $ComStatus , , | #
1766 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-34 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101WS01DAMPERCON-34TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1767 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-34 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERCON-34TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1768 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-34 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERCON-34TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1769 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-34 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01DAMPERCON-34TODO | 4 |  |  | 0 | $ComStatus , , | #
1770 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-24 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERCON-24TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1771 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-24 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERCON-24TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1772 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-24 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERCON-24TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1773 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-24 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERCON-24TODO | 4 |  |  | 0 | $ComStatus , , | #
1774 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-42 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC101ES01DAMPERCON-42TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1775 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-42 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERCON-42TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1776 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-42 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERCON-42TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1777 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-42 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01DAMPERCON-42TODO | 4 |  |  | 0 | $ComStatus , , | #
1778 | EC101_RTU | TUN:EC101 | WS01:AHU | AHU | PLA-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01AHUPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1779 | EC101_RTU | TUN:EC101 | WS01:AHU | AHU | PLA-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101WS01AHUPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
1780 | EC101_RTU | TUN:EC101 | ES01:AHU | AHU | PLA-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01AHUPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1781 | EC101_RTU | TUN:EC101 | ES01:AHU | AHU | PLA-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101ES01AHUPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
1782 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY DISCONNECTING SWITCH - OPEN
1783 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY VOLTAGE PRESENCE
1784 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER OPEN
1785 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER FAULT
1786 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN
1787 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT
1788 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS OPEN
1789 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS FAULT
1790 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER OPEN
1791 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER FAULT
1792 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER OPEN
1793 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER FAULT
1794 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS DISCONNECTING SWITCH OPEN
1795 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS FAULT
1796 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN
1797 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT
1798 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 ABSENCE OF VOLTAGE
1799 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN
1800 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT
1801 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 ABSENCE OF VOLTAGE
1802 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER OPEN
1803 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER FAULT
1804 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER OPEN
1805 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER FAULT
1806 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER OPEN
1807 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER FAULT
1808 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER OPEN
1809 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER FAULT
1810 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SURGE ARRESTER TRIGGERED
1811 | EC101_RTU | TUN:EC101 | MMS | ADS | EL0-LBS01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL0-LBS01TODO | 4 |  |  | 0 | $ComStatus , , | #
1812 | EC101_RTU | TUN:EC101 | MMS | ADS | EL0-LBS01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL0-LBS01TODO | 4 |  |  | 0 | $ComStatus , , | #
1813 | EC101_RTU | TUN:EC101 | MMS | ADS | EL0-LBS02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL0-LBS02TODO | 4 |  |  | 0 | $ComStatus , , | #
1814 | EC101_RTU | TUN:EC101 | MMS | ADS | EL0-LBS02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL0-LBS02TODO | 4 |  |  | 0 | $ComStatus , , | #
1815 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMV-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
1816 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMV-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
1817 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMV-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
1818 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMV-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
1819 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMV-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
1820 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMV-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
1821 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMV-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
1822 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMV-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
1823 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMV-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
1824 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMV-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
1825 | EC101_RTU | TUN:EC101 | MMS | ACB | EL0-CBC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL0-CBC01TODO | 4 |  |  | 0 | $ComStatus , , | #
1826 | EC101_RTU | TUN:EC101 | MMS | ACB | EL0-CBC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL0-CBC01TODO | 4 |  |  | 0 | $ComStatus , , | #
1827 | EC101_RTU | TUN:EC101 | MMS | ACB | EL0-CBC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL0-CBC01TODO | 4 |  |  | 0 | $ComStatus , , | #
1828 | EC101_RTU | TUN:EC101 | MMS | ACB | EL0-CBC02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL0-CBC02TODO | 4 |  |  | 0 | $ComStatus , , | #
1829 | EC101_RTU | TUN:EC101 | MMS | ACB | EL0-CBC02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL0-CBC02TODO | 4 |  |  | 0 | $ComStatus , , | #
1830 | EC101_RTU | TUN:EC101 | MMS | ACB | EL0-CBC02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL0-CBC02TODO | 4 |  |  | 0 | $ComStatus , , | #
1831 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1832 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1833 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1834 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1835 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1836 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1837 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1838 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1839 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1840 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1841 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1842 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1843 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1844 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1845 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1846 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
1847 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
1848 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
1849 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
1850 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
1851 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
1852 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
1853 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
1854 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
1855 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
1856 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
1857 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
1858 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
1859 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
1860 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
1861 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
1862 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
1863 | EC101_RTU | TUN:EC101 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
1864 | EC101_RTU | TUN:EC101 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
1865 | EC101_RTU | TUN:EC101 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
1866 | EC101_RTU | TUN:EC101 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
1867 | EC101_RTU | TUN:EC101 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
1868 | EC101_RTU | TUN:EC101 | MMS | MCB | EL0-LBS01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL0-LBS01TODO | 4 |  |  | 0 | $ComStatus , , | #
1869 | EC101_RTU | TUN:EC101 | MMS | MCB | EL0-LBS01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL0-LBS01TODO | 4 |  |  | 0 | $ComStatus , , | #
1870 | EC101_RTU | TUN:EC101 | MMS | MCB | EL0-LBS02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL0-LBS02TODO | 4 |  |  | 0 | $ComStatus , , | #
1871 | EC101_RTU | TUN:EC101 | MMS | MCB | EL0-LBS02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL0-LBS02TODO | 4 |  |  | 0 | $ComStatus , , | #
1872 | EC101_RTU | TUN:EC101 | MMS | MCB | EL0-CBC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL0-CBC01TODO | 4 |  |  | 0 | $ComStatus , , | #
1873 | EC101_RTU | TUN:EC101 | MMS | MCB | EL0-CBC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL0-CBC01TODO | 4 |  |  | 0 | $ComStatus , , | #
1874 | EC101_RTU | TUN:EC101 | MMS | MCB | EL0-CBC02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL0-CBC02TODO | 4 |  |  | 0 | $ComStatus , , | #
1875 | EC101_RTU | TUN:EC101 | MMS | MCB | EL0-CBC02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL0-CBC02TODO | 4 |  |  | 0 | $ComStatus , , | #
1876 | EC101_RTU | TUN:EC101 | MMS | MCCB | EL1-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL1-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
1877 | EC101_RTU | TUN:EC101 | MMS | MCCB | EL1-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL1-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
1878 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL0-LBS01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSUPS_EL0-LBS01TODO | 4 |  |  | 0 | $ComStatus , , | #
1879 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL0-LBS01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSUPS_EL0-LBS01TODO | 4 |  |  | 0 | $ComStatus , , | #
1880 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL0-LBS02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSUPS_EL0-LBS02TODO | 4 |  |  | 0 | $ComStatus , , | #
1881 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL0-LBS02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSUPS_EL0-LBS02TODO | 4 |  |  | 0 | $ComStatus , , | #
1882 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL0-CBC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSUPS_EL0-CBC01TODO | 4 |  |  | 0 | $ComStatus , , | #
1883 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL0-CBC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSUPS_EL0-CBC01TODO | 4 |  |  | 0 | $ComStatus , , | #
1884 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL0-CBC02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSUPS_EL0-CBC02TODO | 4 |  |  | 0 | $ComStatus , , | #
1885 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL0-CBC02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSUPS_EL0-CBC02TODO | 4 |  |  | 0 | $ComStatus , , | #
1886 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL1-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSUPS_EL1-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
1887 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL1-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSUPS_EL1-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
1888 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL1-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSUPS_EL1-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
1889 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL1-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSUPS_EL1-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
1890 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1891 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1892 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1893 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1894 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1895 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1896 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1897 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1898 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT6-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT6-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1899 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT6-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT6-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1900 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT6-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT6-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1901 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT6-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT6-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1902 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT6-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT6-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1903 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT6-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT6-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1904 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT6-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT6-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1905 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT6-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT6-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1906 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT6-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT6-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
1907 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT6-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT6-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
1908 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT6-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT6-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
1909 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT6-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT6-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
1910 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P--FR2-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P--FR2-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1911 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P--FR2-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P--FR2-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1912 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P--FR2-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P--FR2-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1913 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P--FR2-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P--FR2-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1914 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P--FR2-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P--FR2-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1915 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P--FR2-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P--FR2-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1916 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P--FR2-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P--FR2-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1917 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P--FR2-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P--FR2-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1918 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-24 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMSFD-CON-24TODO | 4 |  |  | 0 | $ComStatus , , | #
1919 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-24 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMSFD-CON-24TODO | 4 |  |  | 0 | $ComStatus , , | #
1920 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-42 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMSFD-CON-42TODO | 4 |  |  | 0 | $ComStatus , , | #
1921 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-42 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMSFD-CON-42TODO | 4 |  |  | 0 | $ComStatus , , | #
1922 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-33 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMSFD-CON-33TODO | 4 |  |  | 0 | $ComStatus , , | #
1923 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-33 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMSFD-CON-33TODO | 4 |  |  | 0 | $ComStatus , , | #
1924 | EC101_RTU | TUN:EC101 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
1925 | EC101_RTU | TUN:EC101 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
1926 | EC101_RTU | TUN:EC101 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
1927 | EC101_RTU | TUN:EC101 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
1928 | EC101_RTU | TUN:EC101 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
1929 | EC101_RTU | TUN:EC101 | MMS | MCCB | EL2-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL2-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
1930 | EC101_RTU | TUN:EC101 | MMS | MCCB | EL2-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL2-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
1931 | EC101_RTU | TUN:EC101 | MMS | LBS | EL2-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSEL2-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
1932 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL2-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSUPS_EL2-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
1933 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL2-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSUPS_EL2-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
1934 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL2-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSUPS_EL2-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
1935 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL2-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSUPS_EL2-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
1936 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1937 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1938 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1939 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1940 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1941 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1942 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1943 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
1944 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT5-IDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT5-IDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1945 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT5-IDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT5-IDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1946 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT5-IDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT5-IDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1947 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT5-IDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT5-IDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1948 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT5-IDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT5-IDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1949 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT5-IDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT5-IDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1950 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT5-IDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT5-IDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1951 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT5-IDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT5-IDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1952 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT5-IDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT5-IDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
1953 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT5-IDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-VT5-IDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
1954 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT5-IDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT5-IDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
1955 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT5-IDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-VT5-IDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
1956 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-FR1-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-FR1-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1957 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-FR1-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-FR1-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1958 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-FR1-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-FR1-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1959 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-FR1-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-FR1-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
1960 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-FR1-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-FR1-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1961 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-FR1-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS3P-FR1-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1962 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-FR1-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-FR1-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1963 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-FR1-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMS2P-FR1-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
1964 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-79 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMSFD-CON-79TODO | 4 |  |  | 0 | $ComStatus , , | #
1965 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-79 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMSFD-CON-79TODO | 4 |  |  | 0 | $ComStatus , , | #
1966 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-34 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMSFD-CON-34TODO | 4 |  |  | 0 | $ComStatus , , | #
1967 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-34 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMSFD-CON-34TODO | 4 |  |  | 0 | $ComStatus , , | #
1968 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-68 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMSFD-CON-68TODO | 4 |  |  | 0 | $ComStatus , , | #
1969 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-68 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC101MMSMSFD-CON-68TODO | 4 |  |  | 0 | $ComStatus , , | #
1970 | EC10A_RTU | TUN:EC10A | SCR | LCP | LCP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASCRLCP01TODO | 4 |  |  | 0 | $ComStatus , , | #COMMUNICATION FAULT WITH PLC
1971 | EC10A_RTU | TUN:EC10A | SCR | LCP | LCP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASCRLCP01TODO | 4 |  |  | 0 | $ComStatus , , | #LOCAL / REMOTE STATUS
1972 | EC10A_RTU | TUN:EC10A | SCR | FMOP | FMOP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASCRFMOP01TODO | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
1973 | EC10A_RTU | TUN:EC10A | SCR | FMOP | FMOP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASCRFMOP01TODO | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
1974 | EC10A_RTU | TUN:EC10A | SCR | FMOP | FMOP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASCRFMOP01TODO | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
1975 | EC10A_RTU | TUN:EC10A | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B OFFLINE
1976 | EC10A_RTU | TUN:EC10A | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC RUNNING.
1977 | EC10A_RTU | TUN:EC10A | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: POWER SUPPLY FAULT
1978 | EC10A_RTU | TUN:EC10A | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CPU MODULE FAULT
1979 | EC10A_RTU | TUN:EC10A | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CRP MODULE FAULT
1980 | EC10A_RTU | TUN:EC10A | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
1981 | EC10A_RTU | TUN:EC10A | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
1982 | EC10A_RTU | TUN:EC10A | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
1983 | EC10A_RTU | TUN:EC10A | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
1984 | EC10A_RTU | TUN:EC10A | TEL | SWI | SWI01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATELSWI01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH FAULT
1985 | EC10A_RTU | TUN:EC10A | OTS | OTS | OTS001 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AOTSOTS001TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1986 | EC10A_RTU | TUN:EC10A | OTS | OTS | OTS001 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AOTSOTS001TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1987 | EC10A_RTU | TUN:EC10A | OTS | OTS | OTS001 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC10AOTSOTS001TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1988 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100421 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASENSORTS100421TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1989 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100421 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASENSORTS100421TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1990 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100421 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASENSORTS100421TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1991 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100421 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASENSORTS100421TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1992 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100421 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC10ASENSORTS100421TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1993 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100421 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC10ASENSORTS100421TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1994 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100521 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASENSORTS100521TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1995 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100521 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASENSORTS100521TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1996 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100521 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASENSORTS100521TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1997 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100521 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASENSORTS100521TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1998 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100521 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC10ASENSORTS100521TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1999 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100521 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC10ASENSORTS100521TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
2000 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100767 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASENSORTS100767TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
2001 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100767 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASENSORTS100767TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
2002 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100767 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASENSORTS100767TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
2003 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100767 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASENSORTS100767TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
2004 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100767 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC10ASENSORTS100767TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
2005 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100767 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC10ASENSORTS100767TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
2006 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100906 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASENSORTS100906TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
2007 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100906 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASENSORTS100906TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
2008 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100906 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASENSORTS100906TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
2009 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100906 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASENSORTS100906TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
2010 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100906 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC10ASENSORTS100906TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
2011 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100906 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC10ASENSORTS100906TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
2012 | EC10A_RTU | TUN:EC10A | SENSOR | VS | VS100456 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASENSORVS100456TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
2013 | EC10A_RTU | TUN:EC10A | SENSOR | VS | VS100456 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC10ASENSORVS100456TODO | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
2014 | EC10A_RTU | TUN:EC10A | SENSOR | VS | VS100862 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ASENSORVS100862TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
2015 | EC10A_RTU | TUN:EC10A | SENSOR | VS | VS100862 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC10ASENSORVS100862TODO | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
2016 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2017 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2018 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
2019 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2020 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2021 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2022 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2023 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2024 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
2025 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
2026 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
2027 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
2028 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
2029 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2030 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2031 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2032 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2033 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
2034 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
2035 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
2036 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
2037 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
2038 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
2039 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
2040 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
2041 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
2042 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
2043 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
2044 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
2045 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
2046 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
2047 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
2048 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
2049 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
2050 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
2051 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
2052 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
2053 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
2054 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
2055 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNEC10ATVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
2056 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2057 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2058 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
2059 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2060 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2061 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2062 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2063 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2064 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
2065 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
2066 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
2067 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
2068 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
2069 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2070 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2071 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2072 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2073 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
2074 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
2075 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
2076 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
2077 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
2078 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
2079 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
2080 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
2081 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
2082 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
2083 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
2084 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
2085 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
2086 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
2087 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
2088 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
2089 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
2090 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
2091 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
2092 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
2093 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
2094 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
2095 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNEC10ATVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
2096 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ADAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2097 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ADAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2098 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ADAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
2099 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ADAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
2100 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ADAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2101 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ADAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2102 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ADAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2103 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10ADAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2104 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ADAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
2105 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ADAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
2106 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ADAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2107 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10ADAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2108 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10APFALPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2109 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10APFALPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2110 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10APFALPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
2111 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10APFALPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2112 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10APFALPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2113 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10APFALPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2114 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10APFALPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2115 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10APFALPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2116 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10APFALPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2117 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10APFALPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2118 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10APFALPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2119 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10APFALPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2120 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10APFALPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2121 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10APFALPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2122 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10APFALPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2123 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10APFALPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2124 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10APFALPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2125 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10APFALPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2126 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10APFASPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2127 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10APFASPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2128 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10APFASPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
2129 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10APFASPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2130 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10APFASPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2131 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10APFASPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2132 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10APFASPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2133 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10APFASPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2134 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10APFASPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2135 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10APFASPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2136 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10APFASPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2137 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10APFASPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2138 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10APFASPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2139 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10APFASPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2140 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNEC10APFASPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2141 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNEC10APFASPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2142 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10APFASPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2143 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10APFASPF-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2144 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY DISCONNECTING SWITCH - OPEN
2145 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY VOLTAGE PRESENCE
2146 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER OPEN
2147 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER FAULT
2148 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN
2149 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT
2150 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS OPEN
2151 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS FAULT
2152 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER OPEN
2153 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER FAULT
2154 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER OPEN
2155 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER FAULT
2156 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS DISCONNECTING SWITCH OPEN
2157 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS FAULT
2158 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN
2159 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT
2160 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 ABSENCE OF VOLTAGE
2161 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN
2162 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT
2163 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 ABSENCE OF VOLTAGE
2164 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER OPEN
2165 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER FAULT
2166 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER OPEN
2167 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER FAULT
2168 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER OPEN
2169 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER FAULT
2170 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER OPEN
2171 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER FAULT
2172 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SURGE ARRESTER TRIGGERED
2173 | EC10A_RTU | TUN:EC10A | MMS | ADS | EL3-LBW01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-LBW01TODO | 4 |  |  | 0 | $ComStatus , , | #
2174 | EC10A_RTU | TUN:EC10A | MMS | ADS | EL3-LBW01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-LBW01TODO | 4 |  |  | 0 | $ComStatus , , | #
2175 | EC10A_RTU | TUN:EC10A | MMS | ADS | EL3-LBW02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-LBW02TODO | 4 |  |  | 0 | $ComStatus , , | #
2176 | EC10A_RTU | TUN:EC10A | MMS | ADS | EL3-LBW02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-LBW02TODO | 4 |  |  | 0 | $ComStatus , , | #
2177 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
2178 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
2179 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
2180 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
2181 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-TRF01TODO | 4 |  |  | 0 | $ComStatus , , | #
2182 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
2183 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
2184 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
2185 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
2186 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-TRF02TODO | 4 |  |  | 0 | $ComStatus , , | #
2187 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2188 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2189 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2190 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2191 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2192 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2193 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2194 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2195 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2196 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2197 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2198 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2199 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2200 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2201 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2202 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2203 | EC10A_RTU | TUN:EC10A | MMS | EL | EL3-PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-PLC01TODO | 4 |  |  | 0 | $ComStatus , , | #
2204 | EC10A_RTU | TUN:EC10A | MMS | EL | EL3-PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-PLC01TODO | 4 |  |  | 0 | $ComStatus , , | #
2205 | EC10A_RTU | TUN:EC10A | MMS | EL | EL3-PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-PLC01TODO | 4 |  |  | 0 | $ComStatus , , | #
2206 | EC10A_RTU | TUN:EC10A | MMS | EL | EL3-PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-PLC01TODO | 4 |  |  | 0 | $ComStatus , , | #
2207 | EC10A_RTU | TUN:EC10A | MMS | EL | EL3-PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-PLC01TODO | 4 |  |  | 0 | $ComStatus , , | #
2208 | EC10A_RTU | TUN:EC10A | MMS | MCB | EL3-LBW01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-LBW01TODO | 4 |  |  | 0 | $ComStatus , , | #
2209 | EC10A_RTU | TUN:EC10A | MMS | MCB | EL3-LBW01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-LBW01TODO | 4 |  |  | 0 | $ComStatus , , | #
2210 | EC10A_RTU | TUN:EC10A | MMS | MCB | EL3-LBW02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-LBW02TODO | 4 |  |  | 0 | $ComStatus , , | #
2211 | EC10A_RTU | TUN:EC10A | MMS | MCB | EL3-LBW02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-LBW02TODO | 4 |  |  | 0 | $ComStatus , , | #
2212 | EC10A_RTU | TUN:EC10A | MMS | MCCB | EL3-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
2213 | EC10A_RTU | TUN:EC10A | MMS | MCCB | EL3-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
2214 | EC10A_RTU | TUN:EC10A | MMS | LBS | EL3-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSEL3-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
2215 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSUPS_EL3-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
2216 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSUPS_EL3-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
2217 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSUPS_EL3-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
2218 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSUPS_EL3-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
2219 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-LBW01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSUPS_EL3-LBW01TODO | 4 |  |  | 0 | $ComStatus , , | #
2220 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-LBW01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSUPS_EL3-LBW01TODO | 4 |  |  | 0 | $ComStatus , , | #
2221 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-LBW02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSUPS_EL3-LBW02TODO | 4 |  |  | 0 | $ComStatus , , | #
2222 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-LBW02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSUPS_EL3-LBW02TODO | 4 |  |  | 0 | $ComStatus , , | #
2223 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSUPS_EL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2224 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMSUPS_EL3-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2225 | EC10A_RTU | TUN:EC10A | MMS | MCB | 3P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMS3P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2226 | EC10A_RTU | TUN:EC10A | MMS | MCB | 3P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMS3P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2227 | EC10A_RTU | TUN:EC10A | MMS | MCB | 2P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMS2P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2228 | EC10A_RTU | TUN:EC10A | MMS | MCB | 2P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMS2P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2229 | EC10A_RTU | TUN:EC10A | MMS | MCB | 3P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMS3P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2230 | EC10A_RTU | TUN:EC10A | MMS | MCB | 3P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMS3P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2231 | EC10A_RTU | TUN:EC10A | MMS | MCB | 2P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMS2P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2232 | EC10A_RTU | TUN:EC10A | MMS | MCB | 2P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNEC10AMMS2P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2233 | QAP01_RTU | TUN:QAP01 | SCR | LCP | LCP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SCRLCP01TODO | 4 |  |  | 0 | $ComStatus , , | #COMMUNICATION FAULT WITH PLC
2234 | QAP01_RTU | TUN:QAP01 | SCR | LCP | LCP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SCRLCP01TODO | 4 |  |  | 0 | $ComStatus , , | #LOCAL / REMOTE STATUS
2235 | QAP01_RTU | TUN:QAP01 | SCR | FMOP | FMOP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SCRFMOP01TODO | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
2236 | QAP01_RTU | TUN:QAP01 | SCR | FMOP | FMOP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SCRFMOP01TODO | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
2237 | QAP01_RTU | TUN:QAP01 | SCR | FMOP | FMOP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SCRFMOP01TODO | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
2238 | QAP01_RTU | TUN:QAP01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B OFFLINE
2239 | QAP01_RTU | TUN:QAP01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC RUNNING.
2240 | QAP01_RTU | TUN:QAP01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: POWER SUPPLY FAULT
2241 | QAP01_RTU | TUN:QAP01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CPU MODULE FAULT
2242 | QAP01_RTU | TUN:QAP01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CRP MODULE FAULT
2243 | QAP01_RTU | TUN:QAP01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
2244 | QAP01_RTU | TUN:QAP01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
2245 | QAP01_RTU | TUN:QAP01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
2246 | QAP01_RTU | TUN:QAP01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
2247 | QAP01_RTU | TUN:QAP01 | TEL | SWI | SWI01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01TELSWI01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH FAULT
2248 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2249 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2250 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
2251 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2252 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2253 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2254 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2255 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2256 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2257 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2258 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2259 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2260 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2261 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2262 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2263 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2264 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2265 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2266 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2267 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2268 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
2269 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2270 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2271 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2272 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2273 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2274 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2275 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2276 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2277 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2278 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2279 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2280 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2281 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2282 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2283 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2284 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFACON-02TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2285 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFACON-02TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2286 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFACON-02TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
2287 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-02TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2288 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-02TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2289 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFACON-02TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2290 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-02TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2291 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFACON-02TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2292 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-02TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2293 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFACON-02TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2294 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-02TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2295 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFACON-02TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2296 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-02TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2297 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFACON-02TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2298 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-02TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2299 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFACON-02TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2300 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFACON-02TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2301 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFACON-02TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2302 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2303 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2304 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
2305 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2306 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2307 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2308 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2309 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2310 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2311 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2312 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2313 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2314 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2315 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2316 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2317 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2318 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2319 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2320 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2321 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2322 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
2323 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2324 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2325 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2326 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2327 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2328 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2329 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2330 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2331 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2332 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2333 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2334 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2335 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2336 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2337 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2338 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFACON-05TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2339 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFACON-05TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2340 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFACON-05TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
2341 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-05TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2342 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-05TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2343 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFACON-05TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2344 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-05TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2345 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFACON-05TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2346 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-05TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2347 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFACON-05TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2348 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-05TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2349 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFACON-05TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2350 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-05TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2351 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFACON-05TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2352 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01PFACON-05TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2353 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01PFACON-05TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2354 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFACON-05TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2355 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01PFACON-05TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2356 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SMCSMC01TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
2357 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC02 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SMCSMC02TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
2358 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SMCSMC03TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
2359 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SMCSMC04TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
2360 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC05 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SMCSMC05TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
2361 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC06 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SMCSMC06TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
2362 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC07 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SMCSMC07TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
2363 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC08 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SMCSMC08TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
2364 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC09 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SMCSMC09TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
2365 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC10 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SMCSMC10TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
2366 | QAP01_RTU | TUN:QAP01 | SED | SED | SED01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SEDSED01TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
2367 | QAP01_RTU | TUN:QAP01 | SED | SED | SED01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SEDSED01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
2368 | QAP01_RTU | TUN:QAP01 | SED | SED | SED02 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SEDSED02TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
2369 | QAP01_RTU | TUN:QAP01 | SED | SED | SED02 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SEDSED02TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
2370 | QAP01_RTU | TUN:QAP01 | SED | SED | SED03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SEDSED03TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
2371 | QAP01_RTU | TUN:QAP01 | SED | SED | SED03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SEDSED03TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
2372 | QAP01_RTU | TUN:QAP01 | SED | SED | SED04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SEDSED04TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
2373 | QAP01_RTU | TUN:QAP01 | SED | SED | SED04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SEDSED04TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
2374 | QAP01_RTU | TUN:QAP01 | OTS | OTS | OTS001 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01OTSOTS001TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
2375 | QAP01_RTU | TUN:QAP01 | OTS | OTS | OTS001 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01OTSOTS001TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
2376 | QAP01_RTU | TUN:QAP01 | OTS | OTS | OTS001 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQAP01OTSOTS001TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
2377 | QAP01_RTU | TUN:QAP01 | OTS | OTS | OTS002 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01OTSOTS002TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
2378 | QAP01_RTU | TUN:QAP01 | OTS | OTS | OTS002 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01OTSOTS002TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
2379 | QAP01_RTU | TUN:QAP01 | OTS | OTS | OTS002 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQAP01OTSOTS002TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
2380 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2381 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2382 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
2383 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2384 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2385 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2386 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2387 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2388 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
2389 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
2390 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
2391 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
2392 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
2393 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2394 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2395 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2396 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2397 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
2398 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
2399 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
2400 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
2401 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
2402 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
2403 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
2404 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
2405 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
2406 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
2407 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
2408 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
2409 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
2410 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
2411 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
2412 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
2413 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
2414 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
2415 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
2416 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
2417 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
2418 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
2419 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNQAP01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
2420 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2421 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2422 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
2423 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2424 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2425 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2426 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2427 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2428 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
2429 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
2430 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
2431 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
2432 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
2433 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2434 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2435 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2436 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2437 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
2438 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
2439 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
2440 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
2441 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
2442 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
2443 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
2444 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
2445 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
2446 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
2447 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
2448 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
2449 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
2450 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
2451 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
2452 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
2453 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
2454 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
2455 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
2456 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
2457 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
2458 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
2459 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNQAP01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
2460 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2461 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2462 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
2463 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2464 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2465 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2466 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2467 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2468 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
2469 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
2470 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
2471 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
2472 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
2473 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2474 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2475 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2476 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2477 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
2478 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
2479 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
2480 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
2481 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
2482 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
2483 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
2484 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
2485 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
2486 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
2487 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
2488 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
2489 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
2490 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
2491 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
2492 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
2493 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
2494 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
2495 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
2496 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
2497 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
2498 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
2499 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNQAP01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
2500 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2501 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2502 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
2503 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2504 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2505 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2506 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2507 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2508 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
2509 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
2510 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
2511 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
2512 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
2513 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2514 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2515 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2516 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2517 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
2518 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
2519 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
2520 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
2521 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
2522 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
2523 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
2524 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
2525 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
2526 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
2527 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
2528 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
2529 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
2530 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
2531 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
2532 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
2533 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
2534 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
2535 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
2536 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
2537 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
2538 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
2539 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNQAP01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
2540 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01SENSORTS101733TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
2541 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01SENSORTS101733TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
2542 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01SENSORTS101733TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
2543 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01SENSORTS101733TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
2544 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQAP01SS01SENSORTS101733TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
2545 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQAP01SS01SENSORTS101733TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
2546 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01SENSORTS101817TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
2547 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01SENSORTS101817TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
2548 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01SENSORTS101817TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
2549 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01SENSORTS101817TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
2550 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQAP01SS01SENSORTS101817TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
2551 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQAP01SS01SENSORTS101817TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
2552 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01SENSORTS102057TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
2553 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01SENSORTS102057TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
2554 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01SENSORTS102057TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
2555 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01SENSORTS102057TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
2556 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQAP01NS01SENSORTS102057TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
2557 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQAP01NS01SENSORTS102057TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
2558 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01SENSORTS102121TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
2559 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01SENSORTS102121TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
2560 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01SENSORTS102121TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
2561 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01SENSORTS102121TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
2562 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQAP01NS01SENSORTS102121TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
2563 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQAP01NS01SENSORTS102121TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
2564 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | VS | VS101763 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01SENSORVS101763TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
2565 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | VS | VS101763 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQAP01SS01SENSORVS101763TODO | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
2566 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | VS | VS102092 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01SENSORVS102092TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
2567 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | VS | VS102092 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQAP01NS01SENSORVS102092TODO | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
2568 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2569 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2570 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2571 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2572 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2573 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2574 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2575 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2576 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
2577 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
2578 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
2579 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
2580 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
2581 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
2582 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
2583 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
2584 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
2585 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
2586 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2587 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2588 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2589 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2590 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2591 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2592 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2593 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2594 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2595 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2596 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
2597 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
2598 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
2599 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
2600 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
2601 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
2602 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
2603 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
2604 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
2605 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
2606 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2607 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2608 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2609 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2610 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
2611 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
2612 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2613 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2614 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2615 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2616 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
2617 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
2618 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2619 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2620 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2621 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2622 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
2623 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
2624 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2625 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2626 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2627 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2628 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
2629 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
2630 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2631 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2632 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2633 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2634 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2635 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2636 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2637 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2638 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2639 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2640 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
2641 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
2642 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
2643 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
2644 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
2645 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
2646 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
2647 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
2648 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
2649 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
2650 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2651 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2652 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2653 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2654 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2655 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2656 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2657 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2658 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2659 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2660 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
2661 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
2662 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
2663 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
2664 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
2665 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
2666 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
2667 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
2668 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
2669 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
2670 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2671 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2672 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-63 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERCON-63TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2673 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-63 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERCON-63TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2674 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-63 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERCON-63TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2675 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-63 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERCON-63TODO | 4 |  |  | 0 | $ComStatus , , | #
2676 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-54 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERCON-54TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2677 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-54 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERCON-54TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2678 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-54 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERCON-54TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2679 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-54 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERCON-54TODO | 4 |  |  | 0 | $ComStatus , , | #
2680 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-66 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERCON-66TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2681 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-66 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERCON-66TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2682 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-66 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERCON-66TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2683 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-66 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERCON-66TODO | 4 |  |  | 0 | $ComStatus , , | #
2684 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-61 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERCON-61TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2685 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-61 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERCON-61TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2686 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-61 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERCON-61TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2687 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-61 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERCON-61TODO | 4 |  |  | 0 | $ComStatus , , | #
2688 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-56 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERCON-56TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2689 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-56 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERCON-56TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2690 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-56 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERCON-56TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2691 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-56 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERCON-56TODO | 4 |  |  | 0 | $ComStatus , , | #
2692 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-51 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERCON-51TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2693 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-51 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERCON-51TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2694 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-51 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERCON-51TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2695 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-51 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERCON-51TODO | 4 |  |  | 0 | $ComStatus , , | #
2696 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-67 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERCON-67TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2697 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-67 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERCON-67TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2698 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-67 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERCON-67TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2699 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-67 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERCON-67TODO | 4 |  |  | 0 | $ComStatus , , | #
2700 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-59 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01SS01DAMPERCON-59TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2701 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-59 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERCON-59TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2702 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-59 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERCON-59TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2703 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-59 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01DAMPERCON-59TODO | 4 |  |  | 0 | $ComStatus , , | #
2704 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-58 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERCON-58TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2705 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-58 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERCON-58TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2706 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-58 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERCON-58TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2707 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-58 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERCON-58TODO | 4 |  |  | 0 | $ComStatus , , | #
2708 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-52 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQAP01NS01DAMPERCON-52TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2709 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-52 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERCON-52TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2710 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-52 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERCON-52TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2711 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-52 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01DAMPERCON-52TODO | 4 |  |  | 0 | $ComStatus , , | #
2712 | QAP01_RTU | TUN:QAP01 | SS01:AHU | AHU | CON-08 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01AHUCON-08TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2713 | QAP01_RTU | TUN:QAP01 | SS01:AHU | AHU | CON-08 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01AHUCON-08TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
2714 | QAP01_RTU | TUN:QAP01 | SS01:AHU | AHU | CON-07 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01AHUCON-07TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2715 | QAP01_RTU | TUN:QAP01 | SS01:AHU | AHU | CON-07 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01SS01AHUCON-07TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
2716 | QAP01_RTU | TUN:QAP01 | NS01:AHU | AHU | CON-06 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01AHUCON-06TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2717 | QAP01_RTU | TUN:QAP01 | NS01:AHU | AHU | CON-06 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01AHUCON-06TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
2718 | QAP01_RTU | TUN:QAP01 | NS01:AHU | AHU | CON-05 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01AHUCON-05TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2719 | QAP01_RTU | TUN:QAP01 | NS01:AHU | AHU | CON-05 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01NS01AHUCON-05TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
2720 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY DISCONNECTING SWITCH - OPEN
2721 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY VOLTAGE PRESENCE
2722 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER OPEN
2723 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER FAULT
2724 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN
2725 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT
2726 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS OPEN
2727 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS FAULT
2728 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER OPEN
2729 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER FAULT
2730 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER OPEN
2731 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER FAULT
2732 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS DISCONNECTING SWITCH OPEN
2733 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS FAULT
2734 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN
2735 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT
2736 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 ABSENCE OF VOLTAGE
2737 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN
2738 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT
2739 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 ABSENCE OF VOLTAGE
2740 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER OPEN
2741 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER FAULT
2742 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER OPEN
2743 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER FAULT
2744 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER OPEN
2745 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER FAULT
2746 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER OPEN
2747 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER FAULT
2748 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SURGE ARRESTER TRIGGERED
2749 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2750 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2751 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2752 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2753 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2754 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2755 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2756 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2757 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2758 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2759 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2760 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2761 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2762 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2763 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2764 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
2765 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
2766 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
2767 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
2768 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
2769 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
2770 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
2771 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
2772 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
2773 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
2774 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
2775 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
2776 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
2777 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
2778 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
2779 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
2780 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
2781 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
2782 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
2783 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
2784 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
2785 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
2786 | QAP01_RTU | TUN:QAP01 | MMS | MCCB | EL1-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSEL1-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
2787 | QAP01_RTU | TUN:QAP01 | MMS | MCCB | EL1-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSEL1-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
2788 | QAP01_RTU | TUN:QAP01 | MMS | LBS | EL1-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSEL1-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
2789 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL1-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSUPS_EL1-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
2790 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL1-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSUPS_EL1-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
2791 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL1-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSUPS_EL1-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
2792 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL1-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSUPS_EL1-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
2793 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2794 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2795 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2796 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2797 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2798 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2799 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2800 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2801 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT6-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
2802 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT6-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
2803 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT6-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
2804 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT6-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
2805 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT6-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
2806 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT6-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
2807 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT6-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
2808 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT6-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
2809 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT6-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
2810 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT6-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
2811 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT6-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
2812 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT6-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
2813 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P--FR2-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P--FR2-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
2814 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P--FR2-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P--FR2-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
2815 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P--FR2-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P--FR2-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
2816 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P--FR2-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P--FR2-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
2817 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P--FR2-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P--FR2-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
2818 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P--FR2-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P--FR2-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
2819 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P--FR2-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P--FR2-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
2820 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P--FR2-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P--FR2-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
2821 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-54 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSMSFD-CON-54TODO | 4 |  |  | 0 | $ComStatus , , | #
2822 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-54 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSMSFD-CON-54TODO | 4 |  |  | 0 | $ComStatus , , | #
2823 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-52 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSMSFD-CON-52TODO | 4 |  |  | 0 | $ComStatus , , | #
2824 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-52 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSMSFD-CON-52TODO | 4 |  |  | 0 | $ComStatus , , | #
2825 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-58 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSMSFD-CON-58TODO | 4 |  |  | 0 | $ComStatus , , | #
2826 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-58 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSMSFD-CON-58TODO | 4 |  |  | 0 | $ComStatus , , | #
2827 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
2828 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
2829 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
2830 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
2831 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
2832 | QAP01_RTU | TUN:QAP01 | MMS | MCCB | EL2-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSEL2-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
2833 | QAP01_RTU | TUN:QAP01 | MMS | MCCB | EL2-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSEL2-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
2834 | QAP01_RTU | TUN:QAP01 | MMS | LBS | EL2-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSEL2-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
2835 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL2-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSUPS_EL2-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
2836 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL2-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSUPS_EL2-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
2837 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL2-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSUPS_EL2-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
2838 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL2-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSUPS_EL2-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
2839 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2840 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2841 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2842 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2843 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2844 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2845 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2846 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
2847 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT5-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
2848 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT5-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
2849 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT5-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
2850 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT5-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
2851 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT5-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
2852 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT5-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
2853 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT5-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
2854 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT5-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
2855 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT5-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
2856 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-VT5-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
2857 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT5-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
2858 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-VT5-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
2859 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-FR1-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-FR1-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
2860 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-FR1-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-FR1-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
2861 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-FR1-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-FR1-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
2862 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-FR1-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-FR1-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
2863 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-FR1-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-FR1-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
2864 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-FR1-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS3P-FR1-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
2865 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-FR1-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-FR1-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
2866 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-FR1-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMS2P-FR1-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
2867 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-63 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSMSFD-CON-63TODO | 4 |  |  | 0 | $ComStatus , , | #
2868 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-63 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSMSFD-CON-63TODO | 4 |  |  | 0 | $ComStatus , , | #
2869 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-59 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSMSFD-CON-59TODO | 4 |  |  | 0 | $ComStatus , , | #
2870 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-59 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSMSFD-CON-59TODO | 4 |  |  | 0 | $ComStatus , , | #
2871 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-67 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSMSFD-CON-67TODO | 4 |  |  | 0 | $ComStatus , , | #
2872 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-67 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQAP01MMSMSFD-CON-67TODO | 4 |  |  | 0 | $ComStatus , , | #
2873 | QEC01_RTU | TUN:QEC01 | SCR | LCP | LCP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SCRLCP01TODO | 4 |  |  | 0 | $ComStatus , , | #COMMUNICATION FAULT WITH PLC
2874 | QEC01_RTU | TUN:QEC01 | SCR | LCP | LCP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SCRLCP01TODO | 4 |  |  | 0 | $ComStatus , , | #LOCAL / REMOTE STATUS
2875 | QEC01_RTU | TUN:QEC01 | SCR | FMOP | FMOP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SCRFMOP01TODO | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
2876 | QEC01_RTU | TUN:QEC01 | SCR | FMOP | FMOP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SCRFMOP01TODO | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
2877 | QEC01_RTU | TUN:QEC01 | SCR | FMOP | FMOP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SCRFMOP01TODO | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
2878 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B OFFLINE
2879 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC RUNNING.
2880 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: POWER SUPPLY FAULT
2881 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CPU MODULE FAULT
2882 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CRP MODULE FAULT
2883 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
2884 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
2885 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
2886 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01TELPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
2887 | QEC01_RTU | TUN:QEC01 | TEL | SWI | SWI01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01TELSWI01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH FAULT
2888 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2889 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2890 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
2891 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2892 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2893 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2894 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2895 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2896 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2897 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2898 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2899 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2900 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2901 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2902 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2903 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2904 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2905 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01PFAPLA-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2906 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2907 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2908 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
2909 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2910 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2911 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2912 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2913 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2914 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2915 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2916 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2917 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2918 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2919 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2920 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2921 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2922 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2923 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01PFAGRD-01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2924 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFAPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2925 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFAPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2926 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFAPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
2927 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFAPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2928 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFAPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2929 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFAPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2930 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFAPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2931 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFAPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2932 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFAPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2933 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFAPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2934 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFAPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2935 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFAPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2936 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFAPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2937 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFAPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2938 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFAPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2939 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFAPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2940 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFAPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2941 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFAPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2942 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2943 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2944 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
2945 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2946 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2947 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2948 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2949 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2950 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2951 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2952 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2953 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2954 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2955 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2956 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2957 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2958 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2959 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFACON-04TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2960 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2961 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2962 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
2963 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2964 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2965 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2966 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2967 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2968 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2969 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2970 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2971 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2972 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2973 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2974 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2975 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2976 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2977 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFACON-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2978 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2979 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2980 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
2981 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2982 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2983 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2984 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2985 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2986 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2987 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2988 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2989 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2990 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2991 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2992 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2993 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2994 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2995 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01PFAGRD-03TODO | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2996 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SMCSMC01TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
2997 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC02 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SMCSMC02TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
2998 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SMCSMC03TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
2999 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SMCSMC04TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
3000 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC05 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SMCSMC05TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
3001 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC06 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SMCSMC06TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
3002 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC07 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SMCSMC07TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
3003 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC08 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SMCSMC08TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
3004 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC09 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SMCSMC09TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
3005 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC10 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SMCSMC10TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
3006 | QEC01_RTU | TUN:QEC01 | SED | SED | SED01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SEDSED01TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
3007 | QEC01_RTU | TUN:QEC01 | SED | SED | SED01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SEDSED01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
3008 | QEC01_RTU | TUN:QEC01 | SED | SED | SED02 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SEDSED02TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
3009 | QEC01_RTU | TUN:QEC01 | SED | SED | SED02 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SEDSED02TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
3010 | QEC01_RTU | TUN:QEC01 | SED | SED | SED03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SEDSED03TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
3011 | QEC01_RTU | TUN:QEC01 | SED | SED | SED03 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SEDSED03TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
3012 | QEC01_RTU | TUN:QEC01 | SED | SED | SED04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SEDSED04TODO | 4 |  |  | 0 | $ComStatus , , | #STATE
3013 | QEC01_RTU | TUN:QEC01 | SED | SED | SED04 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SEDSED04TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
3014 | QEC01_RTU | TUN:QEC01 | OTS | OTS | OTS001 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01OTSOTS001TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3015 | QEC01_RTU | TUN:QEC01 | OTS | OTS | OTS001 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01OTSOTS001TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3016 | QEC01_RTU | TUN:QEC01 | OTS | OTS | OTS001 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01OTSOTS001TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3017 | QEC01_RTU | TUN:QEC01 | OTS | OTS | OTS002 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01OTSOTS002TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3018 | QEC01_RTU | TUN:QEC01 | OTS | OTS | OTS002 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01OTSOTS002TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3019 | QEC01_RTU | TUN:QEC01 | OTS | OTS | OTS002 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01OTSOTS002TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3020 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3021 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3022 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3023 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3024 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3025 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3026 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3027 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3028 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3029 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3030 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3031 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3032 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3033 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3034 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3035 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3036 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3037 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3038 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3039 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3040 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3041 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3042 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3043 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3044 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3045 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3046 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3047 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3048 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3049 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3050 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3051 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3052 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3053 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3054 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3055 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3056 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3057 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
3058 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3059 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNQEC01SS01TVFVT1-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3060 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3061 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3062 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3063 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3064 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3065 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3066 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3067 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3068 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3069 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3070 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3071 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3072 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3073 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3074 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3075 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3076 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3077 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3078 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3079 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3080 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3081 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3082 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3083 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3084 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3085 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3086 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3087 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3088 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3089 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3090 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3091 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3092 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3093 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3094 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3095 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3096 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3097 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
3098 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3099 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNQEC01SS01TVFVT2-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3100 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3101 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3102 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3103 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3104 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3105 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3106 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3107 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3108 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3109 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3110 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3111 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3112 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3113 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3114 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3115 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3116 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3117 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3118 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3119 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3120 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3121 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3122 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3123 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3124 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3125 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3126 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3127 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3128 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3129 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3130 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3131 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3132 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3133 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3134 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3135 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3136 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3137 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
3138 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3139 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNQEC01NS01TVFVT3-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3140 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3141 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3142 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3143 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3144 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3145 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3146 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3147 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3148 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3149 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3150 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3151 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3152 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 2 | deoTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3153 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3154 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3155 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3156 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3157 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3158 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3159 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3160 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3161 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3162 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3163 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3164 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3165 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3166 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3167 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3168 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3169 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3170 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3171 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3172 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3173 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3174 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3175 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3176 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3177 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
3178 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3179 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNQEC01NS01TVFVT4-TVF01TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3180 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01SENSORTS101871TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3181 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01SENSORTS101871TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3182 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01SENSORTS101871TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3183 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01SENSORTS101871TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3184 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01SS01SENSORTS101871TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3185 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01SS01SENSORTS101871TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3186 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01SENSORTS101984TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3187 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01SENSORTS101984TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3188 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01SENSORTS101984TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3189 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01SENSORTS101984TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3190 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01SS01SENSORTS101984TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3191 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01SS01SENSORTS101984TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3192 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS102441TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3193 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS102441TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3194 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS102441TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3195 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS102441TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3196 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORTS102441TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3197 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORTS102441TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3198 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS102499TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3199 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS102499TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3200 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS102499TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3201 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS102499TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3202 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORTS102499TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3203 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORTS102499TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3204 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS102261TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3205 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS102261TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3206 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS102261TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3207 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS102261TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3208 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORTS102261TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3209 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORTS102261TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3210 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100023TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3211 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100023TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3212 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100023TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3213 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100023TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3214 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORTS100023TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3215 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORTS100023TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3216 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100062TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3217 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100062TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3218 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100062TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3219 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100062TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3220 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORTS100062TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3221 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORTS100062TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3222 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100108TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3223 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100108TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3224 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100108TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3225 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100108TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3226 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORTS100108TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3227 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORTS100108TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3228 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100230TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3229 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100230TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3230 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100230TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3231 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100230TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3232 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORTS100230TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3233 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORTS100230TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3234 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100335TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3235 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100335TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3236 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100335TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3237 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORTS100335TODO | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3238 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORTS100335TODO | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3239 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORTS100335TODO | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3240 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | VS | VS101909 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01SENSORVS101909TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3241 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | VS | VS101909 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01SS01SENSORVS101909TODO | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
3242 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS102357 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORVS102357TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3243 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS102357 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORVS102357TODO | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
3244 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS102467 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORVS102467TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3245 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS102467 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORVS102467TODO | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
3246 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS102276 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORVS102276TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3247 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS102276 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORVS102276TODO | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
3248 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS100080 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORVS100080TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3249 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS100080 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORVS100080TODO | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
3250 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS100285 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01SENSORVS100285TODO | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3251 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS100285 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01NS01SENSORVS100285TODO | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
3252 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3253 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3254 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3255 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3256 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3257 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3258 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3259 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3260 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
3261 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
3262 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
3263 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
3264 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
3265 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
3266 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
3267 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
3268 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
3269 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
3270 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
3271 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERVT5-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
3272 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3273 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3274 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3275 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3276 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3277 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3278 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3279 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3280 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
3281 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
3282 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
3283 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
3284 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
3285 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
3286 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
3287 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
3288 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
3289 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
3290 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
3291 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERVT6-TDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
3292 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3293 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3294 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
3295 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
3296 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
3297 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERVT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
3298 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3299 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3300 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
3301 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
3302 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
3303 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERVT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
3304 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3305 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3306 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
3307 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
3308 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
3309 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERVT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
3310 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3311 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3312 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
3313 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
3314 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
3315 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERVT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
3316 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3317 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3318 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3319 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3320 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3321 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3322 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3323 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3324 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
3325 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
3326 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
3327 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
3328 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
3329 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
3330 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
3331 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
3332 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
3333 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
3334 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
3335 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERFR1-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
3336 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3337 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3338 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3339 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3340 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3341 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3342 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3343 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3344 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
3345 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
3346 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
3347 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
3348 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
3349 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
3350 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
3351 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
3352 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
3353 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
3354 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
3355 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERFR2-BDP01TODO | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
3356 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-95 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERCON-95TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3357 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-95 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERCON-95TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3358 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-95 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERCON-95TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3359 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-95 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERCON-95TODO | 4 |  |  | 0 | $ComStatus , , | #
3360 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-94 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERCON-94TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3361 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-94 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERCON-94TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3362 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-94 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERCON-94TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3363 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-94 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERCON-94TODO | 4 |  |  | 0 | $ComStatus , , | #
3364 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-51 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERCON-51TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3365 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-51 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERCON-51TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3366 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-51 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERCON-51TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3367 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-51 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERCON-51TODO | 4 |  |  | 0 | $ComStatus , , | #
3368 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-49 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERCON-49TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3369 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-49 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERCON-49TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3370 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-49 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERCON-49TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3371 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-49 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERCON-49TODO | 4 |  |  | 0 | $ComStatus , , | #
3372 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-34 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERCON-34TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3373 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-34 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERCON-34TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3374 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-34 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERCON-34TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3375 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-34 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERCON-34TODO | 4 |  |  | 0 | $ComStatus , , | #
3376 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-53 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERCON-53TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3377 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-53 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERCON-53TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3378 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-53 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERCON-53TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3379 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-53 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERCON-53TODO | 4 |  |  | 0 | $ComStatus , , | #
3380 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-52 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERCON-52TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3381 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-52 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERCON-52TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3382 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-52 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERCON-52TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3383 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-52 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERCON-52TODO | 4 |  |  | 0 | $ComStatus , , | #
3384 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-50 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01SS01DAMPERCON-50TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3385 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-50 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERCON-50TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3386 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-50 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERCON-50TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3387 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-50 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01DAMPERCON-50TODO | 4 |  |  | 0 | $ComStatus , , | #
3388 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-88 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERCON-88TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3389 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-88 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERCON-88TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3390 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-88 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERCON-88TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3391 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-88 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERCON-88TODO | 4 |  |  | 0 | $ComStatus , , | #
3392 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-58 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01NS01DAMPERCON-58TODO | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3393 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-58 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERCON-58TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3394 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-58 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERCON-58TODO | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3395 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-58 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01DAMPERCON-58TODO | 4 |  |  | 0 | $ComStatus , , | #
3396 | QEC01_RTU | TUN:QEC01 | SS01:AHU | AHU | CON-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01AHUCON-02TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3397 | QEC01_RTU | TUN:QEC01 | SS01:AHU | AHU | CON-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SS01AHUCON-02TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
3398 | QEC01_RTU | TUN:QEC01 | NS01:AHU | AHU | PLA-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01AHUPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3399 | QEC01_RTU | TUN:QEC01 | NS01:AHU | AHU | PLA-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01NS01AHUPLA-02TODO | 4 |  |  | 0 | $ComStatus , , | #RUN
3400 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SCRJETPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B OFFLINE
3401 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SCRJETPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC RUNNING.
3402 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SCRJETPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: POWER SUPPLY FAULT
3403 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SCRJETPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CPU MODULE FAULT
3404 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SCRJETPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CRP MODULE FAULT
3405 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SCRJETPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
3406 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SCRJETPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
3407 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SCRJETPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
3408 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01SCRJETPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
3409 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3410 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3411 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3412 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3413 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3414 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3415 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3416 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3417 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3418 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3419 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3420 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3421 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3422 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3423 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3424 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3425 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3426 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3427 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3428 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3429 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3430 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3431 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3432 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3433 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3434 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3435 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3436 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3437 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3438 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3439 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3440 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3441 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3442 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3443 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3444 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3445 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3446 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL FAULT
3447 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3448 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNQEC01QEC1BJETQEC1B-JET100132TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3449 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3450 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3451 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3452 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3453 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3454 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3455 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3456 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3457 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3458 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3459 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3460 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3461 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3462 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3463 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3464 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3465 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3466 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3467 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3468 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3469 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3470 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3471 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3472 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3473 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3474 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3475 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3476 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3477 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3478 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3479 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3480 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3481 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3482 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3483 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3484 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3485 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3486 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL FAULT
3487 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3488 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNQEC01QEC1BJETQEC1B-JET100133TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3489 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3490 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3491 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3492 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3493 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3494 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3495 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3496 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3497 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3498 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3499 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3500 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3501 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3502 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3503 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3504 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3505 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3506 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3507 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3508 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3509 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3510 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3511 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3512 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3513 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3514 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3515 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3516 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3517 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3518 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3519 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3520 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3521 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3522 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3523 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3524 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3525 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3526 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL FAULT
3527 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3528 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNQEC01QEC1BJETQEC1B-JET100134TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3529 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3530 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3531 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3532 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3533 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3534 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3535 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3536 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3537 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3538 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3539 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3540 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3541 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3542 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3543 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3544 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3545 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3546 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3547 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3548 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3549 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3550 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3551 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3552 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3553 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3554 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3555 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3556 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3557 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3558 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3559 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3560 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3561 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3562 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3563 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3564 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3565 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3566 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL FAULT
3567 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3568 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNQEC01QEC1AJETQEC1A-JET102392TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3569 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3570 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3571 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3572 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3573 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3574 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3575 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3576 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3577 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3578 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3579 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3580 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3581 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3582 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3583 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3584 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3585 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3586 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3587 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3588 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3589 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3590 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3591 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3592 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3593 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3594 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3595 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3596 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3597 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3598 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3599 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3600 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3601 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3602 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3603 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3604 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3605 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3606 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL FAULT
3607 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3608 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNQEC01QEC1AJETQEC1A-JET102393TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3609 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3610 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3611 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Monitoring | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3612 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3613 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3614 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3615 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3616 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3617 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3618 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3619 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3620 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 32 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 32 | aeiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3621 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3622 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3623 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3624 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3625 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3626 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3627 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3628 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3629 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3630 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3631 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3632 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Control | MODBUS:16:Write:Holding Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 |  | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3633 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL2_Control | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 2 | Check SWC Name | ! | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 |  | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3634 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3635 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3636 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3637 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3638 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3639 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3640 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3641 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3642 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3643 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3644 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3645 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3646 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL FAULT
3647 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3648 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 16 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 |  | 0 | 16 | aeiTUNQEC01QEC1AJETQEC1A-JET102394TODO | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3649 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY DISCONNECTING SWITCH - OPEN
3650 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY VOLTAGE PRESENCE
3651 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER OPEN
3652 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER FAULT
3653 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN
3654 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT
3655 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS OPEN
3656 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS FAULT
3657 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER OPEN
3658 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER FAULT
3659 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER OPEN
3660 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER FAULT
3661 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS DISCONNECTING SWITCH OPEN
3662 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #UPS FAULT
3663 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN
3664 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT
3665 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 ABSENCE OF VOLTAGE
3666 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN
3667 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT
3668 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 ABSENCE OF VOLTAGE
3669 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER OPEN
3670 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER FAULT
3671 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER OPEN
3672 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER FAULT
3673 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER OPEN
3674 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER FAULT
3675 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER OPEN
3676 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER FAULT
3677 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSSPLC01TODO | 4 |  |  | 0 | $ComStatus , , | #SURGE ARRESTER TRIGGERED
3678 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
3679 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
3680 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
3681 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
3682 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
3683 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
3684 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
3685 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
3686 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
3687 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
3688 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
3689 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
3690 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
3691 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
3692 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
3693 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB01TODO | 4 |  |  | 0 | $ComStatus , , | #
3694 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
3695 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
3696 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
3697 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
3698 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
3699 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
3700 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
3701 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
3702 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
3703 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
3704 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
3705 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
3706 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
3707 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
3708 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
3709 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSLPS-MDB02TODO | 4 |  |  | 0 | $ComStatus , , | #
3710 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
3711 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
3712 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
3713 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
3714 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL1-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSEL1-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
3715 | QEC01_RTU | TUN:QEC01 | MMS | MCCB | EL1-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSEL1-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
3716 | QEC01_RTU | TUN:QEC01 | MMS | MCCB | EL1-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSEL1-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
3717 | QEC01_RTU | TUN:QEC01 | MMS | LBS | EL1-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSEL1-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
3718 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL1-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSUPS_EL1-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
3719 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL1-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSUPS_EL1-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
3720 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL1-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSUPS_EL1-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
3721 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL1-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSUPS_EL1-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
3722 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
3723 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
3724 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
3725 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT3-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT3-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
3726 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
3727 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
3728 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
3729 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT4-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT4-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
3730 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT6-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
3731 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT6-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
3732 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT6-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
3733 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT6-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
3734 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT6-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
3735 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT6-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
3736 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT6-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
3737 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT6-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
3738 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT6-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
3739 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT6-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
3740 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT6-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
3741 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT6-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
3742 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P--FR2-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P--FR2-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
3743 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P--FR2-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P--FR2-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
3744 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P--FR2-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P--FR2-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
3745 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P--FR2-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P--FR2-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
3746 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P--FR2-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P--FR2-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
3747 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P--FR2-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P--FR2-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
3748 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P--FR2-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P--FR2-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
3749 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P--FR2-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P--FR2-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
3750 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-94 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSMSFD-CON-94TODO | 4 |  |  | 0 | $ComStatus , , | #
3751 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-94 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSMSFD-CON-94TODO | 4 |  |  | 0 | $ComStatus , , | #
3752 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-58 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSMSFD-CON-58TODO | 4 |  |  | 0 | $ComStatus , , | #
3753 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-58 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSMSFD-CON-58TODO | 4 |  |  | 0 | $ComStatus , , | #
3754 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-88 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSMSFD-CON-88TODO | 4 |  |  | 0 | $ComStatus , , | #
3755 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-88 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSMSFD-CON-88TODO | 4 |  |  | 0 | $ComStatus , , | #
3756 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
3757 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
3758 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
3759 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
3760 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL2-IO01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSEL2-IO01TODO | 4 |  |  | 0 | $ComStatus , , | #
3761 | QEC01_RTU | TUN:QEC01 | MMS | MCCB | EL2-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSEL2-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
3762 | QEC01_RTU | TUN:QEC01 | MMS | MCCB | EL2-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSEL2-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
3763 | QEC01_RTU | TUN:QEC01 | MMS | LBS | EL2-UPS | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSEL2-UPSTODO | 4 |  |  | 0 | $ComStatus , , | #
3764 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL2-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSUPS_EL2-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
3765 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL2-VSD01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSUPS_EL2-VSD01TODO | 4 |  |  | 0 | $ComStatus , , | #
3766 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL2-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSUPS_EL2-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
3767 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL2-VSD02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSUPS_EL2-VSD02TODO | 4 |  |  | 0 | $ComStatus , , | #
3768 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
3769 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
3770 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
3771 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT1-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT1-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
3772 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
3773 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
3774 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
3775 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT2-IDP01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT2-IDP01TODO | 4 |  |  | 0 | $ComStatus , , | #
3776 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT5-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
3777 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT5-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
3778 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT5-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
3779 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT5-TDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
3780 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT5-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
3781 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT5-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
3782 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT5-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
3783 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT5-TDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
3784 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT5-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
3785 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-VT5-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
3786 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT5-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
3787 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-03 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-VT5-TDP01-03TODO | 4 |  |  | 0 | $ComStatus , , | #
3788 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-FR1-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-FR1-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
3789 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-FR1-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-FR1-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
3790 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-FR1-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-FR1-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
3791 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-FR1-BDP01-01 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-FR1-BDP01-01TODO | 4 |  |  | 0 | $ComStatus , , | #
3792 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-FR1-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-FR1-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
3793 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-FR1-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS3P-FR1-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
3794 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-FR1-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-FR1-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
3795 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-FR1-BDP01-02 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMS2P-FR1-BDP01-02TODO | 4 |  |  | 0 | $ComStatus , , | #
3796 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-50 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSMSFD-CON-50TODO | 4 |  |  | 0 | $ComStatus , , | #
3797 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-50 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSMSFD-CON-50TODO | 4 |  |  | 0 | $ComStatus , , | #
3798 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-52 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSMSFD-CON-52TODO | 4 |  |  | 0 | $ComStatus , , | #
3799 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-52 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSMSFD-CON-52TODO | 4 |  |  | 0 | $ComStatus , , | #
3800 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-95 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSMSFD-CON-95TODO | 4 |  |  | 0 | $ComStatus , , | #
3801 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-95 | 0 | TODO | SIL0 | MODBUS:4:Read:Input Registers | ERROR: Empty Address Index value ! | 0 | 1 | Check SWC Name | ! | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 |  | 0 | 1 | deiTUNQEC01MMSMSFD-CON-95TODO | 4 |  |  | 0 | $ComStatus , , | #
-END-

## B-Address Qty
FC / Class Name | MPLC | MSPLC | WTDG | SWI | SPLC | SHAFT | TVF | JET | TVD | MEPD | OTS | TTS | VS | LCP | AHU | PFA | SMC | SED | MUL | FXL | IOM | IOC | MDB | MSH1 | MSH2 | MJF1 | MJF2 | CSH | CJF | SCB | MCB | TRU | TRD
MODBUS:1:Read:Coils | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000
MODBUS:2:Read:Discrete Inputs | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000
MODBUS:3:Read:Holding Registers | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000
MODBUS:4:Read:Input Registers | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000 | 40;20000
MODBUS:5:Write:Coil | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 30;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000
MODBUS:6:Write:Holding Register | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 30;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000
MODBUS:15:Write:Coils | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 30;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000
MODBUS:16:Write:Holding Registers | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 30;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000
IEC104:M_SP_NA_1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
IEC104:M_DP_NA_1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
IEC104:M_ME_NA_1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
IEC104:M_ME_NB_1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
IEC104:M_ME_NC_1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
IEC104:M_IT_NA_1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
IEC104:M_SP_TB_1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
IEC104:M_DP_TB_1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
IEC104:C_SC_NA_1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
IEC104:C_DC_NA_1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
IEC104:C_RC_NA_1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
IEC104:C_SE_NA_1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
IEC104:C_SE_NB_1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
IEC104:C_SE_NC_1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
IEC104:C_IC_NA_1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
IEC104:C_CI_NA_1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
IEC104:C_RD_NA_1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20