## Revision
Revision
Date | Version | Author | Observations
2015-09-13 | A0.2 | A. TRAN | Creation | CHANGE TO :
2016-03-02 | A1.1 | C.CAMARA | Update following adopted ICD template
2016-03-16 | A2 | C.CAMARA | Update SIL2; Modbus and TVS Mode
2016-04-06 | B- | C.CAMARA | Update following workshop on the 04/04/2016
2016-08-24 | B0.2 | F.BLAISE | Update following new template and Cegelec comments
2016-09-09 | B0.3 | F.BLAISE | Update analog input following Cegelec comments
2016-09-21 | B0.4 | F.BLAISE | Add DI received by SCADA for SIL-2 commands Add select/execute for A0 type commands
2016-09-27 | B0.5 | Software Team | Modeling LCP, IOC, AHU and SCB equipment classes
2016-11-03 | B0.6 | Software Team | Modeling TVF, CJF and JET equipment classes
2016-11-30 | B0.6 | O. Bernard | Added SIL2 commands from B0.5, SW started their B0.6 from older version. Added size of point type in Definitions tab (used in IO Class) Added "Is Animated" column in Class List
2017-01-30 | B0.7 | C. CAMARA | Update SIL2 and class for rationalization activities
2017-02-06 | B0.8 | E. SANDOZ | Review and correction before sending to HK
2017-04-12 | B0.8 | E. SANDOZ | Back from HK
2017-04-22 | B0.9 | T.MARTINEZ | Migration to 0.34 + VBA code enhancement.
2017-05-10 | B0.9 | H. SALIHEDDINE | - Add Column "Revision" in Class list and Instance List - index address and position bit filling in Class list sheet ( the filling depends on the used protocol) - Instance ID filling in Instance List sheet - VBA code update for point address calculation - I.O class small update for DI, DI , AI Point type corresponding data
2017-05-15 | B0.10 | H. SALIHEDDINE | B0.10_SP18_1 - Add "OPERATING MODE " AI and DI2 points for FXL and MUL Classes B0.10_SP18_2 - Replace « MODBUS:1:Read:Coils » by « MODBUS:4:Read:Input Registers » in column « Operation code (FC, ASDU, ...) » - Manual filling of "Index Address" column in class list
2017-06-28 | B0.10_SP18_3 | T.LO | In "1-Class List", - update class MUL and FXL range min = 1 and range max = 16 for "OPERATING MODE SELECT" and "OPERATNG MODE EXECUTE" - Fix register type (originally input type usesfunc code16, output type uses func code 4…etc) - Update "Index Address" for class MUL In "B-AddressQty", - Enlarge FXL address index In "2-Instance List", - Update "RTU Name" to OCC_TUN and BOCC_TUN - Update "Equipment name" of OTS equipment to OTS01 and OTS02 - Update "Equipment name" of LCP equipment to LCP01" - Update "Sublocation" from TVS:SCR_SCB01 to TVS:SCR-SCB01 In "4-External Variables" - Add CJF class EV
2017-10-18 | B1.1 | MTE | IO List major correction following a dedicated TVS workshop (October 2017).
2017-11-20 | B1.2 | MTE | IO List major correction following a dedicated TVS workshop (20th November 2017).
2017-11-29 | B1.3 | MTE | IO List major correction following dedicated TVS workshops (22nd & 26th November 2017).
2017-11-30 | B1.4 | MTE | Emergency Scenarios Workshop
2017-12-12 | B1.5 | MTE | Class List: Ventilation Normal & Congested Modes Update Emergency Scenarios Update MMS Classes Update - CPELX class to be splitted in several subclasses Instance List: MAR01 & MAR0A available
2017-12-17 | B1.6 | MTE | Class List: MMS Workshop Instance List: MMS Workshop for MAR01 & MAR0A Emergency Scenario
2017-12-21 | B1.7 | MTE | Class List: Correction VENTILATION, PFA, EXF & SED. Instance List: 8 Smoke Curtains.
2018-01-05 | B1.8 | MTE | Class List: Correction of Point Type in class EMERGENCY - Mode Correction of Point Type in class MPLC - PLC-B Status Correction in class MPLC - Operational Status: not animated Addition of the alarm label related to WATCHDOG Instance List: Addition of EC1-01, EC1-0A, QAP-01 and QEC-01 stations
2018-01-10 | B2 | MTE | Delivery revision PLC points: Deletion of previous content, obsolete after Class list changes
2018-03-08 | B2.1 | Chao | 1-Class List:delete a space after "STOP" in ROW110 and ROW151, COLUMN P 2-Instance List: Update Column G and Column K to meet the DB path for TVS for lusail
|  | E.TAI | 1. Update macro version to V2.2 2. Class List: i.Add Point Name (Column G) and Point Description (Column H) to the class name MSFD with CSS point name LOCAL MODE STATUS ii. Add Point Name (Column G) and Point Description (Column H) to the following class: - MCB - ADS - TRF - ACB - MDB - EL - MCCB - LBS - SMDB 3. Instance List: i. Update Location as TVS:OCC under MAIN UNDERGROUND LINE AVERAGE TEMPERATURE, FOXHILL LINE AVERAGE TEMPERATURE, TUNNEL NORMAL & CONGESTED VENTILATION MODES and EMERGENCY SCENARIOS. ii. Fill Instance Id (Column P) iii. except Location: TVS:QEC01, TVS:EC101, TVS:QAP01 and TVS:EC10A, mark "isAComment" (Column B) as Y for other Location

## Introduction
Introduction
For all ICD relative to equipment monitoring & control , this ECI (Equipment Classes & Instances) file template must be used as appendix to define: - the equipment classes, from an I/O point of view - all instances relative to each class
Recommandations
1 | Use one ECI file for each ICD document (one ICD=one subsystem)
2 | Do not change the organisation of the ECI file:
- Sheet "Equipment classes" : define all classes for the relative subsystem (see meaning of each field in the "Definitions" sheet)
- Sheet "Equipment instances" : define all instances for the relative subsystem (see meaning of each field in the "Definitions" sheet)
3 | For each sheet, do not change the organisation of the sheet (does not remove any column) in order to be able to use the standard export/import tools
4 | Create the necessary number of classes: for example, if similar equipment have different numbers of DI, DO, AI, create one class for each case
5 | Define, if possible, contiguous addresses for equipments/points within the same class.
Use the internal macro (### to be implemented in next release ###) to check the consistency of all data included in the sheet "Equipment classes" and "Equipment instances"
Notes
Issues to be addressed in future release
## Use appropriate point & bit value descriptions to create alarm label (DI) #####
### define rules for separators

## Definitions
Subsystem TVS - Equipment classes & instances
Definitions
1-Class List
Column Class | Column Name | Column Description | Values
| Revision | Identifiy the IO revision in witch the information was added , deleted or modified | version (string)
| isAComment | Specify whether the line is a comment or not | Y or N
EQUIPMENT CLASSES
| System | Define the trigram of the system's name in which the equipment is included | XXX
| Sub-system | Define the trigram of the sub-system's name in which the equipment is included | XXX
| Class name | Short equipment name on XXX characters number (minimum 3 characters - maximum 12 characters)
| CSS Point Name | Normalized name, used within the SCADA
EXTERNAL SYSTEM DATA
| Point Name | Name of equipment point from supplier
| Point Description | Any useful documentation on the point
| Point Type | Point can be qualified as Event or Alarm. Operational are not sent to MMS, Technical and Meter are sent to MMS. Hence, supported values are | Operational Event |  | Event which are from the nominal mode of the equipment. For exmaple open/close, locked/unlocked …
|  |  | Operational Alarm |  | Alarm that are from the nominal operation mode of the equipment. For example operator changing mode which put the equipment in Alarm state or equipment changing its status triggering an alarm.
|  |  | Technical Alarm |  | Alarm that deviated from the nominal operation mode. For example all detect fault. These are not part of the system nominal behavior
|  |  | Meter |  | Event which are needed for maintenance procedures.
Command
| Frequency | Time interval between data transmissions from SCADA to MMS | Daily
Weekly
Monthly
| Data Type | Digital Input | DI | 1 | bit
|  |  | DI2 | 2 | bits
|  | Digital Output | DO | 1 | bits
|  |  | DO2 | 2 | bits
|  | Analog Input | AI | 16 | bits
|  |  | AI2 | 32 | bits
|  | Analog Output | AO | 16 | bits
|  |  | AO2 | 32 | bits
EXTERNAL SYSTEM DATA DETAILS
| SIL Level | Identify the SIL level for the equipment point which can be | SIL0
SIL2_Monitoring
SIL2_Control
| Protocol | Applicable protocol: may be Modbus or IEC104
| Operation code | Operation code needed to manage the point at protocol level
| Memory Block | TODO
DI POINT
| DI/DI2 Value = 0 | For a DI or DI2, definition of the supervised status when the value is set to 0
| DI/DI2 Value = 1 | For a DI or DI2, definition of the supervised status when the value is set to 1
| DI2 Value = 2 | For a DI2, definition of the supervised status when the value is set to 2
| DI2 Value = 3 | For a DI2, definition of the supervised status when the value is set to 3
| Default value | Default value of the equipment point
| Alarm severity | Define the alarm severity for each value with the format (value1: severity label 1, value2: severity label 2, etc) Severity labels are: - None for events - Min for Minor alarms - Maj for Major alarms - Crit for Critical alarms Example: - 0: None, 1: Maj - 0: None, 1: None
| Alarm label | This label will be presented to the operators on the HMI for english language. It consists of: CCS Point Name: DI value when=0 / DI value when=1 / …
DO POINT
| DO/DO2 Value = 0 | For a DO or DO2, definition of the supervised status when the value is set to 0
| DO/DO2 Value = 1 | For a DO or DO2, definition of the supervised status when the value is set to 1
| DO2 Value = 2 | For a DO2, definition of the supervised status when the value is set to 2
| DO2 Value = 3 | For a DO2, definition of the supervised status when the value is set to 3
| Default value | Define the default value of the equipment point
| Output duration (ms) | Give the properties of the output signal command in ms: <empty>: continuous signal integer value: temporal duration of the pulse (in ms)
| Timeout for reaction (s) | Expected response time between the command sending and the modification of the associated status
| Initial condition | Pre-condition to be checked before sending the command
| Final condition | Post-condition to be checked to make sure the command is successful
| Associated return status | Return equipment status associated with the command
AI POINT
| Unit | Give the measurement unity of the analog data
| Min value | Define the minimum value of the data
| Max value | Define the maximum value of the data
| Limit 1 (optional) | Threshold in order to add range of the supervised value between min and max values
| Limit 2 (optional) | Threshold in order to add range of the supervised value between min and max values
In the template, alarm thresholds are defined through two value limits plus a minimum value and a maximum value. As shown in the figure on the right, this defines 5 ranges for which an alarm may be defined
| Range <i> alarm severity | Define the alarm severity for a range Severity labels are: - None for events - Min for Minor alarms - Maj for Major alarms - Crit for Critical alarms
| Range <i> alarm label | Define the alarm label for a range
| Dead band | Define the tolerance of variation around a threshold
| Default value | Define the default value of the equipment point
| Alarm label | This label will be presented to the operators on the HMI. It consists on: Equipment description (displayed in HMI): under Min value / under Max value / etc.
AO POINT
| Unit | Give the measurement unity of the analog data
| Range Min value | Define the minimum range of the command value
| Range Max value | Define the maximum range of the command value
| Output duration (ms) | Give the properties of the output signal command in ms: Nothing to fill: continuous signal XXX: temporal duration of the pulse
| Timeout for reaction (s) | Response time between the command and the associated status modification on the equipment
| Initial condition | Conditions to verify before sending the command
| Final condition | Conditions to verify after the sending of the command
| Associated return status | Return equipment status associated with the command
2-Instance List
Column Class | Column Name | Column Description
| Revision | Identifiy the IO revision in witch the information was added , deleted or modified
| GBS Code | TBC
| LBS Code (LRT) | TBC
| LBS Code (QRC) | TBC
| Description | Textual description or precision about the Location/sublocation of the equipment instance
| Location | Define in a short designation the geographical location in which the equipment is based
| Sublocation | Define in a short designation the sublocation (Subsystem / Level / Building / room) in which the equipment is based
| Class name | Class name identical to the class name defined in the "1-Class List" tab
| Equipment name | Give the instance name of the equipment.
| RTU Name | Name of the concentrator (as viewed in the SCADA subsystem) for the equipment
| PLC Name | Name of the partner PLC
| InvalidVar1 | name of the first external variable used to invalidate this equipement (usually comStatus of the gateway or PRTU)
| InvalidVar2 | name of the second external variable used to invalidate this equipement (usually comStatus of the gateway or PRTU)
| InvalidVar3 | name of the third external variable used to invalidate this equipement (usually comStatus of the gateway or PRTU)

## Generation
Execute |  | To do before Generation => Check that there are no ROW filters set in the Class and instance worksheets
Tool version | v2.2 | v2.2
Generation Time: | 3/15/2018 at 11:54:55 AM
Found Classes: | 46
Found Errors: | 0
Found Warnings: | 2503
Not Found Classes: | 0

## 1-Class List
|  | EQUIPMENT CLASSES |  |  |  | EXTERNAL SYSTEM DATA |  |  |  |  | EXTERNAL SYSTEM DATA DETAILS |  |  |  | DI or DI2 | [6 empty] | DO | [8 empty] | AI | [17 empty] | AO | [8 empty] | MMS | SE Engineering |  |  |  | SW Engineering | HMI details (dictionnaries)
Revision | isAComment | System | Sub-system | Class name | CSS Point Name | Point Name | Point Description | Point Type | Frequency | Data Type | SIL Level | Protocol | Operation code (FC, ASDU, ...) | Memory Block | DI or DI2 value = 0 (00) | DI or DI2 value = 1(01) | DI2 value = 2 (10) | DI2 value = 3 (11) | Default value | Alarm severity | Alarm label | DO or DO2 value = 0 (00) | DO or DO2 value = 1(01) | DO2 value = 2 (10) | DO2 value = 3 (11) | Output duration (ms) | Timeout for reaction (s) | Initial condition | Final condition | Associated return status | Unit | Min value | Max value | Limit 1 (optional) | Limit 2 (optional) | Range 1 alarm severity ] -∞,min value] | Range 1 alarm label ] -∞,min value] | Range 2 alarm severity ]min value,limit1] | Range 2 alarm label ]min value,limit1] | Range 3 alarm severity ]limit1,limit2] | Range 3 alarm label ]limit1,limit2] | Range 4 alarm severity ]limit2,max value] | Range 4 alarm label ]limit2,max value] | Range 5 alarm severity ]max value,+∞[ | Range 5 alarm label ]max value,+∞[ | Dead band | Default value | Formula | Unit | Range Min value | Range Max value | Output duration (ms) | Timeout for reaction (s) | Initial condition | Final condition | Associated return status | Formula | [Lusail] PBS code | Data Length | Index Address | Bit position | IsAnimated | Code | System (Native language) | Sub-system (Native language) | Class name (Native language) | Equipment description (displayed in HMI) (Native language) | Description (Details of description) (Native language)
| Y | This part should be filled up by System Engineering and gives the indication on how to modelize prototypes
B1.5 | Y | + |  |  | MASTER PLCs (MPLC)
B1.1 | Y | TUN | TVS | MPLC | PLC STATE | PLC STATE | PLC A/B OFFLINE | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OFFLINE | ONLINE |  |  | ONLINE | 0: Crit, 1: None | PLC STATE : OFFLINE/ONLINE | [37 empty] | 1 | 1 | 0 | YES | PlcState
B1.8 | Y | TUN | TVS | MPLC | OPERATIONAL STATUS | OPERATIONAL STATUS | PLC RUNNING. | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | STOP | RUNNING |  |  | RUNNING | 0: Crit, 1: None | OPERATIONAL STATUS : STOP/RUNNING | [37 empty] | 1 | 1 | 1 | NO | OpStatus
B1.3 | Y | TUN | TVS | MPLC | PLC-A STATUS | PRIMARY MODE ACTIVE | PLC A/B : PRIMARY MODE ACTIVE | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | STANDBY | ACTIVE |  |  | ACTIVE | 0: Maj, 1: None | PLC-A STATUS : STANDBY/ACTIVE | [37 empty] | 1 | 1 | 2 | YES | PlcA
B1.8 | Y | TUN | TVS | MPLC | PLC-B STATUS | SECONDARY MODE ACTIVE (STANDBY) | PLC A/B: SECONDARY MODE ACTIVE (STANDBY) | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | STANDBY | ACTIVE |  |  | STANDBY | 0: None, 1: None | PLC-B STATUS : STANDBY/ACTIVE | [37 empty] | 1 | 1 | 3 | YES | PlcB
B1.3 | Y | TUN | TVS | MPLC | APPLICATIONS ARE DIFFERENT ON THE TWO PLCS | APPLICATIONS ARE DIFFERENT ON THE TWO PLCS | APPLICATIONS ARE DIFFERENT ON THE TWO PLCS | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | APPLICATIONS ARE DIFFERENT ON THE TWO PLCS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 4 | NO | AppDiff
B1.1 | Y | TUN | TVS | MPLC | POWER SUPPLY STATUS | POWER SUPPLY FAULT | PLC A/B: POWER SUPPLY FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | POWER SUPPLY STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 5 | NO | PwStat
B1.2 | Y | TUN | TVS | MPLC | CPU MODULE STATUS | CPU MODULE FAULT | PLC A/B: CPU MODULE FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | CPU MODULE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 6 | NO | CpuStat
B1.2 | Y | TUN | TVS | MPLC | CRP MODULE STATUS | CRP MODULE FAULT | PLC A/B: CRP MODULE FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | CRP MODULE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 7 | NO | CrpStat
B1.3 | Y | TUN | TVS | MPLC | NOE MODULE COMMUNICATION [SCADA] STATUS | NOE MODULE FAULT (SCADA COMMUNICATION) | PLC A/B: NOE MODULE FAULT (SCADA COMMUNICATION) | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | NOE MODULE COMMUNICATION [SCADA] STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 8 | NO | ComScada
B1.3 | Y | TUN | TVS | MPLC | NOE MODULE COMMUNICATION [STATION PLC] STATUS | NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION) | PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION) | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | NOE MODULE COMMUNICATION [STATION PLC] STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 9 | NO | ComStation
B1.2 | Y | TUN | TVS | MPLC | COMMUNICATION WITH SCADA STATUS | COMMUNICATION FAULT WITH SCADA | PLC A/B: COMMUNICATION FAULT WITH SCADA | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH SCADA STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 10 | NO | SdStat
B1.2 | Y | TUN | TVS | MPLC | COMMUNICATION WITH STATION PEA-01 PLC STATUS | COMMUNICATION FAULT WITH STATION PEA-01 PLC | PLC A/B: COMMUNICATION FAULT WITH STATION PEA-01 PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH STATION PEA-01 PLC STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 11 | NO | ComPea
B1.2 | Y | TUN | TVS | MPLC | COMMUNICATION WITH STATION MAR-01 PLC STATUS | COMMUNICATION FAULT WITH STATION MAR-01 PLC | PLC A/B: COMMUNICATION FAULT WITH STATION MAR-01 PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH STATION MAR-01 PLC STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 12 | NO | ComMar1
B1.2 | Y | TUN | TVS | MPLC | COMMUNICATION WITH STATION MAR-02 PLC STATUS | COMMUNICATION FAULT WITH STATION MAR-02 PLC | PLC A/B: COMMUNICATION FAULT WITH STATION MAR-02 PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH STATION MAR-02 PLC STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 13 | NO | ComMar2
B1.2 | Y | TUN | TVS | MPLC | COMMUNICATION WITH STATION MAR-03 PLC STATUS | COMMUNICATION FAULT WITH STATION MAR-03 PLC | PLC A/B: COMMUNICATION FAULT WITH STATION MAR-03 PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH STATION MAR-03 PLC STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 14 | NO | ComMar3
B1.2 | Y | TUN | TVS | MPLC | COMMUNICATION WITH STATION MAR-04 PLC STATUS | COMMUNICATION FAULT WITH STATION MAR-04 PLC | PLC A/B: COMMUNICATION FAULT WITH STATION MAR-04 PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH STATION MAR-04 PLC STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 15 | NO | ComMar4
B1.2 | Y | TUN | TVS | MPLC | COMMUNICATION WITH STATION QEC-01 PLC STATUS | COMMUNICATION FAULT WITH STATION QEC-01 PLC | PLC A/B: COMMUNICATION FAULT WITH STATION QEC-01 PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH STATION QEC-01 PLC STATUS : NORMAL/FAULTY | [37 empty] | 1 | 2 | 0 | NO | ComQec
B1.2 | Y | TUN | TVS | MPLC | COMMUNICATION WITH STATION EC1-01 PLC STATUS | COMMUNICATION FAULT WITH STATION EC1-01 PLC | PLC A/B: COMMUNICATION FAULT WITH STATION EC1-01 PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH STATION EC1-01 PLC STATUS : NORMAL/FAULTY | [37 empty] | 1 | 2 | 1 | NO | ComEc
B1.2 | Y | TUN | TVS | MPLC | COMMUNICATION WITH STATION QAP-01 PLC STATUS | COMMUNICATION FAULT WITH STATION QAP-01 PLC | PLC A/B: COMMUNICATION FAULT WITH STATION QAP-01 PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH STATION QAP-01 PLC STATUS : NORMAL/FAULTY | [37 empty] | 1 | 2 | 2 | NO | ComQap
B1.2 | Y | TUN | TVS | MPLC | COMMUNICATION WITH STATION FXH-02 PLC STATUS | COMMUNICATION FAULT WITH STATION FXH-02 PLC | PLC A/B: COMMUNICATION FAULT WITH STATION FXH-02 PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH STATION FXH-02 PLC STATUS : NORMAL/FAULTY | [37 empty] | 1 | 2 | 3 | NO | ComFxh
B1.2 | Y | TUN | TVS | MPLC | COMMUNICATION WITH SHAFT PEA-0A PLC STATUS | COMMUNICATION FAULT WITH SHAFT PEA-0A PLC | PLC A/B: COMMUNICATION FAULT WITH SHAFT PEA-0A PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH SHAFT PEA-0A PLC STATUS : NORMAL/FAULTY | [37 empty] | 1 | 2 | 4 | NO | ComPeaa
B1.2 | Y | TUN | TVS | MPLC | COMMUNICATION WITH SHAFT PEA-1B PLC STATUS | COMMUNICATION FAULT WITH SHAFT PEA-1B PLC | PLC A/B: COMMUNICATION FAULT WITH SHAFT PEA-1B PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH SHAFT PEA-1B PLC STATUS : NORMAL/FAULTY | [37 empty] | 1 | 2 | 5 | NO | ComPeab
B1.2 | Y | TUN | TVS | MPLC | COMMUNICATION WITH SHAFT MAR-0A PLC STATUS | COMMUNICATION FAULT WITH SHAFT MAR-0A PLC | PLC A/B: COMMUNICATION FAULT WITH SHAFT MAR-0A PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH SHAFT MAR-0A PLC STATUS : NORMAL/FAULTY | [37 empty] | 1 | 2 | 6 | NO | ComMara
B1.2 | Y | TUN | TVS | MPLC | COMMUNICATION WITH SHAFT EC1-0A PLC STATUS | COMMUNICATION FAULT WITH SHAFT EC1-0A PLC | PLC A/B: COMMUNICATION FAULT WITH SHAFT EC1-0A PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH SHAFT EC1-0A PLC STATUS : NORMAL/FAULTY | [37 empty] | 1 | 2 | 7 | NO | ComEca
B1.2 | Y | TUN | TVS | MPLC | COMMUNICATION WITH SHAFT QAP-1B PLC STATUS | COMMUNICATION FAULT WITH SHAFT QAP-1B PLC | PLC A/B: COMMUNICATION FAULT WITH SHAFT QAP-1B PLC | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | COMMUNICATION WITH SHAFT QAP-1B PLC STATUS : NORMAL/FAULTY | [37 empty] | 1 | 2 | 8 | NO | ComQapb
B0.9 | Y | + |  |  | Watchdog (WTDG)
B1.1 | Y | TUN | TVS | WTDG | Watchdog Counter | Watchdog Counter | Watchdog Counter for each TVS Master PLC | Operational Alarm |  | AI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | Count | 0 | 65535 |  |  | Critical | Watchdog Counter Failure | [10 empty] | UINT | [10 empty] | 16 | 1 |  | NO | Counter
B1.5 | Y | + |  |  | SWITCH
B1.2 | Y | TUN | TVS | SWI | SWITCH STATUS | SWITCH FAULT | SWITCH FAULT | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SWITCH STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 |  | YES | SwStat
B1.5 | Y | + |  |  | STATION/SHAFT PLC
B1.3 | Y | TUN | TVS | SPLC | PLC STATE | PLC STATE | PLC A/B OFFLINE | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OFFLINE | ONLINE |  |  | ONLINE | 0: Crit, 1: None | PLC STATE : OFFLINE/ONLINE | [37 empty] | 1 | 1 | 0 | YES | PlcState
B1.3 | Y | TUN | TVS | SPLC | OPERATIONAL STATUS | OPERATIONAL STATUS | PLC RUNNING. | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | STOP | RUNNING |  |  | RUNNING | 0: Crit, 1: None | OPERATIONAL STATUS : STOP/RUNNING | [37 empty] | 1 | 1 | 1 | YES | OpStatus
B1.3 | Y | TUN | TVS | SPLC | POWER SUPPLY STATUS | POWER SUPPLY FAULT | PLC A/B: POWER SUPPLY FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | POWER SUPPLY STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 2 | NO | PwStat
B1.3 | Y | TUN | TVS | SPLC | CPU MODULE STATUS | CPU MODULE FAULT | PLC A/B: CPU MODULE FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | CPU MODULE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 3 | NO | CpuStat
B1.3 | Y | TUN | TVS | SPLC | CRP MODULE STATUS | CRP MODULE FAULT | PLC A/B: CRP MODULE FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | CRP MODULE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 4 | NO | CrpStat
B1.3 | Y | TUN | TVS | SPLC | CRA MODULE STATUS | NRP MODULE FAULT | NRP MODULE FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | CRA MODULE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 5 | NO | CraStat
B1.3 | Y | TUN | TVS | SPLC | NRP MODULE STATUS | NRP MODULE FAULT | NRP MODULE FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | NRP MODULE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 6 | NO | NrpStat
B1.3 | Y | TUN | TVS | SPLC | NOE MODULE COMMUNICATION STATUS | NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION) | PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION) | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | NOE MODULE COMMUNICATION STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 7 | NO | ComStat
B1.3 | Y | TUN | TVS | SPLC | IO MODULE STATUS | NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION) | PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION) | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | IO MODULE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 8 | NO | IoStat
B1.1 | Y | + |  |  | FIRE MANUAL OVERRIDE PANEL (FMOP)
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL EMERGENCY MODE | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL EMERGENCY MODE : INACTIVE/ACTIVE | [37 empty] | 1 | 1 | 0 | YES | EmergNod
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL RIGHT SCENARIO PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL RIGHT SCENARIO PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | 1 | 1 | 1 | NO | RightStat
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL LEFT SCENARIO PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL LEFT SCENARIO PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | 1 | 1 | 2 | NO | LeftStat
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | 1 | 1 | 3 | NO | Spare1
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | 1 | 1 | 4 | NO | Spare2
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | 1 | 1 | 5 | NO | Spare3
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | 1 | 1 | 6 | NO | Spare4
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | 1 | 1 | 7 | NO | Spare5
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | 1 | 1 | 8 | NO | Spare6
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | 1 | 1 | 9 | NO | Spare7
B1.3 | Y | TUN | TVS | FMOP | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | NA | ACTIVE / INACTIVE STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS : INACTIVE/ACTIVE | [37 empty] | 1 | 1 | 10 | NO | Spare8
B0.9 | Y | + |  |  | LOCAL CONTROL PANEL (LCP) [STATION HMI]
B1.2 | Y | TUN | TVS | LCP | COMMUNICATION WITH PLC STATUS | COMMUNICATION FAULT WITH PLC | COMMUNICATION FAULT WITH PLC | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | COMMUNICATION WITH PLC STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 0 | YES | ComFaultPlc
B1.1 | Y | TUN | TVS | LCP | LCP MODE | LCP MODE | LOCAL / REMOTE STATUS | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | REMOTE | LOCAL |  |  | REMOTE | 0: None, 1: Maj | LCP MODE : REMOTE/LOCAL | [37 empty] | 1 | 1 | 1 | YES | LcpMode
B1.5 | Y | + |  |  | TUNNEL NORMAL & CONGESTED VENTILATION MODES
B1.5 | N | TUN | TVS | VENTILATION | OPERATING MODE | OPERATING MODE | OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP) | Operational Event |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | AUTO PLC | MANUAL SCADA |  |  | AUTO PLC | 0: None, 1: None | OPERATING MODE : AUTO PLC/MANUAL SCADA | [37 empty] | 1 | 1 | 0 | YES | OpMode
B1.5 | N | TUN | TVS | VENTILATION | ACTIVE VENTILATION MODE | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | PISTON | MECHANICAL | COOLING | INCONSISTANT | PISTON | 0: None, 1: None, 2: None, 3: Crit | ACTIVE VENTILATION MODE : PISTON/MECHANICAL/COOLING/INCONSISTANT | [37 empty] | 2 | 1 | 2 | YES | ActMode
B1.5 | N | TUN | TVS | VENTILATION | PLC AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | Command |  | DO | SIL0 | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE AUTO MODE |  |  |  | 10 | OPERATING MODE = MANUAL SCADA |  | OPERATING MODE = AUTO PLC | [28 empty] | 1 | 1 |  | NO | CmdAuto
B1.5 | N | TUN | TVS | VENTILATION | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 2 | OPERATING MODE = AUTO PLC |  | SCADA MANUAL MODE SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 2 |  | NO | CmdSelMan
B1.5 | N | TUN | TVS | VENTILATION | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 4 | NO | AckSelMan
B1.5 | N | TUN | TVS | VENTILATION | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 10 | OPERATING MODE = AUTO PLC |  | SCADA MANUAL MODE EXECUTE ACK = ACKNOWLEDGE and OPERATING MODE = MANUAL SCADA | [28 empty] | 1 | 3 |  | NO | CmdExeMan
B1.5 | N | TUN | TVS | VENTILATION | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 6 | NO | AckExeMan
B1.5 | N | TUN | TVS | VENTILATION | PISTON MODE SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE PISTON MODE |  |  |  | 2 | ACTIVE VENTILATION MODE != PISTON MODE |  | PISTON MODE SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 4 |  | NO | CmdSelPis
B1.5 | N | TUN | TVS | VENTILATION | PISTON MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | PISTON MODE SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 8 | NO | AckSelPis
B1.5 | N | TUN | TVS | VENTILATION | PISTON MODE EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE PISTON MODE |  |  |  | 40 | ACTIVE VENTILATION MODE != PISTON MODE |  | PISTON MODE EXECUTE ACK = ACKNOWLEDGE and ACTIVE VENTILATION MODE = PISTON MODE | [28 empty] | 1 | 5 |  | NO | CmdExePis
B1.5 | N | TUN | TVS | VENTILATION | PISTON MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | PISTON MODE EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 10 | NO | AckExePis
B1.5 | N | TUN | TVS | VENTILATION | MECHANICAL MODE SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE MECHANICAL MODE |  |  |  | 2 | ACTIVE VENTILATION MODE != MECHANICAL MODE |  | MECHANICAL MODE SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 6 |  | NO | CmdSelMech
B1.5 | N | TUN | TVS | VENTILATION | MECHANICAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | MECHANICAL MODE SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 12 | NO | AckSelMech
B1.5 | N | TUN | TVS | VENTILATION | MECHANICAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE MECHANICAL MODE |  |  |  | 40 | ACTIVE VENTILATION MODE != MECHANICAL MODE |  | MECHANICAL MODE EXECUTE ACK = ACKNOWLEDGE and ACTIVE VENTILATION MODE = MECHANICAL MODE | [28 empty] | 1 | 7 |  | NO | CmdExeMech
B1.5 | N | TUN | TVS | VENTILATION | MECHANICAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | MECHANICAL MODE EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 14 | NO | AckExeMech
B1.5 | N | TUN | TVS | VENTILATION | COOLING MODE SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE COOLING MODE |  |  |  | 2 | ACTIVE VENTILATION MODE != COOLING MODE |  | COOLING MODE SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 8 |  | NO | CmdExelCool
B1.5 | N | TUN | TVS | VENTILATION | COOLING MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | COOLING MODE SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 2 | 0 | NO | AckSelCool
B1.5 | N | TUN | TVS | VENTILATION | COOLING MODE EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE COOLING MODE |  |  |  | 40 | ACTIVE VENTILATION MODE != COOLING MODE |  | COOLING MODE EXECUTE ACK = ACKNOWLEDGE and ACTIVE VENTILATION MODE = COOLING MODE | [28 empty] | 1 | 9 |  | NO | CmdExeCool
B1.5 | N | TUN | TVS | VENTILATION | COOLING MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | COOLING MODE EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 2 | 2 | NO | AckExeCool
B1.5 | Y | + |  |  | EMERGENCY SCENARIO
B1.8 | Y | TUN | TVS | EMERGENCY | SCENARIO ACTIVATION PROPOSAL BY TVS | OPERATING MODE | OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP) | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | SCENARIO ACTIVATION PROPOSAL BY TVS : INACTIVE/ACTIVE | [37 empty] | 1 | 1 | 0 | YES | ScenAct
B1.5 | Y | TUN | TVS | EMERGENCY | ACTIVATION STATUS OF EMERGENCY SCENARIO | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | ACTIVATION STATUS OF EMERGENCY SCENARIO : INACTIVE/ACTIVE | [37 empty] | 1 | 1 | 2 | YES | ActEmerg
B1.5 | Y | TUN | TVS | EMERGENCY | SCENARIO CONFIRMATION BY SCADA OPERATOR SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | SCENARIO CONFIRMATION |  |  |  | 2 | SCENARIO ACTIVATION PROPOSAL BY TVS = ACTIVE and ACTIVATION STATUS OF EMERGENCY SCENARIO = INACTIVE |  | SCENARIO CONFIRMATION BY SCADA OPERATOR SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 1 |  | NO | CmdSelMan
B1.5 | Y | TUN | TVS | EMERGENCY | SCENARIO CONFIRMATION BY SCADA OPERATOR SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCENARIO CONFIRMATION BY SCADA OPERATOR SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 4 | NO | AckSelMan
B1.5 | Y | TUN | TVS | EMERGENCY | SCENARIO CONFIRMATION BY SCADA OPERATOR EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | SCENARIO CONFIRMATION |  |  |  | 10 | SCENARIO ACTIVATION PROPOSAL BY TVS = ACTIVE and ACTIVATION STATUS OF EMERGENCY SCENARIO = INACTIVE |  | SCENARIO CONFIRMATION BY SCADA OPERATOR EXECUTE ACK = ACKNOWLEDGE and ACTIVATION STATUS OF EMERGENCY SCENARIO = ACTIVE | [28 empty] | 1 | 2 |  | NO | CmdExeMan
B1.5 | Y | TUN | TVS | EMERGENCY | SCENARIO CONFIRMATION BY SCADA OPERATOR EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCENARIO CONFIRMATION BY SCADA OPERATOR EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 6 | NO | AckExeMan
B1.5 | Y | + |  |  | MAIN UNDERGROUND LINE AVERAGE TEMPERATURE
B1.5 | Y | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 1 | AVERAGE TUNNEL TEMPERATURE ZONE 1 | AVERAGE TUNNEL TEMPERATURE ZONE 1 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 1 |  | YES | Zone1
B1.5 | Y | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 2 | AVERAGE TUNNEL TEMPERATURE ZONE 2 | AVERAGE TUNNEL TEMPERATURE ZONE 2 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 3 |  | YES | Zone2
B1.5 | Y | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 3 | AVERAGE TUNNEL TEMPERATURE ZONE 3 | AVERAGE TUNNEL TEMPERATURE ZONE 3 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 5 |  | YES | Zone3
B1.5 | Y | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 4 | AVERAGE TUNNEL TEMPERATURE ZONE 4 | AVERAGE TUNNEL TEMPERATURE ZONE 4 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 7 |  | YES | Zone4
B1.5 | Y | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 5 | AVERAGE TUNNEL TEMPERATURE ZONE 5 | AVERAGE TUNNEL TEMPERATURE ZONE 5 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 9 |  | YES | Zone5
B1.5 | Y | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 6 | AVERAGE TUNNEL TEMPERATURE ZONE 6 | AVERAGE TUNNEL TEMPERATURE ZONE 6 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 11 |  | YES | Zone6
B1.5 | Y | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 7 | AVERAGE TUNNEL TEMPERATURE ZONE 7 | AVERAGE TUNNEL TEMPERATURE ZONE 7 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 13 |  | YES | Zone7
B1.5 | Y | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 8 | AVERAGE TUNNEL TEMPERATURE ZONE 8 | AVERAGE TUNNEL TEMPERATURE ZONE 8 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 15 |  | YES | Zone8
B1.5 | Y | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 9 | AVERAGE TUNNEL TEMPERATURE ZONE 9 | AVERAGE TUNNEL TEMPERATURE ZONE 9 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 17 |  | YES | Zone9
B1.5 | Y | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 10 | AVERAGE TUNNEL TEMPERATURE ZONE 10 | AVERAGE TUNNEL TEMPERATURE ZONE 10 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 19 |  | YES | Zone10
B1.5 | Y | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 11 | AVERAGE TUNNEL TEMPERATURE ZONE 11 | AVERAGE TUNNEL TEMPERATURE ZONE 11 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 21 |  | YES | Zone11
B1.5 | Y | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 12 | AVERAGE TUNNEL TEMPERATURE ZONE 12 | AVERAGE TUNNEL TEMPERATURE ZONE 12 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 23 |  | YES | Zone12
B1.5 | Y | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 13 | AVERAGE TUNNEL TEMPERATURE ZONE 13 | AVERAGE TUNNEL TEMPERATURE ZONE 13 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 25 |  | YES | Zone13
B1.5 | Y | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 14 | AVERAGE TUNNEL TEMPERATURE ZONE 14 | AVERAGE TUNNEL TEMPERATURE ZONE 14 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 27 |  | YES | Zone14
B1.5 | Y | TUN | TVS | MUL | AVERAGE TUNNEL TEMPERATURE ZONE 15 | AVERAGE TUNNEL TEMPERATURE ZONE 15 | AVERAGE TUNNEL TEMPERATURE ZONE 15 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 29 |  | YES | Zone15
B1.5 | Y | TUN | TVS | MUL | AVERAGE OUTDOOR TEMPERATURE | AVERAGE OUTDOOR TEMPERATURE | AVERAGE OUTDOOR TEMPERATURE | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 31 |  | YES | OutTem
B1.5 | Y | + |  |  | FOXHILL LINE AVERAGE TEMPERATURE
B1.5 | Y | TUN | TVS | FXL | AVERAGE TUNNEL TEMPERATURE ZONE 16 | AVERAGE TUNNEL TEMPERATURE ZONE 16 | AVERAGE TUNNEL TEMPERATURE ZONE 16 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 1 |  | YES | Zone16
B1.5 | Y | TUN | TVS | FXL | AVERAGE TUNNEL TEMPERATURE ZONE 17 | AVERAGE TUNNEL TEMPERATURE ZONE 17 | AVERAGE TUNNEL TEMPERATURE ZONE 17 | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 3 |  | YES | Zone17
B1.5 | Y | TUN | TVS | FXL | AVERAGE OUTDOOR TEMPERATURE | AVERAGE OUTDOOR TEMPERATURE | AVERAGE OUTDOOR TEMPERATURE | Operational Event |  | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 5 |  | YES | OutTem
B0.9 | Y | + |  |  | TUNNEL VENTILATION FAN (TVF)
B1.3 | Y | TUN | TVS | TVF | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OFF | LOCAL | REMOTE | INCONSISTANT | REMOTE | 0: Crit, 1: Maj, 2: None, 3: Crit | ELECTRICAL PANEL SELECTOR SWITCH STATUS : OFF/LOCAL/REMOTE/INCONSISTANT | [37 empty] | 2 | 1 | 0 | YES | SwitchStat
B1.3 | Y | TUN | TVS | TVF | OPERATING MODE | OPERATING MODE | OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP) | Operational Event |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | AUTO SCADA | MANUAL SCADA |  |  | AUTO SCADA | 0: None, 1: None | OPERATING MODE : AUTO SCADA/MANUAL SCADA | [37 empty] | 1 | 1 | 2 | YES | OperatingMode
B2.1 | Y | TUN | TVS | TVF | RUN STATUS | RUN STATUS | SUPPLY / EXHAUST / STOP STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | STOP | REVERSE | FORWARD | INCONSISTANT | STOP | 0: None, 1: None, 2: None, 3: Crit | RUN STATUS : STOP/REVERSE/FORWARD/INCONSISTANT | [37 empty] | 2 | 1 | 4 | YES | RunStatus
B1.1 | Y | TUN | TVS | TVF | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | Command |  | DO | SIL0 | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE AUTO MODE |  |  |  | 10 | OPERATING MODE = MANUAL SCADA |  | OPERATING MODE = AUTO SCADA | [28 empty] | 1 | 1 |  | NO | CmdAuto
B1.1 | Y | TUN | TVS | TVF | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 2 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 2 |  | NO | CmdSelMan
B1.1 | Y | TUN | TVS | TVF | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 6 | NO | AckSelMan
B1.1 | Y | TUN | TVS | TVF | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 10 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE EXECUTE ACK = ACKNOWLEDGE and OPERATING MODE = MANUAL SCADA | [28 empty] | 1 | 3 |  | NO | CmdExeMan
B1.1 | Y | TUN | TVS | TVF | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 8 | NO | AckExeMan
B1.2 | Y | TUN | TVS | TVF | VSD ELECTRICAL STATUS | VSD ELECTRICAL STATUS | VSD ELECTRICAL STATUS | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | VSD ELECTRICAL STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 10 | NO | EleStat
B1.2 | Y | TUN | TVS | TVF | VSD FAIL TO START STATUS | VSD FAIL TO START | VSD FAIL TO START | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | VSD FAIL TO START STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 12 | NO | StartStat
B1.2 | Y | TUN | TVS | TVF | VSD FAIL TO STOP STATUS | VSD FAIL TO STOP | VSD FAIL TO STOP | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | VSD FAIL TO STOP STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 14 | NO | StopStat
B1.3 | Y | TUN | TVS | TVF | VSD SPEED FREQUENCY | VSD SPEED FREQUENCY | VSD SPEED FREQUENCY | Meter | Daily | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | Hz | 0 | 60 | [14 empty] | UINT | [10 empty] | 32 | 2 |  | YES | SpeedFreq
B1.2 | Y | TUN | TVS | TVF | VSD SPEED ORDER | VSD SPEED ORDER | VSD SPEED ORDER | Command |  | DO2 | SIL0 | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | LOW SPEED | HIGH SPEED | INVALID |  | NA | No initial condition Toggle command, either low or high selected | No final condition Toggle command, either low or high selected | No associated return status Change on VSD SPEED FREQUENCY AI | [28 empty] | 2 | 4 |  | NO | CmdSpeedOrd
B1.1 | Y | TUN | TVS | TVF | STOP ORDER (VSD) SELECT | STOP ORDER (VSD) SELECT | STOP ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | STOP SELECTION |  |  |  | 2 | RUN STATUS = FORWARD or RUN STATUS = REVERSE |  | STOP ORDER (VSD) SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 5 |  | NO | CmdSelStop
B1.1 | Y | TUN | TVS | TVF | STOP ORDER (VSD) SELECT ACK | STOP ORDER (VSD) SELECT ACK | STOP ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | STOP ORDER (VSD) SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 4 | 0 | NO | AckSelStop
B1.1 | Y | TUN | TVS | TVF | STOP ORDER (VSD) EXECUTE | STOP ORDER (VSD) EXECUTE | STOP ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | STOP CONFIRMATION |  |  |  | 40 | RUN STATUS = FORWARD or RUN STATUS = REVERSE |  | STOP ORDER (VSD) EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = STOP | [28 empty] | 1 | 6 |  | NO | CmdExeStop
B1.1 | Y | TUN | TVS | TVF | STOP ORDER (VSD) EXECUTE ACK | STOP ORDER (VSD) EXECUTE ACK | STOP ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | STOP ORDER (VSD) EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 4 | 2 | NO | AckExeStop
B1.1 | Y | TUN | TVS | TVF | FORWARD ORDER (VSD) SELECT | FORWARD ORDER (VSD) SELECT | FORWARD DIRECTION ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | FORWARD SELECTION |  |  |  | 2 | RUN STATUS = STOP |  | FORWARD ORDER (VSD) SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 7 |  | NO | CmdSelFwOrd
B1.1 | Y | TUN | TVS | TVF | FORWARD ORDER (VSD) SELECT ACK | FORWARD ORDER (VSD) SELECT ACK | FORWARD DIRECTION ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | FORWARD ORDER (VSD) SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 4 | 4 | NO | AckSelFwOrd
B1.1 | Y | TUN | TVS | TVF | FORWARD ORDER (VSD) EXECUTE | FORWARD ORDER (VSD) EXECUTE | FORWARD DIRECTION ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | FORWARD CONFIRMATION |  |  |  | 40 | RUN STATUS = STOP |  | FORWARD ORDER (VSD) EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = FORWARD | [28 empty] | 1 | 8 |  | NO | CmdExeFwOrd
B1.1 | Y | TUN | TVS | TVF | FORWARD ORDER (VSD) EXECUTE ACK | FORWARD ORDER (VSD) EXECUTE ACK | FORWARD DIRECTION ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | FORWARD ORDER (VSD) EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 4 | 6 | NO | AckExeFwOrd
B1.1 | Y | TUN | TVS | TVF | REVERSE ORDER (VSD) SELECT | REVERSE ORDER (VSD) SELECT | REVERSE DIRECTION ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | REVERSE SELECTION |  |  |  | 2 | RUN STATUS = STOP |  | REVERSE ORDER (VSD) SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 9 |  | NO | CmdSelRvOrd
B1.1 | Y | TUN | TVS | TVF | REVERSE ORDER (VSD) SELECT ACK | REVERSE ORDER (VSD) SELECT ACK | REVERSE DIRECTION ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | REVERSE ORDER (VSD) SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 4 | 8 | NO | AckSelRvOrd
B1.1 | Y | TUN | TVS | TVF | REVERSE ORDER (VSD) EXECUTE | REVERSE ORDER (VSD) EXECUTE | REVERSE DIRECTION ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | REVERSE CONFIRMATION |  |  |  | 40 | RUN STATUS = STOP |  | REVERSE ORDER (VSD) EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = REVERSE | [28 empty] | 1 | 10 |  | NO | CmdExeRvOrd
B1.1 | Y | TUN | TVS | TVF | REVERSE ORDER (VSD) EXECUTE ACK | REVERSE ORDER (VSD) EXECUTE ACK | REVERSE DIRECTION ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | REVERSE ORDER (VSD) EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 4 | 10 | NO | AckExeRvOrd
B1.2 | Y | TUN | TVS | TVF | FAN AVAILABILITY STATUS | FAN AVAILABILITY STATUS | FAN UNAVAILABLE STATUS | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | AVAILABLE | UNAVAILABLE |  |  | AVAILABLE | 0: None, 1: Crit | FAN AVAILABILITY STATUS : AVAILABLE/UNAVAILABLE | [37 empty] | 1 | 4 | 12 | NO | AvailStat
B1.2 | Y | TUN | TVS | TVF | CIRCUIT BREAKER POSITION | CIRCUIT BREAKER OPEN | VSD CIRCUIT BREAKER OPEN | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OPEN | CLOSE |  |  | OPEN | 0: None, 1: None | CIRCUIT BREAKER POSITION : OPEN/CLOSE | [37 empty] | 1 | 4 | 14 | NO | CirPos
B1.2 | Y | TUN | TVS | TVF | CIRCUIT BREAKER TRIPPED STATUS | CIRCUIT BREAKER OUTAGE | VSD CIRCUIT BREAKER FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Crit | CIRCUIT BREAKER TRIPPED STATUS : NORMAL/TRIPPED | [37 empty] | 1 | 5 | 0 | NO | CirTrip
B1.2 | Y | TUN | TVS | TVF | FAN HEATER CIRCUIT BREAKER POSITION | FAN HEATER CIRCUIT BREAKER OPEN | FAN HEATER CIRCUIT BREAKER OPEN | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OPEN | CLOSE |  |  | OPEN | 0: None, 1: None | FAN HEATER CIRCUIT BREAKER POSITION : OPEN/CLOSE | [37 empty] | 1 | 5 | 1 | NO | FanPos
B1.2 | Y | TUN | TVS | TVF | FAN HEATER CIRCUIT BREAKER TRIPPED STATUS | FAN HEATER CIRCUIT BREAKER OUTAGE | FAN HEATER CIRCUIT BREAKER FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | FAN HEATER CIRCUIT BREAKER TRIPPED STATUS : NORMAL/TRIPPED | [37 empty] | 1 | 5 | 2 | NO | FanTrip
B1.2 | Y | TUN | TVS | TVF | FORWARD START-UP MISMATCH OUTAGE STATUS | FORWARD START-UP MISMATCH OUTAGE | FORWARD COMMAND MISMATCH ALARM | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | FORWARD START-UP MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 5 | 3 | NO | ForOut
B1.2 | Y | TUN | TVS | TVF | REVERSE START-UP MISMATCH OUTAGE STATUS | REVERSE START-UP MISMATCH OUTAGE | REVERSE COMMAND MISMATCH ALARM | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | REVERSE START-UP MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 5 | 4 | NO | RevOut
B1.2 | Y | TUN | TVS | TVF | STOP MISMATCH OUTAGE STATUS | STOP MISMATCH OUTAGE | STOP COMMAND MISMATCH ALARM | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | STOP MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 5 | 5 | NO | StopOut
B1.2 | Y | TUN | TVS | TVF | WINDING TEMPERATURE STATUS | WINDING TEMPERATURE | WINDING TEMPERATURE FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | WINDING TEMPERATURE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 5 | 6 | NO | WindTem
B1.2 | Y | TUN | TVS | TVF | FRONT BEARING TEMPERATURE STATUS | FRONT BEARING TEMPERATURE 1 FAULT | FRONT BEARING TEMPERATURE 1 FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | FRONT BEARING TEMPERATURE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 5 | 7 | NO | FrontTem
B1.2 | Y | TUN | TVS | TVF | REAR BEARING TEMPERATURE STATUS | REAR BEARING TEMPERATURE 1 FAULT | REAR BEARING TEMPERATURE 1 FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | REAR BEARING TEMPERATURE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 5 | 8 | NO | RearTem
B1.2 | Y | TUN | TVS | TVF | VIBRATION 1ST LEVEL STATUS | VIBRATION 1ST LEVEL ALARM | VIBRATION 1ST LEVEL ALARM | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VIBRATION 1ST LEVEL STATUS : NORMAL/FAULTY | [37 empty] | 1 | 5 | 9 | NO | Vib1
B1.2 | Y | TUN | TVS | TVF | VIBRATION 2ND LEVEL STATUS | VIBRATION 2ND LEVEL ALARM | VIBRATION 2ND LEVEL ALARM | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | VIBRATION 2ND LEVEL STATUS : NORMAL/FAULTY | [37 empty] | 1 | 5 | 10 | NO | Vib2
B1.2 | Y | TUN | TVS | TVF | MORE THAN 10 STARTUP PER HOUR STATUS | MORE THAN 6 STARTUP PER HOUR | MORE THAN 6 STARTUP PER HOUR | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | MORE THAN 10 STARTUP PER HOUR STATUS : NORMAL/FAULTY | [37 empty] | 1 | 5 | 11 | NO | More10
B1.2 | Y | TUN | TVS | TVF | RUNNING HOURS | RUNNING HOURS | RUNNING HOURS | Meter | Daily | AI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | h | 0 | 65535 | [14 empty] | UINT | [10 empty] | 16 | 6 |  | NO | RunHrs
B0.9 | Y | + |  |  | JET FAN
B1.3 | Y | TUN | TVS | JET | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OFF | LOCAL | REMOTE | INCONSISTANT | REMOTE | 0: Crit, 1: Maj, 2: None, 3: Crit | ELECTRICAL PANEL SELECTOR SWITCH STATUS : OFF/LOCAL/REMOTE/INCONSISTANT | [37 empty] | 2 | 1 | 0 | YES | SwitchStat
B1.3 | Y | TUN | TVS | JET | OPERATING MODE | OPERATING MODE | OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP) | Operational Event |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | AUTO SCADA | MANUAL SCADA |  |  | AUTO SCADA | 0: None, 1: None | OPERATING MODE : AUTO SCADA/MANUAL SCADA | [37 empty] | 1 | 1 | 2 | YES | OperatingMode
B2.1 | Y | TUN | TVS | JET | RUN STATUS | RUN STATUS | SUPPLY / EXHAUST / STOP STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | STOP | REVERSE | FORWARD | INCONSISTANT | STOP | 0: None, 1: None, 2: None, 3: Crit | RUN STATUS : STOP/REVERSE/FORWARD/INCONSISTANT | [37 empty] | 2 | 1 | 4 | YES | RunStatus
B1.1 | Y | TUN | TVS | JET | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | Command |  | DO | SIL0 | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE AUTO MODE |  |  |  | 10 | OPERATING MODE = MANUAL SCADA |  | OPERATING MODE = AUTO SCADA | [28 empty] | 1 | 1 |  | NO | CmdAutoCom
B1.1 | Y | TUN | TVS | JET | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 2 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 2 |  | NO | CmdSelMan
B1.1 | Y | TUN | TVS | JET | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 6 | NO | AckSelMan
B1.1 | Y | TUN | TVS | JET | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 10 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE EXECUTE ACK = ACKNOWLEDGE and OPERATING MODE = MANUAL SCADA | [28 empty] | 1 | 3 |  | NO | CmdExeMan
B1.1 | Y | TUN | TVS | JET | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 8 | NO | AckExeMan
B1.2 | Y | TUN | TVS | JET | VSD ELECTRICAL STATUS | VSD ELECTRICAL STATUS | VSD ELECTRICAL STATUS | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | VSD ELECTRICAL STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 10 | NO | EleStat
B1.2 | Y | TUN | TVS | JET | VSD FAIL TO START STATUS | VSD FAIL TO START | VSD FAIL TO START | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | VSD FAIL TO START STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 12 | NO | FailStart
B1.2 | Y | TUN | TVS | JET | VSD FAIL TO STOP STATUS | VSD FAIL TO STOP | VSD FAIL TO STOP | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | VSD FAIL TO STOP STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 14 | NO | FailStop
B1.2 | Y | TUN | TVS | JET | VSD SPEED FREQUENCY | VSD SPEED FREQUENCY | VSD SPEED FREQUENCY | Meter | Daily | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | Hz | 0 | 60 | [14 empty] | UINT | [10 empty] | 32 | 2 |  | YES | SpeedFrep
B1.2 | Y | TUN | TVS | JET | VSD SPEED ORDER | VSD SPEED ORDER | VSD SPEED ORDER | Command |  | DO | SIL0 | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | HIGH SPEED |  |  |  | NA | No initial condition Toggle command, either low or high selected | No final condition Toggle command, either low or high selected | No associated return status Change on VSD SPEED FREQUENCY AI | [28 empty] | 1 | 4 |  | NO | CmdSpeedOrd
B1.1 | Y | TUN | TVS | JET | STOP ORDER (VSD) SELECT | STOP ORDER (VSD) SELECT | STOP ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | STOP SELECTION |  |  |  | 2 | RUN STATUS = FORWARD or RUN STATUS = REVERSE |  | STOP ORDER (VSD) SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 5 |  | NO | CmdSelStop
B1.1 | Y | TUN | TVS | JET | STOP ORDER (VSD) SELECT ACK | STOP ORDER (VSD) SELECT ACK | STOP ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | STOP ORDER (VSD) SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 4 | 0 | NO | AckSelStop
B1.1 | Y | TUN | TVS | JET | STOP ORDER (VSD) EXECUTE | STOP ORDER (VSD) EXECUTE | STOP ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | STOP CONFIRMATION |  |  |  | 40 | RUN STATUS = FORWARD or RUN STATUS = REVERSE |  | STOP ORDER (VSD) EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = STOP | [28 empty] | 1 | 6 |  | NO | CmdExeStop
B1.1 | Y | TUN | TVS | JET | STOP ORDER (VSD) EXECUTE ACK | STOP ORDER (VSD) EXECUTE ACK | STOP ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | STOP ORDER (VSD) EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 4 | 2 | NO | AckExeStop
B1.1 | Y | TUN | TVS | JET | FORWARD ORDER (VSD) SELECT | FORWARD ORDER (VSD) SELECT | FORWARD DIRECTION ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | FORWARD SELECTION |  |  |  | 2 | RUN STATUS = STOP |  | FORWARD ORDER (VSD) SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 7 |  | NO | CmdSelFwOrd
B1.1 | Y | TUN | TVS | JET | FORWARD ORDER (VSD) SELECT ACK | FORWARD ORDER (VSD) SELECT ACK | FORWARD DIRECTION ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | FORWARD ORDER (VSD) SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 4 | 4 | NO | AckSelFwOrd
B1.1 | Y | TUN | TVS | JET | FORWARD ORDER (VSD) EXECUTE | FORWARD ORDER (VSD) EXECUTE | FORWARD DIRECTION ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | FORWARD CONFIRMATION |  |  |  | 40 | RUN STATUS = STOP |  | FORWARD ORDER (VSD) EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = FORWARD | [28 empty] | 1 | 8 |  | NO | CmdExeFwOrd
B1.1 | Y | TUN | TVS | JET | FORWARD ORDER (VSD) EXECUTE ACK | FORWARD ORDER (VSD) EXECUTE ACK | FORWARD DIRECTION ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | FORWARD ORDER (VSD) EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 4 | 6 | NO | AckExeFwOrd
B1.1 | Y | TUN | TVS | JET | REVERSE ORDER (VSD) SELECT | REVERSE ORDER (VSD) SELECT | REVERSE DIRECTION ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | REVERSE SELECTION |  |  |  | 2 | RUN STATUS = STOP |  | REVERSE ORDER (VSD) SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 9 |  | NO | CmdSelRvOrd
B1.1 | Y | TUN | TVS | JET | REVERSE ORDER (VSD) SELECT ACK | REVERSE ORDER (VSD) SELECT ACK | REVERSE DIRECTION ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | REVERSE ORDER (VSD) SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 4 | 8 | NO | AckSelRvOrd
B1.1 | Y | TUN | TVS | JET | REVERSE ORDER (VSD) EXECUTE | REVERSE ORDER (VSD) EXECUTE | REVERSE DIRECTION ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | REVERSE CONFIRMATION |  |  |  | 40 | RUN STATUS = STOP |  | REVERSE ORDER (VSD) EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = REVERSE | [28 empty] | 1 | 10 |  | NO | CmdExeRvOrd
B1.1 | Y | TUN | TVS | JET | REVERSE ORDER (VSD) EXECUTE ACK | REVERSE ORDER (VSD) EXECUTE ACK | REVERSE DIRECTION ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | REVERSE ORDER (VSD) EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 4 | 10 | NO | AckExeRvOrd
B1.1 | Y | TUN | TVS | JET | FAN AVAILABILITY STATUS | FAN AVAILABILITY STATUS | FAN UNAVAILABLE STATUS | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | AVAILABLE | UNAVAILABLE |  |  | AVAILABLE | 0: None, 1: Crit | FAN AVAILABILITY STATUS : AVAILABLE/UNAVAILABLE | [37 empty] | 1 | 5 | 0 | NO | AvailStat
B1.3 | Y | TUN | TVS | JET | CIRCUIT BREAKER POSITION | CIRCUIT BREAKER OPEN | VSD CIRCUIT BREAKER OPEN | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OPEN | CLOSE |  |  | OPEN | 0: None, 1: None | CIRCUIT BREAKER POSITION : OPEN/CLOSE | [37 empty] | 1 | 5 | 1 | NO | CirOpen
B1.3 | Y | TUN | TVS | JET | CIRCUIT BREAKER TRIPPED STATUS | CIRCUIT BREAKER OUTAGE | VSD CIRCUIT BREAKER FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Crit | CIRCUIT BREAKER TRIPPED STATUS : NORMAL/TRIPPED | [37 empty] | 1 | 5 | 2 | NO | CirOut
B1.3 | Y | TUN | TVS | JET | FAN HEATER CIRCUIT BREAKER POSITION | FAN HEATER CIRCUIT BREAKER OPEN | FAN HEATER CIRCUIT BREAKER OPEN | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OPEN | CLOSE |  |  | OPEN | 0: None, 1: None | FAN HEATER CIRCUIT BREAKER POSITION : OPEN/CLOSE | [37 empty] | 1 | 5 | 3 | NO | FanOpen
B1.3 | Y | TUN | TVS | JET | FAN HEATER CIRCUIT BREAKER TRIPPED STATUS | FAN HEATER CIRCUIT BREAKER OUTAGE | FAN HEATER CIRCUIT BREAKER FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | FAN HEATER CIRCUIT BREAKER TRIPPED STATUS : NORMAL/TRIPPED | [37 empty] | 1 | 5 | 4 | NO | FanOut
B1.2 | Y | TUN | TVS | JET | FORWARD START-UP MISMATCH OUTAGE STATUS | FORWARD START-UP MISMATCH OUTAGE | FORWARD COMMAND MISMATCH ALARM | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | FORWARD START-UP MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 5 | 5 | NO | ForOut
B1.2 | Y | TUN | TVS | JET | REVERSE START-UP MISMATCH OUTAGE STATUS | REVERSE START-UP MISMATCH OUTAGE | REVERSE COMMAND MISMATCH ALARM | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | REVERSE START-UP MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 5 | 6 | NO | RevOut
B1.2 | Y | TUN | TVS | JET | STOP MISMATCH OUTAGE STATUS | STOP MISMATCH OUTAGE | STOP COMMAND MISMATCH ALARM | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | STOP MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 5 | 7 | NO | StopOut
B1.2 | Y | TUN | TVS | JET | WINDING TEMPERATURE STATUS | WINDING TEMPERATURE | WINDING TEMPERATURE FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | WINDING TEMPERATURE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 5 | 8 | NO | WindTem
B1.2 | Y | TUN | TVS | JET | FRONT BEARING TEMPERATURE STATUS | FRONT BEARING TEMPERATURE 1 | FRONT BEARING TEMPERATURE 1 FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | FRONT BEARING TEMPERATURE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 5 | 9 | NO | FrontTem1
B1.2 | Y | TUN | TVS | JET | REAR BEARING TEMPERATURE STATUS | REAR BEARING TEMPERATURE 1 | REAR BEARING TEMPERATURE 1 FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | REAR BEARING TEMPERATURE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 5 | 10 | NO | RearTem
B1.2 | Y | TUN | TVS | JET | VIBRATION 1ST LEVEL STATUS | VIBRATION 1ST LEVEL | VIBRATION 1ST LEVEL ALARM | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VIBRATION 1ST LEVEL STATUS : NORMAL/FAULTY | [37 empty] | 1 | 5 | 11 | NO | Vib1
B1.2 | Y | TUN | TVS | JET | VIBRATION 2ND LEVEL STATUS | VIBRATION 2ND LEVEL | VIBRATION 2ND LEVEL FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | VIBRATION 2ND LEVEL STATUS : NORMAL/FAULTY | [37 empty] | 1 | 5 | 12 | NO | Vib2
B1.2 | Y | TUN | TVS | JET | MORE THAN 10 STARTUP PER HOUR STATUS | MORE THAN 6 STARTUP PER HOUR | MORE THAN 6 STARTUP PER HOUR | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | MORE THAN 10 STARTUP PER HOUR STATUS : NORMAL/FAULTY | [37 empty] | 1 | 5 | 13 | NO | More6hr
B1.2 | Y | TUN | TVS | JET | RUNNING HOURS | RUNNING HOURS | RUNNING HOURS | Meter | Daily | AI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | h | 0 | 65535 | [14 empty] | UINT | [10 empty] | 16 | 6 |  | NO | RunHrs
B0.9 | Y | + |  |  | TVS DAMPER [TVD] : BYPASS DAMPER (BDP) / TUNNEL DAMPER (TDP)
B1.3 | Y | TUN | TVS | TVD | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OFF | LOCAL | REMOTE | INCONSISTANT | REMOTE | 0: Crit, 1: Maj, 2: None, 3: Crit | ELECTRICAL PANEL SELECTOR SWITCH STATUS : OFF/LOCAL/REMOTE/INCONSISTANT | [37 empty] | 2 | 1 | 0 | YES | SwitchStat
B1.3 | Y | TUN | TVS | TVD | OPERATING MODE | OPERATING MODE | OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP) | Operational Event |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | AUTO SCADA | MANUAL SCADA |  |  | AUTO SCADA | 0: None, 1: None | OPERATING MODE : AUTO SCADA/MANUAL SCADA | [37 empty] | 1 | 1 | 2 | YES | OpMod
B1.5 | Y | TUN | TVS | TVD | ARRAY STATUS | STATUS | DAMPER OPENED STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INCONSISTANT | OPEN | CLOSED | INCONSISTANT | CLOSED | 0: Maj, 1: None, 2: None, 3: Crit | ARRAY STATUS : INCONSISTANT/OPEN/CLOSED/INCONSISTANT | [37 empty] | 2 | 1 | 4 | YES | Stat
B1.1 | Y | TUN | TVS | TVD | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | Command |  | DO | SIL0 | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE AUTO MODE |  |  |  | 10 | OPERATING MODE = MANUAL SCADA |  | OPERATING MODE = AUTO SCADA | [28 empty] | 1 | 1 |  | NO | CmdAuto
B1.1 | Y | TUN | TVS | TVD | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 2 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 2 |  | NO | CmdSelMan
B1.1 | Y | TUN | TVS | TVD | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 6 | NO | AckSelMan
B1.1 | Y | TUN | TVS | TVD | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 10 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE EXECUTE ACK = ACKNOWLEDGE and OPERATING MODE = MANUAL SCADA | [28 empty] | 1 | 3 |  | NO | CmdExeMan
B1.1 | Y | TUN | TVS | TVD | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 8 | NO | AckExeMan
B1.1 | Y | TUN | TVS | TVD | OPEN ORDER SELECT | OPEN ORDER SELECT | OPEN ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | OPEN SELECTION |  |  |  | 2 | STATUS = CLOSE |  | OPEN ORDER SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 4 |  | NO | CmdSelOpen
B1.1 | Y | TUN | TVS | TVD | OPEN ORDER SELECT ACK | OPEN ORDER SELECT ACK | OPEN ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | OPEN ORDER SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 10 | NO | AckSelOpen
B1.1 | Y | TUN | TVS | TVD | OPEN ORDER EXECUTE | OPEN ORDER EXECUTE | OPEN ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | OPEN CONFIRMATION |  |  |  | 40 | STATUS = CLOSE |  | OPEN ORDER EXECUTE ACK = ACKNOWLEDGE and STATUS = OPEN | [28 empty] | 1 | 5 |  | NO | CmdExeOpen
B1.1 | Y | TUN | TVS | TVD | OPEN ORDER EXECUTE ACK | OPEN ORDER EXECUTE ACK | OPEN ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | OPEN ORDER EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 12 | NO | AckExeOpen
B1.1 | Y | TUN | TVS | TVD | CLOSE ORDER SELECT | CLOSE ORDER SELECT | CLOSE ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | CLOSE SELECTION |  |  |  | 2 | STATUS = OPEN |  | CLOSE ORDER SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 6 |  | NO | CmdSelClose
B1.1 | Y | TUN | TVS | TVD | CLOSE ORDER SELECT ACK | CLOSE ORDER SELECT ACK | CLOSE ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | CLOSE ORDER SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 14 | NO | AckSelClose
B1.1 | Y | TUN | TVS | TVD | CLOSE ORDER EXECUTE | CLOSE ORDER EXECUTE | CLOSE ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | CLOSE CONFIRMATION |  |  |  | 40 | STATUS = OPEN |  | CLOSE ORDER EXECUTE ACK = ACKNOWLEDGE and STATUS = CLOSE | [28 empty] | 1 | 7 |  | NO | CmdExeClose
B1.1 | Y | TUN | TVS | TVD | CLOSE ORDER EXECUTE ACK | CLOSE ORDER EXECUTE ACK | CLOSE ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | CLOSE ORDER EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 2 | 0 | NO | AckExeClose
B1.3 | Y | TUN | TVS | TVD | DAMPER SUPPLY CIRCUIT BREAKER POSITION | DAMPER SUPPLY CIRCUIT BREAKER OPEN | DAMPER SUPPLY CIRCUIT BREAKER OPEN | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OPEN | CLOSE |  |  | OPEN | 0: None, 1: None | DAMPER SUPPLY CIRCUIT BREAKER POSITION : OPEN/CLOSE | [37 empty] | 1 | 2 | 2 | NO | DamOpen
B1.3 | Y | TUN | TVS | TVD | DAMPER SUPPLY CIRCUIT BREAKER TRIPPED STATUS | DAMPER SUPPLY CIRCUIT BREAKER OUTAGE | DAMPER SUPPLY CIRCUIT BREAKER FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Crit | DAMPER SUPPLY CIRCUIT BREAKER TRIPPED STATUS : NORMAL/TRIPPED | [37 empty] | 1 | 2 | 4 | NO | DamOut
B1.3 | Y | TUN | TVS | TVD | OPEN MISMATCH OUTAGE STATUS | FAIL TO OPEN STATUS | OPEN MISMATCH ALARM | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | OPEN MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 2 | 6 | NO | FailOpen
B1.3 | Y | TUN | TVS | TVD | CLOSE MISMATCH OUTAGE STATUS | FAIL TO CLOSE STATUS | CLOSE MISMATCH ALARM | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | CLOSE MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 2 | 8 | NO | FailClose
B1.3 | Y | + |  |  | ISOLATION DAMPER (IDP)
B1.3 | N | TUN | TVS | IDP | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OFF | LOCAL | REMOTE | INCONSISTANT | REMOTE | 0: Crit, 1: Maj, 2: None, 3: Crit | ELECTRICAL PANEL SELECTOR SWITCH STATUS : OFF/LOCAL/REMOTE/INCONSISTANT | [37 empty] | 2 | 1 | 0 | YES | SwitchStat
B1.5 | N | TUN | TVS | IDP | ARRAY STATUS | STATUS | DAMPER OPENED STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INCONSISTANT | OPEN | CLOSED | INCONSISTANT | CLOSED | 0: Maj, 1: None, 2: None, 3: Crit | ARRAY STATUS : INCONSISTANT/OPEN/CLOSED/INCONSISTANT | [37 empty] | 2 | 1 | 2 | YES | Stat
B1.3 | N | TUN | TVS | IDP | DAMPER SUPPLY CIRCUIT BREAKER POSITION | IDP-MCB-H closed status | IDP-MCB-H closed status | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OPEN | CLOSE |  |  | OPEN | 0: None, 1: None | DAMPER SUPPLY CIRCUIT BREAKER POSITION : OPEN/CLOSE | [37 empty] | 1 | 1 | 4 | NO | CloseStat
B1.3 | N | TUN | TVS | IDP | DAMPER SUPPLY CIRCUIT BREAKER TRIPPED STATUS | IDP- MCB-H tripped status | IDP- MCB-H tripped status | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Crit | DAMPER SUPPLY CIRCUIT BREAKER TRIPPED STATUS : NORMAL/TRIPPED | [37 empty] | 1 | 1 | 6 | NO | TripStat
B1.3 | N | TUN | TVS | IDP | OPEN MISMATCH OUTAGE STATUS | FAIL TO OPEN STATUS | OPEN MISMATCH ALARM | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | OPEN MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 8 | NO | FailOpen
B1.3 | N | TUN | TVS | IDP | CLOSE MISMATCH OUTAGE STATUS | FAIL TO CLOSE STATUS | CLOSE MISMATCH ALARM | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | CLOSE MISMATCH OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 10 | NO | FailClose
B0.9 | Y | + |  |  | MOTORIZED SMOKE FIRE DAMPER (MSFD)
B1.5 | N | TUN | TVS | MSFD | ARRAY STATUS | STATUS | DAMPER OPENED STATUS | Operational Alarm |  | DI2 | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INCONSISTANT | OPEN | CLOSED | INCONSISTANT | CLOSED | 0: Maj, 1: None, 2: None, 3: Crit | ARRAY STATUS : INCONSISTANT/OPEN/CLOSED/INCONSISTANT | [37 empty] | 2 | 1 | 0 | YES | Stat
B1.5 | N | TUN | TVS | MSFD | DAMPER SUPPLY CIRCUIT BREAKER POSITION | MSFD - CON- MCB closed status | MSFD - CON- MCB closed status | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | OPEN | CLOSE |  |  | OPEN | 0: None, 1: None | DAMPER SUPPLY CIRCUIT BREAKER POSITION : OPEN/CLOSE | [37 empty] | 1 | 1 | 2 | NO | CloseStat
B1.5 | N | TUN | TVS | MSFD | DAMPER SUPPLY CIRCUIT BREAKER TRIPPED STATUS | MSFD - CON- MCB tripped status | MSFD - CON- MCB tripped status | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Crit | DAMPER SUPPLY CIRCUIT BREAKER TRIPPED STATUS : NORMAL/TRIPPED | [37 empty] | 1 | 1 | 4 | NO | TripStat
B1.5 | N | TUN | TVS | MSFD | LOCAL MODE STATUS | LOCAL MODE STATUS | LOCAL MODE STATUS | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | AUTO | LOCAL |  |  | AUTO | 0: None, 1: Crit | LOCAL MODE STATUS : AUTO/LOCAL | [37 empty] | 1 | 1 | 6 | NO | LocalMod
B0.9 | Y | + |  |  | OUTDOOR TEMPERATURE SENSOR (OTS)
B1.2 | Y | TUN | TVS | OTS | AVAILABILITY STATUS | AVAILABILITY STATUS | UNAVAILABLE STATUS | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | AVAILABLE | UNAVAILABLE |  |  | AVAILABLE | 0: None, 1: Maj | AVAILABILITY STATUS : AVAILABLE/UNAVAILABLE | [37 empty] | 1 | 1 | 0 | NO | AvailStat
B1.2 | Y | TUN | TVS | OTS | TEMPERATURE OUTAGE STATUS | SENSOR OUTAGE | SENSOR FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | TEMPERATURE OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 1 | NO | SenOut
B1.2 | Y | TUN | TVS | OTS | AVERAGE TEMPERATURE EXCLUSION STATUS | AVERAGE TEMPERATURE EXCLUSION | AVERAGE TEMPERATURE EXCLUSION | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | AVERAGE TEMPERATURE EXCLUSION STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 2 | NO | AveTem
B0.9 | Y | TUN | TVS | OTS | TEMPERATURE MEASUREMENT | TEMPERATURE MEASUREMENT | TEMPERATURE MEASUREMENT | Meter | Daily | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 2 |  | YES | TemMeasure
B1.1 | Y | + |  |  | TUNNEL TEMPERATURE/HUMIDITY SENSOR (TTS)
B1.1 | Y | TUN | TVS | TTS | AVAILABILITY STATUS | AVAILABILITY STATUS | UNAVAILABLE STATUS | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | AVAILABLE | UNAVAILABLE |  |  | AVAILABLE | 0: None, 1: Maj | AVAILABILITY STATUS : AVAILABLE/UNAVAILABLE | [37 empty] | 1 | 1 | 0 | NO | Availability
B1.2 | Y | TUN | TVS | TTS | TEMPERATURE SENSOR OUTAGE STATUS | TEMPERATURE SENSOR OUTAGE | TEMPERATURE SENSOR FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | TEMPERATURE SENSOR OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 1 | NO | TemOut
B1.2 | Y | TUN | TVS | TTS | HUMIDITY SENSOR OUTAGE STATUS | HUMIDITY SENSOR OUTAGE | HUMIDITY SENSOR FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | HUMIDITY SENSOR OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 2 | NO | HumOut
B1.2 | Y | TUN | TVS | TTS | AVERAGE TEMPERATURE EXCLUSION STATUS | AVERAGE TEMPERATURE EXCLUSION | AVERAGE TEMPERATURE EXCLUSION | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | AVERAGE TEMPERATURE EXCLUSION STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 3 | NO | AveTem
B0.9 | Y | TUN | TVS | TTS | TEMPERATURE MEASUREMENT | TEMPERATURE MEASUREMENT | TEMPERATURE MEASUREMENT | Meter | Daily | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | °C | -20 | 80 | [14 empty] | FLOAT | [10 empty] | 32 | 2 |  | YES | Temperature
B0.9 | Y | TUN | TVS | TTS | HUMIDITY MEASUREMENT | HUMIDITY MEASUREMENT | HUMIDITY MEASUREMENT | Meter | Daily | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | % | 0 | 100 | [14 empty] | FLOAT | [10 empty] | 32 | 4 |  | YES | Humidity
B0.9 | Y | + |  |  | VELOCITY SENSOR (VES)
B1.1 | Y | TUN | TVS | VS | AVAILABILITY STATUS | AVAILABILITY STATUS | UNAVAILABLE STATUS | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | AVAILABLE | UNAVAILABLE |  |  | AVAILABLE | 0: None, 1: Maj | AVAILABILITY STATUS : AVAILABLE/UNAVAILABLE | [37 empty] | 1 | 1 | 0 | NO | Availability
B1.2 | Y | TUN | TVS | VS | SENSOR OUTAGE STATUS | SENSOR OUTAGE | SENSOR FAULT | Technical Alarm | Daily | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SENSOR OUTAGE STATUS : NORMAL/FAULTY | [37 empty] | 1 | 1 | 1 | NO | SenStat
B0.9 | Y | TUN | TVS | VS | VELOCITY MEASUREMENT | VELOCITY MEASUREMENT | VELOCITY MEASUREMENT | Meter | Daily | AI2 | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | [16 empty] | m/s | -10 | 10 | [14 empty] | FLOAT | [10 empty] | 32 | 2 |  | YES | Velocity
B0.9 | Y | + |  |  | AIR HANDLING UNIT
B1.3 | Y | TUN | TVS | AHU | CONTROL MODE | OPERATING MODE | OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP) | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | REMOTE | LOCAL |  |  | REMOTE | 0: None, 1: Crit | CONTROL MODE : REMOTE/LOCAL | [37 empty] | 1 | 1 | 0 | YES | ControlMod
B1.3 | Y | TUN | TVS | AHU | RUN STATUS | STATUS | RUN | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | STOPPED | RUNNING |  |  | STOPPED | 0: None, 1: None | RUN STATUS : STOPPED/RUNNING | [37 empty] | 1 | 1 | 1 | YES | RunStat
B0.9 | Y | + |  |  | PRESSURIZATION FAN
B1.3 | Y | TUN | TVS | PFA | CONTROL MODE | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | REMOTE | LOCAL |  |  | REMOTE | 0: None, 1: Crit | CONTROL MODE : REMOTE/LOCAL | [37 empty] | 1 | 1 | 0 | YES | ControlMod
B1.3 | Y | TUN | TVS | PFA | OPERATING MODE | OPERATING MODE | OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP) | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | AUTO SCADA | MANUAL SCADA |  |  | AUTO SCADA | 0: None, 1: Maj | OPERATING MODE : AUTO SCADA/MANUAL SCADA | [37 empty] | 1 | 1 | 2 | YES | OpMode
B1.3 | Y | TUN | TVS | PFA | RUN STATUS | STATUS | RUN | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | STOPPED | RUNNING |  |  | STOPPED | 0: None, 1: None | RUN STATUS : STOPPED/RUNNING | [37 empty] | 1 | 1 | 4 | YES | RunStat
B1.1 | Y | TUN | TVS | PFA | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | Command |  | DO | SIL0 | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE AUTO MODE |  |  |  | 10 | OPERATING MODE = MANUAL SCADA |  | OPERATING MODE = AUTO SCADA | [28 empty] | 1 | 1 |  | NO | CmdAuto
B1.1 | Y | TUN | TVS | PFA | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 2 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 2 |  | NO | CmdSelMan
B1.1 | Y | TUN | TVS | PFA | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 6 | NO | AckSelMan
B1.1 | Y | TUN | TVS | PFA | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 10 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE EXECUTE ACK = ACKNOWLEDGE and OPERATING MODE = MANUAL SCADA | [28 empty] | 1 | 3 |  | NO | CmdExeMan
B1.1 | Y | TUN | TVS | PFA | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 8 | NO | AckExeMan
B1.1 | Y | TUN | TVS | PFA | RUN ORDER SELECT | RUN ORDER SELECT | RUN ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | RUN SELECTION |  |  |  | 2 | RUN STATUS = STOPPED |  | RUN ORDER SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 4 |  | NO | CmdSelRun
B1.1 | Y | TUN | TVS | PFA | RUN ORDER SELECT ACK | RUN ORDER SELECT ACK | RUN ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | RUN ORDER SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 10 | NO | AckSelRun
B1.1 | Y | TUN | TVS | PFA | RUN ORDER EXECUTE | RUN ORDER EXECUTE | RUN ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | RUN CONFIRMATION |  |  |  | 40 | RUN STATUS = STOPPED |  | RUN ORDER EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = RUNNING | [28 empty] | 1 | 5 |  | NO | CmdExeRun
B1.1 | Y | TUN | TVS | PFA | RUN ORDER EXECUTE ACK | RUN ORDER EXECUTE ACK | RUN ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | RUN ORDER EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 12 | NO | AckExeRun
B1.1 | Y | TUN | TVS | PFA | STOP ORDER SELECT | STOP ORDER SELECT | STOP ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | STOP SELECTION |  |  |  | 2 | RUN STATUS = RUNNING |  | STOP ORDER SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 6 |  | NO | CmdSelStop
B1.1 | Y | TUN | TVS | PFA | STOP ORDER SELECT ACK | STOP ORDER SELECT ACK | STOP ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | STOP ORDER SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 14 | NO | AckSelStop
B1.1 | Y | TUN | TVS | PFA | STOP ORDER EXECUTE | STOP ORDER EXECUTE | STOP ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | STOP CONFIRMATION |  |  |  | 40 | RUN STATUS = RUNNING |  | STOP ORDER EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = STOPPED | [28 empty] | 1 | 7 |  | NO | CmdExeStop
B1.1 | Y | TUN | TVS | PFA | STOP ORDER EXECUTE ACK | STOP ORDER EXECUTE ACK | STOP ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | STOP ORDER EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 2 | 0 | NO | AckExeStop
B1.2 | Y | TUN | TVS | PFA | START MISMATCH STATUS | START MISMATCH | START MISMATCH | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | START MISMATCH STATUS : NORMAL/FAULTY | [37 empty] | 1 | 2 | 2 | NO | StartMis
B1.2 | Y | TUN | TVS | PFA | STOP MISMATCH STATUS | STOP MISMATCH | STOP MISMATCH | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | STOP MISMATCH STATUS : NORMAL/FAULTY | [37 empty] | 1 | 2 | 4 | NO | StopMis
B1.3 | Y | + |  |  | EXTRACT FAN (for Pearl and fox Hill station)
B1.3 | Y | TUN | TVS | EXF | CONTROL MODE | ELECTRICAL PANEL SELECTOR SWITCH STATUS | ELECTRICAL PANEL SELECTOR SWITCH STATUS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | REMOTE | LOCAL |  |  | REMOTE | 0: None, 1: Crit | CONTROL MODE : REMOTE/LOCAL | [37 empty] | 1 | 1 | 0 | YES | ControlMod
B1.3 | Y | TUN | TVS | EXF | OPERATING MODE | OPERATING MODE | OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP) | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | AUTO SCADA | MANUAL SCADA |  |  | AUTO SCADA | 0: None, 1: Maj | OPERATING MODE : AUTO SCADA/MANUAL SCADA | [37 empty] | 1 | 1 | 2 | YES | OpMode
B1.3 | Y | TUN | TVS | EXF | RUN STATUS | STATUS | RUN | Operational Event |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | STOPPED | RUNNING |  |  | STOPPED | 0: None, 1: None | RUN STATUS : STOPPED/RUNNING | [37 empty] | 1 | 1 | 4 | YES | AutoCom
B1.3 | Y | TUN | TVS | EXF | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | SCADA AUTO MODE COMMAND | Command |  | DO | SIL0 | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE AUTO MODE |  |  |  | 10 | OPERATING MODE = MANUAL SCADA |  | OPERATING MODE = AUTO SCADA | [28 empty] | 1 | 1 |  | NO | CmdMan
B1.3 | Y | TUN | TVS | EXF | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | SCADA MANUAL MODE SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 2 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 2 |  | NO | CmdSelMan
B1.3 | Y | TUN | TVS | EXF | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | SCADA MANUAL MODE SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 6 | NO | AckSelMan
B1.3 | Y | TUN | TVS | EXF | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | SCADA MANUAL MODE EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | ACTIVATE MANUAL MODE |  |  |  | 10 | OPERATING MODE = AUTO SCADA |  | SCADA MANUAL MODE EXECUTE ACK = ACKNOWLEDGE and OPERATING MODE = MANUAL SCADA | [28 empty] | 1 | 3 |  | NO | CmdExeMan
B1.3 | Y | TUN | TVS | EXF | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | SCADA MANUAL MODE EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | SCADA MANUAL MODE EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 8 | NO | AckExeMan
B1.3 | Y | TUN | TVS | EXF | RUN ORDER SELECT | RUN ORDER SELECT | RUN ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | RUN SELECTION |  |  |  | 2 | RUN STATUS = STOPPED |  | RUN ORDER SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 4 |  | NO | CmdSelRun
B1.3 | Y | TUN | TVS | EXF | RUN ORDER SELECT ACK | RUN ORDER SELECT ACK | RUN ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | RUN ORDER SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 10 | NO | AckSelRun
B1.3 | Y | TUN | TVS | EXF | RUN ORDER EXECUTE | RUN ORDER EXECUTE | RUN ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | RUN CONFIRMATION |  |  |  | 40 | RUN STATUS = STOPPED |  | RUN ORDER EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = RUNNING | [28 empty] | 1 | 5 |  | NO | CmdExeRun
B1.3 | Y | TUN | TVS | EXF | RUN ORDER EXECUTE ACK | RUN ORDER EXECUTE ACK | RUN ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | RUN ORDER EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 12 | NO | AckExeRun
B1.3 | Y | TUN | TVS | EXF | STOP ORDER SELECT | STOP ORDER SELECT | STOP ORDER SELECT | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | STOP SELECTION |  |  |  | 2 | RUN STATUS = RUNNING |  | STOP ORDER SELECT ACK = ACKNOWLEDGE | [28 empty] | 1 | 6 |  | NO | CmdSelStop
B1.3 | Y | TUN | TVS | EXF | STOP ORDER SELECT ACK | STOP ORDER SELECT ACK | STOP ORDER SELECT ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | STOP ORDER SELECT ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 1 | 14 | NO | AckSelStop
B1.3 | Y | TUN | TVS | EXF | STOP ORDER EXECUTE | STOP ORDER EXECUTE | STOP ORDER EXECUTE | Command |  | DO | SIL2_Control | MODBUS-TCP | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [7 empty] | NONE | STOP CONFIRMATION |  |  |  | 40 | RUN STATUS = RUNNING |  | STOP ORDER EXECUTE ACK = ACKNOWLEDGE and RUN STATUS = STOPPED | [28 empty] | 1 | 7 |  | NO | CmdExeStop
B1.3 | Y | TUN | TVS | EXF | STOP ORDER EXECUTE ACK | STOP ORDER EXECUTE ACK | STOP ORDER EXECUTE ACK | Operational Alarm |  | DI2 | SIL2_Control | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INITIAL STATE | ACKNOWLEDGE | ERROR | TIMEOUT | INITIAL STATE | 0: None, 1: None, 2: Crit, 3: Crit | STOP ORDER EXECUTE ACK : INITIAL STATE/ACKNOWLEDGE/ERROR/TIMEOUT | [37 empty] | 2 | 2 | 0 | NO | AckExeStop
B1.3 | Y | TUN | TVS | EXF | START MISMATCH STATUS | START MISMATCH | START MISMATCH | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | START MISMATCH STATUS : NORMAL/FAULTY | [37 empty] | 1 | 2 | 2 | NO | StartMis
B1.3 | Y | TUN | TVS | EXF | STOP MISMATCH STATUS | STOP MISMATCH | STOP MISMATCH | Operational Alarm |  | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | STOP MISMATCH STATUS : NORMAL/FAULTY | [37 empty] | 1 | 2 | 4 | NO | StopMis
B0.9 | Y | + |  |  | SMOKE CURTAINS
B1.3 | Y | TUN | TVS | SMC | STATE | STATE | STATE | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | RAISED | DOWN |  |  | RAISED | 0: None, 1: Crit | STATE : RAISED/DOWN | [37 empty] | 1 | 1 | 0 | YES | State
B0.9 | Y | + |  |  | STATION ENTRANCE DOOR
B1.7 | Y | TUN | TVS | SED | STATE | STATE | STATE | Operational Event |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSED | OPEN |  |  | CLOSED | 0: None, 1: None | STATE : CLOSED/OPEN | [37 empty] | 1 | 1 | 0 | YES | State
B1.7 | Y | TUN | TVS | SED | OPEN ORDER SENT BY TVS | OPEN ORDER SENT BY TVS | OPEN ORDER SENT BY TVS | Operational Alarm |  | DI | SIL2_Monitoring | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | INACTIVE | ACTIVE |  |  | INACTIVE | 0: None, 1: Crit | OPEN ORDER SENT BY TVS : INACTIVE/ACTIVE | [37 empty] | 1 | 1 | 1 | NO | Open
B1.5 | Y | + |  |  | STATION PLC CONTROL BAY
B1.5 | N | TUN | TVS | SPLCMMS | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN : NORMAL/FAULTY | [37 empty] | 1 | 1 | 0 | NO | Vac240SwOp
B1.5 | N | TUN | TVS | SPLCMMS | 240VAC SUPPLY VOLTAGE PRESENCE | 240VAC SUPPLY VOLTAGE PRESENCE | 240VAC SUPPLY VOLTAGE PRESENCE | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | 240VAC SUPPLY VOLTAGE PRESENCE : NORMAL/FAULTY | [37 empty] | 1 | 1 | 1 | NO | Vac240Volt
B1.5 | N | TUN | TVS | SPLCMMS | VOLTAGE RELAY CIRCUIT BREAKER OPEN | VOLTAGE RELAY CIRCUIT BREAKER OPEN | VOLTAGE RELAY CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VOLTAGE RELAY CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 1 | 2 | NO | VolOpen
B1.5 | N | TUN | TVS | SPLCMMS | VOLTAGE RELAY CIRCUIT BREAKER FAULT | VOLTAGE RELAY CIRCUIT BREAKER FAULT | VOLTAGE RELAY CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VOLTAGE RELAY CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 1 | 3 | NO | VolFault
B1.5 | N | TUN | TVS | SPLCMMS | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 1 | 4 | NO | VolSupOpen
B1.5 | N | TUN | TVS | SPLCMMS | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 1 | 5 | NO | VolSupFault
B1.5 | N | TUN | TVS | SPLCMMS | CABINET SOCKETS CIRCUIT BREAKERS OPEN | CABINET SOCKETS CIRCUIT BREAKERS OPEN | CABINET SOCKETS CIRCUIT BREAKERS OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | CABINET SOCKETS CIRCUIT BREAKERS OPEN : NORMAL/FAULTY | [37 empty] | 1 | 1 | 6 | NO | CabOpen
B1.5 | N | TUN | TVS | SPLCMMS | CABINET SOCKETS CIRCUIT BREAKERS FAULT | CABINET SOCKETS CIRCUIT BREAKERS FAULT | CABINET SOCKETS CIRCUIT BREAKERS FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | CABINET SOCKETS CIRCUIT BREAKERS FAULT : NORMAL/FAULTY | [37 empty] | 1 | 1 | 7 | NO | CabFault
B1.5 | N | TUN | TVS | SPLCMMS | SERVICES CIRCUIT BREAKER OPEN | SERVICES CIRCUIT BREAKER OPEN | SERVICES CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | SERVICES CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 1 | 8 | NO | SerOpen
B1.5 | N | TUN | TVS | SPLCMMS | SERVICES CIRCUIT BREAKER FAULT | SERVICES CIRCUIT BREAKER FAULT | SERVICES CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | SERVICES CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 1 | 9 | NO | SerFault
B1.5 | N | TUN | TVS | SPLCMMS | UPS CIRCUIT BREAKER OPEN | UPS CIRCUIT BREAKER OPEN | UPS CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | UPS CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 1 | 10 | NO | UpsBreOpen
B1.5 | N | TUN | TVS | SPLCMMS | UPS CIRCUIT BREAKER FAULT | UPS CIRCUIT BREAKER FAULT | UPS CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | UPS CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 1 | 11 | NO | UpsBreFault
B1.5 | N | TUN | TVS | SPLCMMS | UPS DISCONNECTING SWITCH OPEN | UPS DISCONNECTING SWITCH OPEN | UPS DISCONNECTING SWITCH OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | UPS DISCONNECTING SWITCH OPEN : NORMAL/FAULTY | [37 empty] | 1 | 1 | 12 | NO | UpsSwOpen
B1.5 | N | TUN | TVS | SPLCMMS | UPS FAULT | UPS FAULT | UPS FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | UPS FAULT : NORMAL/FAULTY | [37 empty] | 1 | 1 | 13 | NO | UpsFault
B1.5 | N | TUN | TVS | SPLCMMS | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 1 | 14 | NO | Sup24Vdc1Open
B1.5 | N | TUN | TVS | SPLCMMS | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 1 | 15 | NO | Sup24Vdc1Fault
B1.5 | N | TUN | TVS | SPLCMMS | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE : NORMAL/FAULTY | [37 empty] | 1 | 2 | 0 | NO | Sup24Vdc1Volt
B1.5 | N | TUN | TVS | SPLCMMS | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 2 | 1 | NO | Sup24Vdc2Open
B1.5 | N | TUN | TVS | SPLCMMS | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 2 | 2 | NO | Sup24Vdc2Fault
B1.5 | N | TUN | TVS | SPLCMMS | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE : NORMAL/FAULTY | [37 empty] | 1 | 2 | 3 | NO | Sup24Vdc2Volt
B1.5 | N | TUN | TVS | SPLCMMS | SWITCH CIRCUIT BREAKER OPEN | SWITCH CIRCUIT BREAKER OPEN | SWITCH CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SWITCH CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 2 | 4 | NO | SwOpen
B1.5 | N | TUN | TVS | SPLCMMS | SWITCH CIRCUIT BREAKER FAULT | SWITCH CIRCUIT BREAKER FAULT | SWITCH CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SWITCH CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 2 | 5 | NO | SwFault
B1.5 | N | TUN | TVS | SPLCMMS | LCP CIRCUIT BREAKER OPEN | LCP CIRCUIT BREAKER OPEN | LCP CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | LCP CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 2 | 6 | NO | LcpOpen
B1.5 | N | TUN | TVS | SPLCMMS | LCP CIRCUIT BREAKER FAULT | LCP CIRCUIT BREAKER FAULT | LCP CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | LCP CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 2 | 7 | NO | LcpFault
B1.5 | N | TUN | TVS | SPLCMMS | PLC SUPPLY 1 CIRCUIT BREAKER OPEN | PLC SUPPLY 1 CIRCUIT BREAKER OPEN | PLC SUPPLY 1 CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | PLC SUPPLY 1 CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 2 | 8 | NO | Plc1Open
B1.5 | N | TUN | TVS | SPLCMMS | PLC SUPPLY 1 CIRCUIT BREAKER FAULT | PLC SUPPLY 1 CIRCUIT BREAKER FAULT | PLC SUPPLY 1 CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | PLC SUPPLY 1 CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 2 | 9 | NO | Plc1Fault
B1.5 | N | TUN | TVS | SPLCMMS | PLC SUPPLY 2 CIRCUIT BREAKER OPEN | PLC SUPPLY 2 CIRCUIT BREAKER OPEN | PLC SUPPLY 2 CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | PLC SUPPLY 2 CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 2 | 10 | NO | Plc2Open
B1.5 | N | TUN | TVS | SPLCMMS | PLC SUPPLY 2 CIRCUIT BREAKER FAULT | PLC SUPPLY 2 CIRCUIT BREAKER FAULT | PLC SUPPLY 2 CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | PLC SUPPLY 2 CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 2 | 11 | NO | Plc2Fault
B1.5 | N | TUN | TVS | SPLCMMS | SURGE ARRESTER TRIGGERED | SURGE ARRESTER TRIGGERED | SURGE ARRESTER TRIGGERED | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SURGE ARRESTER TRIGGERED : NORMAL/FAULTY | [37 empty] | 1 | 2 | 12 | NO | SuArTrig
B1.6 | Y | + |  |  | MASTER PLC CONTROL BAY
B1.6 | N | TUN | TVS | MPLCMMS | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN : NORMAL/FAULTY | [37 empty] | 1 | 1 | 0 | NO | Vac240SwOp
B1.6 | N | TUN | TVS | MPLCMMS | 240VAC SUPPLY VOLTAGE PRESENCE | 240VAC SUPPLY VOLTAGE PRESENCE | 240VAC SUPPLY VOLTAGE PRESENCE | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Crit | 240VAC SUPPLY VOLTAGE PRESENCE : NORMAL/FAULTY | [37 empty] | 1 | 1 | 1 | NO | Vac240Volt
B1.6 | N | TUN | TVS | MPLCMMS | VOLTAGE RELAY CIRCUIT BREAKER OPEN | VOLTAGE RELAY CIRCUIT BREAKER OPEN | VOLTAGE RELAY CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VOLTAGE RELAY CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 1 | 2 | NO | VolOpen
B1.6 | N | TUN | TVS | MPLCMMS | VOLTAGE RELAY CIRCUIT BREAKER FAULT | VOLTAGE RELAY CIRCUIT BREAKER FAULT | VOLTAGE RELAY CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VOLTAGE RELAY CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 1 | 3 | NO | VolFault
B1.6 | N | TUN | TVS | MPLCMMS | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 1 | 4 | NO | VolSupOpen
B1.6 | N | TUN | TVS | MPLCMMS | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 1 | 5 | NO | VolSupFault
B1.6 | N | TUN | TVS | MPLCMMS | CABINET SOCKETS CIRCUIT BREAKER OPEN | CABINET SOCKETS CIRCUIT BREAKER OPEN | CABINET SOCKETS CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | CABINET SOCKETS CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 1 | 6 | NO | CabOpen
B1.6 | N | TUN | TVS | MPLCMMS | CABINET SOCKETS CIRCUIT BREAKER FAULT | CABINET SOCKETS CIRCUIT BREAKER FAULT | CABINET SOCKETS CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | CABINET SOCKETS CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 1 | 7 | NO | CabFault
B1.6 | N | TUN | TVS | MPLCMMS | SERVICES CIRCUIT BREAKER OPEN | SERVICES CIRCUIT BREAKER OPEN | SERVICES CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | SERVICES CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 1 | 8 | NO | SerOpen
B1.6 | N | TUN | TVS | MPLCMMS | SERVICES CIRCUIT BREAKER FAULT | SERVICES CIRCUIT BREAKER FAULT | SERVICES CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Min | SERVICES CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 1 | 9 | NO | SerFault
B1.6 | N | TUN | TVS | MPLCMMS | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 1 | 10 | NO | Sup24Vdc1Open
B1.6 | N | TUN | TVS | MPLCMMS | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 1 | 11 | NO | Sup24Vdc1Fault
B1.6 | N | TUN | TVS | MPLCMMS | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE : NORMAL/FAULTY | [37 empty] | 1 | 1 | 12 | NO | Sup24Vdc1Volt
B1.6 | N | TUN | TVS | MPLCMMS | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 1 | 13 | NO | Sup24Vdc2Open
B1.6 | N | TUN | TVS | MPLCMMS | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 1 | 14 | NO | Sup24Vdc2Fault
B1.6 | N | TUN | TVS | MPLCMMS | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE : NORMAL/FAULTY | [37 empty] | 1 | 1 | 15 | NO | Sup24Vdc2Volt
B1.6 | N | TUN | TVS | MPLCMMS | SWITCH 1 CIRCUIT BREAKER OPEN | SWITCH 1 CIRCUIT BREAKER OPEN | SWITCH 1 CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SWITCH 1 CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 2 | 0 | NO | Sw1Open
B1.6 | N | TUN | TVS | MPLCMMS | SWITCH 1 CIRCUIT BREAKER FAULT | SWITCH 1 CIRCUIT BREAKER FAULT | SWITCH 1 CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SWITCH 1 CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 2 | 1 | NO | Sw1Fault
B1.6 | N | TUN | TVS | MPLCMMS | SWITCH 2 CIRCUIT BREAKER OPEN | SWITCH 2 CIRCUIT BREAKER OPEN | SWITCH 2 CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SWITCH 2 CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 2 | 2 | NO | Sw2Open
B1.6 | N | TUN | TVS | MPLCMMS | SWITCH 2 CIRCUIT BREAKER FAULT | SWITCH 2 CIRCUIT BREAKER FAULT | SWITCH 2 CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SWITCH 2 CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 2 | 3 | NO | Sw2Fault
B1.6 | N | TUN | TVS | MPLCMMS | PLC A CIRCUIT BREAKER OPEN | PLC A CIRCUIT BREAKER OPEN | PLC A CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | PLC A CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 2 | 4 | NO | PlcAOpen
B1.6 | N | TUN | TVS | MPLCMMS | PLC A CIRCUIT BREAKER FAULT | PLC A CIRCUIT BREAKER FAULT | PLC A CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | PLC A CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 2 | 5 | NO | PlcAFault
B1.6 | N | TUN | TVS | MPLCMMS | PLC B CIRCUIT BREAKER OPEN | PLC B CIRCUIT BREAKER OPEN | PLC B CIRCUIT BREAKER OPEN | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | PLC B CIRCUIT BREAKER OPEN : NORMAL/FAULTY | [37 empty] | 1 | 2 | 6 | NO | PlcBOpen
B1.6 | N | TUN | TVS | MPLCMMS | PLC B CIRCUIT BREAKER FAULT | PLC B CIRCUIT BREAKER FAULT | PLC B CIRCUIT BREAKER FAULT | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | PLC B CIRCUIT BREAKER FAULT : NORMAL/FAULTY | [37 empty] | 1 | 2 | 7 | NO | PlcBFault
B1.6 | N | TUN | TVS | MPLCMMS | SURGE ARRESTER TRIGGERED | SURGE ARRESTER TRIGGERED | SURGE ARRESTER TRIGGERED | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | SURGE ARRESTER TRIGGERED : NORMAL/FAULTY | [37 empty] | 1 | 2 | 8 | NO | SuArTrig
B1.6 | Y | + |  |  | Auxiliary MCB (MCB)
B1.6 | N | TUN | TVS | MCB | Auxiliary MCB trip status | Auxiliary MCB trip status | Auxiliary MCB trip status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Crit | Auxiliary MCB trip status : NORMAL/TRIPPED | [37 empty] | 1 | 1 | 0 | NO | McbTrip
B1.6 | N | TUN | TVS | MCB | Auxiliary MCB closed status | Auxiliary MCB closed status | Auxiliary MCB closed status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Auxiliary MCB closed status : CLOSE/OPEN | [37 empty] | 1 | 1 | 1 | NO | McbClose
B1.6 | Y | + |  |  | Auxiliary Switch Isolator (ADS)
B1.6 | N | TUN | TVS | ADS | Load breaker switched closed | Load breaker switched closed | Load breaker switched closed | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Load breaker switched closed : CLOSE/OPEN | [37 empty] | 1 | 1 | 0 | NO | LoadClose
B1.6 | N | TUN | TVS | ADS | LBS Auxiliary Switch racked position | LBS Auxiliary Switch racked position | LBS Auxiliary Switch racked position | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | IN | OUT |  |  | IN | 0: None, 1: Maj | LBS Auxiliary Switch racked position : IN/OUT | [37 empty] | 1 | 1 | 1 | NO | LbsPos
B1.6 | Y | + |  |  | TRANSFORMER (TRF)
B1.6 | N | TUN | TVS | TRF | Emergency power off | Emergency power off | Emergency power off | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Emergency power off : NORMAL/FAULTY | [37 empty] | 1 | 1 | 0 | NO | EmOff
B1.6 | N | TUN | TVS | TRF | Transformer fault | Transformer fault | Transformer fault | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Transformer fault : NORMAL/FAULTY | [37 empty] | 1 | 1 | 1 | NO | TranFault
B1.6 | N | TUN | TVS | TRF | Emergency power cut | Emergency power cut | Emergency power cut | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Emergency power cut : NORMAL/FAULTY | [37 empty] | 1 | 1 | 2 | NO | EmCut
B1.6 | N | TUN | TVS | TRF | Transformer high Temperature pre alarm | Transformer high Temperature pre alarm | Transformer high Temperature pre alarm | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Transformer high Temperature pre alarm : NORMAL/FAULTY | [37 empty] | 1 | 1 | 3 | NO | PreAlarm
B1.6 | N | TUN | TVS | TRF | Transformer high Temperature Alarm | Transformer high Temperature Alarm | Transformer high Temperature Alarm | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Transformer high Temperature Alarm : NORMAL/FAULTY | [37 empty] | 1 | 1 | 4 | NO | Alarm
B1.6 | Y | + |  |  | Auxiliary Circuit Breaker (ACB)
B1.6 | N | TUN | TVS | ACB | Main circuit breaker fault | Main circuit breaker fault | Main circuit breaker fault | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Main circuit breaker fault : NORMAL/FAULTY | [37 empty] | 1 | 1 | 0 | NO | Fault
B1.6 | N | TUN | TVS | ACB | Main circuit breaker open/closed status | Main circuit breaker open/closed status | Main circuit breaker open/closed status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Main circuit breaker open/closed status : CLOSE/OPEN | [37 empty] | 1 | 1 | 1 | NO | Status
B1.6 | N | TUN | TVS | ACB | Main CBC ACB racked position | Main CBC ACB racked position | Main CBC ACB racked position | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | IN | OUT |  |  | IN | 0: None, 1: Maj | Main CBC ACB racked position : IN/OUT | [37 empty] | 1 | 1 | 2 | NO | Position
B1.6 | Y | + |  |  | Main distribution board cabinet (MDB)
B1.6 | N | TUN | TVS | MDB | Power normal MCSD 1 status | Power normal MCSD 1 status | Power normal MCSD 1 status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Power normal MCSD 1 status : CLOSE/OPEN | [37 empty] | 1 | 1 | 0 | NO | Mcsd1Stat
B1.6 | N | TUN | TVS | MDB | Power replacement MCSD 2 status | Power replacement MCSD 2 status | Power replacement MCSD 2 status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Power replacement MCSD 2 status : CLOSE/OPEN | [37 empty] | 1 | 1 | 1 | NO | Mcsd2Stat
B1.6 | N | TUN | TVS | MDB | MDB-01 MCSD 1 racked position | MDB-01 MCSD 1 racked position | MDB-01 MCSD 1 racked position | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | IN | OUT |  |  | IN | 0: None, 1: Maj | MDB-01 MCSD 1 racked position : IN/OUT | [37 empty] | 1 | 1 | 2 | NO | Mcsd1pos
B1.6 | N | TUN | TVS | MDB | MDB-01 MCSD 2 racked position | MDB-01 MCSD 2 racked position | MDB-01 MCSD 2 racked position | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | IN | OUT |  |  | IN | 0: None, 1: Maj | MDB-01 MCSD 2 racked position : IN/OUT | [37 empty] | 1 | 1 | 3 | NO | Mcsd2pos
B1.6 | N | TUN | TVS | MDB | Change over | Change over | Change over | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Change over : NORMAL/FAULTY | [37 empty] | 1 | 1 | 4 | NO | Change
B1.6 | N | TUN | TVS | MDB | Phase failure relay 1 | Phase failure relay 1 | Phase failure relay 1 | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Phase failure relay 1 : NORMAL/FAULTY | [37 empty] | 1 | 1 | 5 | NO | relay1
B1.6 | N | TUN | TVS | MDB | Phase failure relay 2 | Phase failure relay 2 | Phase failure relay 2 | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Phase failure relay 2 : NORMAL/FAULTY | [37 empty] | 1 | 1 | 6 | NO | relay2
B1.6 | N | TUN | TVS | MDB | MCB closed status | MCB closed status | MCB closed status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | MCB closed status : CLOSE/OPEN | [37 empty] | 1 | 1 | 7 | NO | Closed
B1.6 | N | TUN | TVS | MDB | MCB tripped status | MCB tripped status | MCB tripped status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | MCB tripped status : NORMAL/TRIPPED | [37 empty] | 1 | 1 | 8 | NO | Trip
B1.6 | N | TUN | TVS | MDB | Emergency power cut (push button) | Emergency power cut (push button) | Emergency power cut (push button) | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Emergency power cut (push button) : NORMAL/FAULTY | [37 empty] | 1 | 1 | 9 | NO | PowerCut
B1.6 | N | TUN | TVS | MDB | MCCB 1 Incomer EL2 status | MCCB 1 Incomer EL2 status | MCCB 1 Incomer EL2 status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | MCCB 1 Incomer EL2 status : CLOSE/OPEN | [37 empty] | 1 | 1 | 10 | NO | Mccb1Stat
B1.6 | N | TUN | TVS | MDB | MCCB 1 Incomer EL2 trip | MCCB 1 Incomer EL2 trip | MCCB 1 Incomer EL2 trip | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | MCCB 1 Incomer EL2 trip : NORMAL/TRIPPED | [37 empty] | 1 | 1 | 11 | NO | Mccb1Trip
B1.6 | N | TUN | TVS | MDB | MCCB 2 Incomer EL2 status | MCCB 2 Incomer EL2 status | MCCB 2 Incomer EL2 status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | MCCB 2 Incomer EL2 status : CLOSE/OPEN | [37 empty] | 1 | 1 | 12 | NO | Mccb2Stat
B1.6 | N | TUN | TVS | MDB | MCCB 2 Incomer EL2 trip | MCCB 2 Incomer EL2 trip | MCCB 2 Incomer EL2 trip | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | MCCB 2 Incomer EL2 trip : NORMAL/TRIPPED | [37 empty] | 1 | 1 | 13 | NO | Mccb2Trip
B1.6 | N | TUN | TVS | MDB | MCCB 3 Incomer EL2 status | MCCB 3 Incomer EL2 status | MCCB 3 Incomer EL2 status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | MCCB 3 Incomer EL2 status : CLOSE/OPEN | [37 empty] | 1 | 1 | 14 | NO | Mccb3Stat
B1.6 | N | TUN | TVS | MDB | MCCB 3 Incomer EL2 trip | MCCB 3 Incomer EL2 trip | MCCB 3 Incomer EL2 trip | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | MCCB 3 Incomer EL2 trip : NORMAL/TRIPPED | [37 empty] | 1 | 1 | 15 | NO | Mccb3Trip
B1.6 | Y | + |  |  | Electrical Control Panel (EL)
B1.6 | N | TUN | TVS | EL | Phase failure relay | Phase failure relay | Phase failure relay | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Phase failure relay : NORMAL/FAULTY | [37 empty] | 1 | 1 | 0 | NO | Relay
B1.6 | N | TUN | TVS | EL | LBS Main incomer isolator status | LBS Main incomer isolator status | LBS Main incomer isolator status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | LBS Main incomer isolator status : CLOSE/OPEN | [37 empty] | 1 | 1 | 1 | NO | Isolator
B1.6 | N | TUN | TVS | EL | UPS supply status | UPS supply status | UPS supply status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | UPS supply status : NORMAL/FAULTY | [37 empty] | 1 | 1 | 2 | NO | Supply
B1.6 | N | TUN | TVS | EL | UPS faulty | UPS faulty | UPS faulty | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | UPS faulty : NORMAL/FAULTY | [37 empty] | 1 | 1 | 3 | NO | Faulty
B1.6 | N | TUN | TVS | EL | 24VDC UPS power status | 24VDC UPS power status | 24VDC UPS power status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | 24VDC UPS power status : NORMAL/FAULTY | [37 empty] | 1 | 1 | 4 | NO | Power
B1.6 | Y | + |  |  | MCCB
B1.6 | N | TUN | TVS | MCCB | MCCB trip status | MCCB trip status | MCCB trip status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Crit | MCCB trip status : NORMAL/TRIPPED | [37 empty] | 1 | 1 | 0 | NO | Trip
B1.6 | N | TUN | TVS | MCCB | MCCB closed status | MCCB closed status | MCCB closed status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | MCCB closed status : CLOSE/OPEN | [37 empty] | 1 | 1 | 1 | NO | Closed
B1.6 | Y | + |  |  | LBS
B1.6 | N | TUN | TVS | LBS | LBS closed status | LBS closed status | LBS closed status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | LBS closed status : CLOSE/OPEN | [37 empty] | 1 | 1 | 0 | NO | Closed
B1.6 | Y | + |  |  | Shaft Main distribution board cabinet (SMDB)
B1.6 | N | TUN | TVS | SMDB | Power normal ACB 1 closed | Power normal ACB 1 closed | Power normal ACB 1 closed | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Power normal ACB 1 closed : CLOSE/OPEN | [37 empty] | 1 | 1 | 0 | NO | Acb1Closed
B1.6 | N | TUN | TVS | SMDB | Power normal ACB 1 tripped | Power normal ACB 1 tripped | Power normal ACB 1 tripped | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | Power normal ACB 1 tripped : NORMAL/TRIPPED | [37 empty] | 1 | 1 | 1 | NO | Acb1Trip
B1.6 | N | TUN | TVS | SMDB | Power replacement ACB 2 closed status | Power replacement ACB 2 closed status | Power replacement ACB 2 closed status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Power replacement ACB 2 closed status : CLOSE/OPEN | [37 empty] | 1 | 1 | 2 | NO | Acb2Closed
B1.6 | N | TUN | TVS | SMDB | Power replacement ACB 2 Triped status | Power replacement ACB 2 Triped status | Power replacement ACB 2 Triped status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | Power replacement ACB 2 Triped status : NORMAL/TRIPPED | [37 empty] | 1 | 1 | 3 | NO | Acb2Trip
B1.6 | N | TUN | TVS | SMDB | MDB-01 ACB 1 racked position | MDB-01 ACB 1 racked position | MDB-01 ACB 1 racked position | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | IN | OUT |  |  | IN | 0: None, 1: Maj | MDB-01 ACB 1 racked position : IN/OUT | [37 empty] | 1 | 1 | 4 | NO | Acb1Pos
B1.6 | N | TUN | TVS | SMDB | MDB-01 ACB 2 racked position | MDB-01 ACB 2 racked position | MDB-01 ACB 2 racked position | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | IN | OUT |  |  | IN | 0: None, 1: Maj | MDB-01 ACB 2 racked position : IN/OUT | [37 empty] | 1 | 1 | 5 | NO | Acb2Pos
B1.6 | N | TUN | TVS | SMDB | Change over | Change over | Change over | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Change over : NORMAL/FAULTY | [37 empty] | 1 | 1 | 6 | NO | Change
B1.6 | N | TUN | TVS | SMDB | Phase failure relay 1 | Phase failure relay 1 | Phase failure relay 1 | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Phase failure relay 1 : NORMAL/FAULTY | [37 empty] | 1 | 1 | 7 | NO | Relay1
B1.6 | N | TUN | TVS | SMDB | Phase failure relay 2 | Phase failure relay 2 | Phase failure relay 2 | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Phase failure relay 2 : NORMAL/FAULTY | [37 empty] | 1 | 1 | 8 | NO | Relay2
B1.6 | N | TUN | TVS | SMDB | MCB closed status | MCB closed status | MCB closed status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | MCB closed status : CLOSE/OPEN | [37 empty] | 1 | 1 | 9 | NO | McbClose
B1.6 | N | TUN | TVS | SMDB | MCB tripped status | MCB tripped status | MCB tripped status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | MCB tripped status : NORMAL/TRIPPED | [37 empty] | 1 | 1 | 10 | NO | McbTrip
B1.6 | N | TUN | TVS | SMDB | Emergency power cut (push button) | Emergency power cut (push button) | Emergency power cut (push button) | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | FAULTY |  |  | NORMAL | 0: None, 1: Maj | Emergency power cut (push button) : NORMAL/FAULTY | [37 empty] | 1 | 1 | 11 | NO | PowerCut
B1.6 | N | TUN | TVS | SMDB | Control cabinet MCCB PLC01 closed status | Control cabinet MCCB PLC01 closed status | Control cabinet MCCB PLC01 closed status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Control cabinet MCCB PLC01 closed status : CLOSE/OPEN | [37 empty] | 1 | 1 | 12 | NO | Plc01Close
B1.6 | N | TUN | TVS | SMDB | Control cabinet MCCB PLC01 on tripped status | Control cabinet MCCB PLC01 on tripped status | Control cabinet MCCB PLC01 on tripped status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | Control cabinet MCCB PLC01 on tripped status : NORMAL/TRIPPED | [37 empty] | 1 | 1 | 13 | NO | Plc01Trip
B1.6 | N | TUN | TVS | SMDB | Control cabinet MCCB VSD1 closed status | Control cabinet MCCB VSD1 closed status | Control cabinet MCCB VSD1 closed status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Control cabinet MCCB VSD1 closed status : CLOSE/OPEN | [37 empty] | 1 | 1 | 14 | NO | Vsd1Close
B1.6 | N | TUN | TVS | SMDB | Control cabinet MCCB VSD1 on tripped status | Control cabinet MCCB VSD1 on tripped status | Control cabinet MCCB VSD1 on tripped status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | Control cabinet MCCB VSD1 on tripped status : NORMAL/TRIPPED | [37 empty] | 1 | 1 | 15 | NO | Vsd1Trip
B1.6 | N | TUN | TVS | SMDB | Control cabinet MCCB VSD2 closed status | Control cabinet MCCB VSD2 closed status | Control cabinet MCCB VSD2 closed status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Control cabinet MCCB VSD2 closed status : CLOSE/OPEN | [37 empty] | 1 | 2 | 0 | NO | Vsd2Close
B1.6 | N | TUN | TVS | SMDB | Control cabinet MCCB VSD2 on tripped status | Control cabinet MCCB VSD2 on tripped status | Control cabinet MCCB VSD2 on tripped status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | Control cabinet MCCB VSD2 on tripped status : NORMAL/TRIPPED | [37 empty] | 1 | 2 | 1 | NO | Vsd2Trip
B1.6 | N | TUN | TVS | SMDB | Spare E1 cabinet closed status | Spare E1 cabinet closed status | Spare E1 cabinet closed status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Spare E1 cabinet closed status : CLOSE/OPEN | [37 empty] | 1 | 2 | 2 | NO | E1Close
B1.6 | N | TUN | TVS | SMDB | Spare E1 tripped status | Spare E1 tripped status | Spare E1 tripped status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | Spare E1 tripped status : NORMAL/TRIPPED | [37 empty] | 1 | 2 | 3 | NO | E1Trip
B1.6 | N | TUN | TVS | SMDB | Spare E2 cabinet closed status | Spare E2 cabinet closed status | Spare E2 cabinet closed status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | CLOSE | OPEN |  |  | CLOSE | 0: None, 1: Maj | Spare E2 cabinet closed status : CLOSE/OPEN | [37 empty] | 1 | 2 | 4 | NO | E2Close
B1.6 | N | TUN | TVS | SMDB | Spare E2 tripped status | Spare E2 tripped status | Spare E2 tripped status | Technical Alarm | Weekly | DI | SIL0 | MODBUS-TCP | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | NORMAL | TRIPPED |  |  | NORMAL | 0: None, 1: Maj | Spare E2 tripped status : NORMAL/TRIPPED | [37 empty] | 1 | 2 | 5 | NO | E2Trip
Note on F284: TENA ANIES Miguel: All these classes are for MMS purposes, no need to present them on SCADA HMI, just in SCADA Historian

## 2-Instance List
|  | LRT/QRC DESIGNATION |  |  |  | EQUIPMENT INSTANCES | [8 empty] | PRTU Configuration
Revision | isAComment | [Lusail] GBS Code | [Lusail] LBS Code LRT Designation Code | [Lusail] LBS Code QRC Designation Code | Description | Location | Sublocation | Class name | Equipment name | RTU Name | PLC Name | InvalidVar1 | InvalidVar2 | InvalidVar3 | Instance Id | External System Name | Device Unit Id | FEP Name | FEP instance Id | Short name | Unique ID code | SCADA Transfert function (Internal THALES) | Address | Description (Native language) | ToBeInstantiated
B0.9 | Y |  |  |  |  | BOCC
B0.9 | Y |  |  |  |  | MASTER PLCs (MPLC)
B2.1 | Y |  |  |  | Master PLC at BOCC | TUN:BOCC | MPLC | MPLC | MPLC01 | BOCC_RTU |  |  |  |  | 1 |  |  |  |  | &MPLC01 | TUN_BOCC_MPLC_MPLC01 |  |  |  | YES | TUNBOCCMPLCMPLC01 | 17
B1.6 | Y |  |  |  |  | MMS Equipment
B2.1 | N |  |  |  | Master PLC at BOCC (MMS) | TUN:BOCC | MMS | MPLCMMS | MPLC01 | BOCC_RTU |  |  |  |  | 2 |  |  |  |  | &MPLC01 | TUN_BOCC_MMS_MPLC01 |  |  |  | YES | TUNBOCCMMSMPLC01 | 16
B0.9 | Y |  |  |  |  | Watchdog (WTGD)
B2.1 | Y |  |  |  | Watchdog TVS Master PLC BOCC | TUN:BOCC | WTDG | WTDG | WTDG01 | BOCC_RTU |  |  |  |  | 3 |  |  |  |  | &WTDG01 | TUN_BOCC_WTDG_WTDG01 |  |  |  | YES | TUNBOCCWTDGWTDG01 | 17
B0.9 | Y |  |  |  |  | Switch
B2.1 | Y |  |  |  | Switch 1 | TUN:BOCC | SWI | SWI | SWI01 | BOCC_RTU |  |  |  |  | 4 |  |  |  |  | &SWI01 | TUN_BOCC_SWI_SWI01 |  |  |  | YES | TUNBOCCSWISWI01 | 15
B2.1 | Y |  |  |  | Switch 2 | TUN:BOCC | SWI | SWI | SWI02 | BOCC_RTU |  |  |  |  | 5 |  |  |  |  | &SWI02 | TUN_BOCC_SWI_SWI02 |  |  |  | YES | TUNBOCCSWISWI02 | 15
B0.9 | Y |  |  |  |  | OCC
B0.9 | Y |  |  |  |  | MASTER PLCs (MPLC)
B2.1 | Y |  |  |  | Master PLC at OCC | TUN:OCC | MPLC | MPLC | MPLC01 | OCC_RTU |  |  |  |  | 1 |  |  |  |  | &MPLC01 | TUN_OCC_MPLC_MPLC01 |  |  |  | YES | TUNOCCMPLCMPLC01 | 16
B1.6 | Y |  |  |  |  | MMS Equipment
B2.1 | N |  |  |  | Master PLC at OCC (MMS) | TUN:OCC | MMS | MPLCMMS | MPLC01 | OCC_RTU |  |  |  |  | 2 |  |  |  |  | &MPLC01 | TUN_OCC_MMS_MPLC01 |  |  |  | YES | TUNOCCMMSMPLC01 | 15
B0.9 | Y |  |  |  |  | Watchdog (WTGD)
B2.1 | Y |  |  |  | Watchdog TVS Master PLC OCC | TUN:OCC | WTDG | WTDG | WTDG01 | OCC_RTU |  |  |  |  | 3 |  |  |  |  | &WTDG01 | TUN_OCC_WTDG_WTDG01 |  |  |  | YES | TUNOCCWTDGWTDG01 | 16
B0.9 | Y |  |  |  |  | Switch
B2.1 | Y |  |  |  | Switch 1 | TUN:OCC | SWI | SWI | SWI01 | OCC_RTU |  |  |  |  | 4 |  |  |  |  | &SWI01 | TUN_OCC_SWI_SWI01 |  |  |  | YES | TUNOCCSWISWI01 | 14
B2.1 | Y |  |  |  | Switch 2 | TUN:OCC | SWI | SWI | SWI02 | OCC_RTU |  |  |  |  | 5 |  |  |  |  | &SWI02 | TUN_OCC_SWI_SWI02 |  |  |  | YES | TUNOCCSWISWI02 | 14
B1.5 | Y |  |  |  |  | MAIN UNDERGROUND LINE AVERAGE TEMPERATURE
B2.1 | Y |  |  |  | MAIN UNDERGROUND AVERAGE TEMPERATURE | TUN:OCC | TEMP | MUL | MUL01 | OCC_RTU |  |  |  |  | 6 |  |  |  |  | &MUL01 | TUN_OCC_TEMP_MUL01 |  |  |  | YES | TUNMULTEMPMUL01 | 15
B1.5 | Y |  |  |  |  | FOXHILL LINE AVERAGE TEMPERATURE
B2.1 | Y |  |  |  | FOXHILL LINE AVERAGE TEMPERATURE | TUN:OCC | TEMP | FXL | FXL01 | OCC_RTU |  |  |  |  | 7 |  |  |  |  | &FXL01 | TUN_OCC_TEMP_FXL01 |  |  |  | YES | TUNFXLTEMPFXL01 | 15
B1.5 | Y |  |  |  |  | TUNNEL NORMAL & CONGESTED VENTILATION MODES
B2.1 | N |  |  |  | TUNNEL NORMAL & CONGESTED VENTILATION MODES | TUN:OCC | MODES | VENTILATION | VENTILATION | OCC_RTU |  |  |  |  | 8 |  |  |  |  | &VENTILATION | TUN_OCC_MODES_VENTILATION |  |  |  | YES | TUNMODESVENTILATION | 19
B1.5 | Y |  |  |  |  | EMERGENCY SCENARIOS
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1011 - Push-pull direction TO PEA-01 - Tunnel fire between PEA-0A and PEA-01 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1011 | OCC_RTU |  |  |  |  | 9 |  |  |  |  | &SCENARIO1011 | TUN_OCC_EMERGENCY_SCENARIO1011 |  |  |  | YES | TUNEMERGENCYSCENARIO1011 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1012 - Push-pull direction TO PEA-0A - Tunnel fire between PEA-0A and PEA-01 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1012 | OCC_RTU |  |  |  |  | 10 |  |  |  |  | &SCENARIO1012 | TUN_OCC_EMERGENCY_SCENARIO1012 |  |  |  | YES | TUNEMERGENCYSCENARIO1012 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1021 - Push-pull direction TO PEA-1B - Tunnel fire between PEA-01 and PEA-1B | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1021 | OCC_RTU |  |  |  |  | 11 |  |  |  |  | &SCENARIO1021 | TUN_OCC_EMERGENCY_SCENARIO1021 |  |  |  | YES | TUNEMERGENCYSCENARIO1021 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1022 - Push-pull direction TO PEA-01 - Tunnel fire between PEA-01 and PEA-1B | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1022 | OCC_RTU |  |  |  |  | 12 |  |  |  |  | &SCENARIO1022 | TUN_OCC_EMERGENCY_SCENARIO1022 |  |  |  | YES | TUNEMERGENCYSCENARIO1022 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1031 - Push-pull direction TO MAR-0A - Tunnel fire between PEA-1B and MAR-0A | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1031 | OCC_RTU |  |  |  |  | 13 |  |  |  |  | &SCENARIO1031 | TUN_OCC_EMERGENCY_SCENARIO1031 |  |  |  | YES | TUNEMERGENCYSCENARIO1031 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1032 - Push-pull direction TO PEA-1B - Tunnel fire between PEA-1B and MAR-0A | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1032 | OCC_RTU |  |  |  |  | 14 |  |  |  |  | &SCENARIO1032 | TUN_OCC_EMERGENCY_SCENARIO1032 |  |  |  | YES | TUNEMERGENCYSCENARIO1032 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1041 - Push-pull direction TO MAR-01 - Tunnel fire between MAR-0A and MAR-01 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1041 | OCC_RTU |  |  |  |  | 15 |  |  |  |  | &SCENARIO1041 | TUN_OCC_EMERGENCY_SCENARIO1041 |  |  |  | YES | TUNEMERGENCYSCENARIO1041 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1042 - Push-pull direction TO MAR-0A - Tunnel fire between MAR-0A and MAR-01 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1042 | OCC_RTU |  |  |  |  | 16 |  |  |  |  | &SCENARIO1042 | TUN_OCC_EMERGENCY_SCENARIO1042 |  |  |  | YES | TUNEMERGENCYSCENARIO1042 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1051 - Push-pull direction TO MAR-02 - Tunnel fire between MAR-01 and MAR-02 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1051 | OCC_RTU |  |  |  |  | 17 |  |  |  |  | &SCENARIO1051 | TUN_OCC_EMERGENCY_SCENARIO1051 |  |  |  | YES | TUNEMERGENCYSCENARIO1051 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1052 - Push-pull direction TO MAR-01 - Tunnel fire between MAR-01 and MAR-02 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1052 | OCC_RTU |  |  |  |  | 18 |  |  |  |  | &SCENARIO1052 | TUN_OCC_EMERGENCY_SCENARIO1052 |  |  |  | YES | TUNEMERGENCYSCENARIO1052 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1061 - Push-pull direction TO MAR-03 - Tunnel fire between MAR-02 and MAR-03 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1061 | OCC_RTU |  |  |  |  | 19 |  |  |  |  | &SCENARIO1061 | TUN_OCC_EMERGENCY_SCENARIO1061 |  |  |  | YES | TUNEMERGENCYSCENARIO1061 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1062 - Push-pull direction TO MAR-02 - Tunnel fire between MAR-02 and MAR-03 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1062 | OCC_RTU |  |  |  |  | 20 |  |  |  |  | &SCENARIO1062 | TUN_OCC_EMERGENCY_SCENARIO1062 |  |  |  | YES | TUNEMERGENCYSCENARIO1062 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1071 - Push-pull direction TO MAR-04 - Tunnel fire between MAR-03 and MAR-04 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1071 | OCC_RTU |  |  |  |  | 21 |  |  |  |  | &SCENARIO1071 | TUN_OCC_EMERGENCY_SCENARIO1071 |  |  |  | YES | TUNEMERGENCYSCENARIO1071 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1072 - Push-pull direction TO MAR-03 - Tunnel fire between MAR-03 and MAR-04 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1072 | OCC_RTU |  |  |  |  | 22 |  |  |  |  | &SCENARIO1072 | TUN_OCC_EMERGENCY_SCENARIO1072 |  |  |  | YES | TUNEMERGENCYSCENARIO1072 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1081 - Push-pull direction TO QEC-01 - Tunnel fire between MAR-04 and QEC-01 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1081 | OCC_RTU |  |  |  |  | 23 |  |  |  |  | &SCENARIO1081 | TUN_OCC_EMERGENCY_SCENARIO1081 |  |  |  | YES | TUNEMERGENCYSCENARIO1081 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1082 - Push-pull direction TO MAR-04 - Tunnel fire between MAR-04 and QEC-01 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1082 | OCC_RTU |  |  |  |  | 24 |  |  |  |  | &SCENARIO1082 | TUN_OCC_EMERGENCY_SCENARIO1082 |  |  |  | YES | TUNEMERGENCYSCENARIO1082 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1091 - Push-pull direction TO QEC portal - Tunnel fire between QEC-01 and QEC portal | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1091 | OCC_RTU |  |  |  |  | 25 |  |  |  |  | &SCENARIO1091 | TUN_OCC_EMERGENCY_SCENARIO1091 |  |  |  | YES | TUNEMERGENCYSCENARIO1091 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1092 - Push-pull direction TO QEC-01 - Tunnel fire between QEC-01 and QEC portal | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1092 | OCC_RTU |  |  |  |  | 26 |  |  |  |  | &SCENARIO1092 | TUN_OCC_EMERGENCY_SCENARIO1092 |  |  |  | YES | TUNEMERGENCYSCENARIO1092 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1101 - Push-pull direction TO EC1-0A - Tunnel fire between QEC-01 (YLB) and EC1-0A | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1101 | OCC_RTU |  |  |  |  | 27 |  |  |  |  | &SCENARIO1101 | TUN_OCC_EMERGENCY_SCENARIO1101 |  |  |  | YES | TUNEMERGENCYSCENARIO1101 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1102 - Push-pull direction TO QEC-01 - Tunnel fire between QEC-01 (YLB) and EC1-0A | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1102 | OCC_RTU |  |  |  |  | 28 |  |  |  |  | &SCENARIO1102 | TUN_OCC_EMERGENCY_SCENARIO1102 |  |  |  | YES | TUNEMERGENCYSCENARIO1102 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1111 - Push-pull direction TO EC1-01 - Tunnel fire between EC1-0A and EC1-01 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1111 | OCC_RTU |  |  |  |  | 29 |  |  |  |  | &SCENARIO1111 | TUN_OCC_EMERGENCY_SCENARIO1111 |  |  |  | YES | TUNEMERGENCYSCENARIO1111 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1112 - Push-pull direction TO EC1-0A - Tunnel fire between EC1-0A and EC1-01 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1112 | OCC_RTU |  |  |  |  | 30 |  |  |  |  | &SCENARIO1112 | TUN_OCC_EMERGENCY_SCENARIO1112 |  |  |  | YES | TUNEMERGENCYSCENARIO1112 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1121 - Push-pull direction TO QAP-01 - Tunnel fire between EC1-01 and QAP-01 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1121 | OCC_RTU |  |  |  |  | 31 |  |  |  |  | &SCENARIO1121 | TUN_OCC_EMERGENCY_SCENARIO1121 |  |  |  | YES | TUNEMERGENCYSCENARIO1121 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1122 - Push-pull direction TO EC1-01 - Tunnel fire between EC1-01 and QAP-01 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1122 | OCC_RTU |  |  |  |  | 32 |  |  |  |  | &SCENARIO1122 | TUN_OCC_EMERGENCY_SCENARIO1122 |  |  |  | YES | TUNEMERGENCYSCENARIO1122 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1131 - Push-pull direction TO QAP-1B - Tunnel fire between QAP-01 and QAP-1B | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1131 | OCC_RTU |  |  |  |  | 33 |  |  |  |  | &SCENARIO1131 | TUN_OCC_EMERGENCY_SCENARIO1131 |  |  |  | YES | TUNEMERGENCYSCENARIO1131 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1132 - Push-pull direction TO QAP-01 - Tunnel fire between QAP-01 and QAP-1B | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1132 | OCC_RTU |  |  |  |  | 34 |  |  |  |  | &SCENARIO1132 | TUN_OCC_EMERGENCY_SCENARIO1132 |  |  |  | YES | TUNEMERGENCYSCENARIO1132 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1141 - Push-pull direction TO EC2-1A portal - Tunnel fire between QAP-1B and EC2-1A portal | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1141 | OCC_RTU |  |  |  |  | 35 |  |  |  |  | &SCENARIO1141 | TUN_OCC_EMERGENCY_SCENARIO1141 |  |  |  | YES | TUNEMERGENCYSCENARIO1141 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1142 - Push-pull direction TO QAP-1B - Tunnel fire between QAP-1B and EC2-1A portal | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1142 | OCC_RTU |  |  |  |  | 36 |  |  |  |  | &SCENARIO1142 | TUN_OCC_EMERGENCY_SCENARIO1142 |  |  |  | YES | TUNEMERGENCYSCENARIO1142 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1151 - Push-pull direction TO FXH-0A portal - Tunnel fire between QAP-1B and FXH-0A portal | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1151 | OCC_RTU |  |  |  |  | 37 |  |  |  |  | &SCENARIO1151 | TUN_OCC_EMERGENCY_SCENARIO1151 |  |  |  | YES | TUNEMERGENCYSCENARIO1151 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1152 - Push-pull direction TO QAP-1B - Tunnel fire between QAP-1B and FXH-0A portal | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1152 | OCC_RTU |  |  |  |  | 38 |  |  |  |  | &SCENARIO1152 | TUN_OCC_EMERGENCY_SCENARIO1152 |  |  |  | YES | TUNEMERGENCYSCENARIO1152 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1161 - Push-pull direction TO FXH-1A portal - Tunnel fire between FXH-02 and FXH-1A portal | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1161 | OCC_RTU |  |  |  |  | 39 |  |  |  |  | &SCENARIO1161 | TUN_OCC_EMERGENCY_SCENARIO1161 |  |  |  | YES | TUNEMERGENCYSCENARIO1161 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1162 - Push-pull direction TO FXH-02 - Tunnel fire between FXH-02 and FXH-1A portal | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1162 | OCC_RTU |  |  |  |  | 40 |  |  |  |  | &SCENARIO1162 | TUN_OCC_EMERGENCY_SCENARIO1162 |  |  |  | YES | TUNEMERGENCYSCENARIO1162 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1171 - Push-pull direction TO FXH-02 - Tunnel fire between FXH-2A portal and FXH-02 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1171 | OCC_RTU |  |  |  |  | 41 |  |  |  |  | &SCENARIO1171 | TUN_OCC_EMERGENCY_SCENARIO1171 |  |  |  | YES | TUNEMERGENCYSCENARIO1171 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 1172 - Push-pull direction TO FXH-2A portal - Tunnel fire between FXH-2A portal and FXH-02 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO1172 | OCC_RTU |  |  |  |  | 42 |  |  |  |  | &SCENARIO1172 | TUN_OCC_EMERGENCY_SCENARIO1172 |  |  |  | YES | TUNEMERGENCYSCENARIO1172 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 2510 - Push-pull direction NOT APPLICABLE - Station fire - PEA-01 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2510 | OCC_RTU |  |  |  |  | 43 |  |  |  |  | &SCENARIO2510 | TUN_OCC_EMERGENCY_SCENARIO2510 |  |  |  | YES | TUNEMERGENCYSCENARIO2510 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 2520 - Push-pull direction NOT APPLICABLE - Station fire - MAR-01 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2520 | OCC_RTU |  |  |  |  | 44 |  |  |  |  | &SCENARIO2520 | TUN_OCC_EMERGENCY_SCENARIO2520 |  |  |  | YES | TUNEMERGENCYSCENARIO2520 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 2530 - Push-pull direction NOT APPLICABLE - Station fire - MAR-02 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2530 | OCC_RTU |  |  |  |  | 45 |  |  |  |  | &SCENARIO2530 | TUN_OCC_EMERGENCY_SCENARIO2530 |  |  |  | YES | TUNEMERGENCYSCENARIO2530 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 2540 - Push-pull direction NOT APPLICABLE - Station fire - MAR-03 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2540 | OCC_RTU |  |  |  |  | 46 |  |  |  |  | &SCENARIO2540 | TUN_OCC_EMERGENCY_SCENARIO2540 |  |  |  | YES | TUNEMERGENCYSCENARIO2540 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 2550 - Push-pull direction NOT APPLICABLE - Station fire - MAR-04 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2550 | OCC_RTU |  |  |  |  | 47 |  |  |  |  | &SCENARIO2550 | TUN_OCC_EMERGENCY_SCENARIO2550 |  |  |  | YES | TUNEMERGENCYSCENARIO2550 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 2560 - Push-pull direction NOT APPLICABLE - Station fire - QEC-01 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2560 | OCC_RTU |  |  |  |  | 48 |  |  |  |  | &SCENARIO2560 | TUN_OCC_EMERGENCY_SCENARIO2560 |  |  |  | YES | TUNEMERGENCYSCENARIO2560 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 2570 - Push-pull direction NOT APPLICABLE - Station fire - EC1-01 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2570 | OCC_RTU |  |  |  |  | 49 |  |  |  |  | &SCENARIO2570 | TUN_OCC_EMERGENCY_SCENARIO2570 |  |  |  | YES | TUNEMERGENCYSCENARIO2570 | 24
B2.1 | Y |  |  |  | EMERGENCY SCENARIO 2580 - Push-pull direction NOT APPLICABLE - Station fire - QAP-01 | TUN:OCC | EMERGENCY | EMERGENCY | SCENARIO2580 | OCC_RTU |  |  |  |  | 50 |  |  |  |  | &SCENARIO2580 | TUN_OCC_EMERGENCY_SCENARIO2580 |  |  |  | YES | TUNEMERGENCYSCENARIO2580 | 24
B0.9 | Y |  |  |  |  | MAR-01
B0.9 | Y |  |  |  |  | LOCAL CONTROL PANEL (LCP) [STATION HMI]
B2.1 | Y |  |  |  | Local control panel | TUN:MAR01 | SCR | LCP | LCP01 | MAR01_RTU |  |  |  |  | 1 |  |  |  |  | &LCP01 | TUN_MAR01_SCR_LCP01 |  |  |  | YES | TUNMAR01SCRLCP01 | 16
B1.5 | Y |  |  |  |  | FIRE MANUAL OVERRIDE PANEL (FMOP)
B2.1 | Y |  |  |  | Fire control panel | TUN:MAR01 | SCR | FMOP | FMOP01 | MAR01_RTU |  |  |  |  | 2 |  |  |  |  | &FMOP01 | TUN_MAR01_SCR_FMOP01 |  |  |  | YES | TUNMAR01SCRFMOP01 | 17
B0.9 | Y |  |  |  |  | Station PLC (SPLC)
B2.1 | Y |  |  |  | Station PLC | TUN:MAR01 | TEL | SPLC | PLC01 | MAR01_RTU |  |  |  |  | 3 |  |  |  |  | &PLC01 | TUN_MAR01_TEL_PLC01 |  |  |  | YES | TUNMAR01TELPLC01 | 16
B0.9 | Y |  |  |  |  | Switch (SWI)
B2.1 | Y |  |  |  | Switch | TUN:MAR01 | TEL | SWI | SWI01 | MAR01_RTU |  |  |  |  | 4 |  |  |  |  | &SWI01 | TUN_MAR01_TEL_SWI01 |  |  |  | YES | TUNMAR01TELSWI01 | 16
B0.9 | Y |  |  |  |  | PRESSURIZATION FAN (PFA)
B2.1 | Y |  |  |  | Pressurization fan Lobby | TUN:MAR01 | NS01:PFA | PFA | CON-04 | MAR01_RTU |  |  |  |  | 5 |  |  |  |  | &CON-04 | TUN_MAR01_NS01_PFA_CON-04 |  |  |  | YES | TUNMAR01NS01PFACON-04 | 21
B2.1 | Y |  |  |  | Pressurization fan Staircase | TUN:MAR01 | NS01:PFA | PFA | GRD-01 | MAR01_RTU |  |  |  |  | 6 |  |  |  |  | &GRD-01 | TUN_MAR01_NS01_PFA_GRD-01 |  |  |  | YES | TUNMAR01NS01PFAGRD-01 | 21
B2.1 | Y |  |  |  | Pressurization fan Lobby | TUN:MAR01 | SS01:PFA | PFA | CON-03 | MAR01_RTU |  |  |  |  | 7 |  |  |  |  | &CON-03 | TUN_MAR01_SS01_PFA_CON-03 |  |  |  | YES | TUNMAR01SS01PFACON-03 | 21
B2.1 | Y |  |  |  | Pressurization fan Staircase | TUN:MAR01 | SS01:PFA | PFA | GRD-03 | MAR01_RTU |  |  |  |  | 8 |  |  |  |  | &GRD-03 | TUN_MAR01_SS01_PFA_GRD-03 |  |  |  | YES | TUNMAR01SS01PFAGRD-03 | 21
B0.9 | Y |  |  |  |  | SMOKE CURTAINS (SMC)
B2.1 | Y |  |  |  | Smoke Curtains 1 | TUN:MAR01 | SMC | SMC | SMC01 | MAR01_RTU |  |  |  |  | 9 |  |  |  |  | &SMC01 | TUN_MAR01_SMC_SMC01 |  |  |  | YES | TUNMAR01SMCSMC01 | 16
B2.1 | Y |  |  |  | Smoke Curtains 2 | TUN:MAR01 | SMC | SMC | SMC02 | MAR01_RTU |  |  |  |  | 10 |  |  |  |  | &SMC02 | TUN_MAR01_SMC_SMC02 |  |  |  | YES | TUNMAR01SMCSMC02 | 16
B2.1 | Y |  |  |  | Smoke Curtains 3 | TUN:MAR01 | SMC | SMC | SMC03 | MAR01_RTU |  |  |  |  | 11 |  |  |  |  | &SMC03 | TUN_MAR01_SMC_SMC03 |  |  |  | YES | TUNMAR01SMCSMC03 | 16
B2.1 | Y |  |  |  | Smoke Curtains 4 | TUN:MAR01 | SMC | SMC | SMC04 | MAR01_RTU |  |  |  |  | 12 |  |  |  |  | &SMC04 | TUN_MAR01_SMC_SMC04 |  |  |  | YES | TUNMAR01SMCSMC04 | 16
B2.1 | Y |  |  |  | Smoke Curtains 5 | TUN:MAR01 | SMC | SMC | SMC05 | MAR01_RTU |  |  |  |  | 13 |  |  |  |  | &SMC05 | TUN_MAR01_SMC_SMC05 |  |  |  | YES | TUNMAR01SMCSMC05 | 16
B2.1 | Y |  |  |  | Smoke Curtains 6 | TUN:MAR01 | SMC | SMC | SMC06 | MAR01_RTU |  |  |  |  | 14 |  |  |  |  | &SMC06 | TUN_MAR01_SMC_SMC06 |  |  |  | YES | TUNMAR01SMCSMC06 | 16
B2.1 | Y |  |  |  | Smoke Curtains 7 | TUN:MAR01 | SMC | SMC | SMC07 | MAR01_RTU |  |  |  |  | 15 |  |  |  |  | &SMC07 | TUN_MAR01_SMC_SMC07 |  |  |  | YES | TUNMAR01SMCSMC07 | 16
B2.1 | Y |  |  |  | Smoke Curtains 8 | TUN:MAR01 | SMC | SMC | SMC08 | MAR01_RTU |  |  |  |  | 16 |  |  |  |  | &SMC08 | TUN_MAR01_SMC_SMC08 |  |  |  | YES | TUNMAR01SMCSMC08 | 16
B0.9 | Y |  |  |  |  | STATION ENTRANCE DOOR (SED)
B2.1 | Y |  |  |  | Station entrance door 1 | TUN:MAR01 | SED | SED | SED01 | MAR01_RTU |  |  |  |  | 17 |  |  |  |  | &SED01 | TUN_MAR01_SED_SED01 |  |  |  | YES | TUNMAR01SEDSED01 | 16
B2.1 | Y |  |  |  | Station entrance door 2 | TUN:MAR01 | SED | SED | SED02 | MAR01_RTU |  |  |  |  | 18 |  |  |  |  | &SED02 | TUN_MAR01_SED_SED02 |  |  |  | YES | TUNMAR01SEDSED02 | 16
B2.1 | Y |  |  |  | Station entrance door 3 | TUN:MAR01 | SED | SED | SED03 | MAR01_RTU |  |  |  |  | 19 |  |  |  |  | &SED03 | TUN_MAR01_SED_SED03 |  |  |  | YES | TUNMAR01SEDSED03 | 16
B2.1 | Y |  |  |  | Station entrance door 4 | TUN:MAR01 | SED | SED | SED04 | MAR01_RTU |  |  |  |  | 20 |  |  |  |  | &SED04 | TUN_MAR01_SED_SED04 |  |  |  | YES | TUNMAR01SEDSED04 | 16
B0.9 | Y |  |  |  |  | Outdoor temperature sensor (OTS)
B2.1 | Y |  |  |  | Outdoor temperature sensor 1 | TUN:MAR01 | OTS | OTS | OTS001 | MAR01_RTU |  |  |  |  | 21 |  |  |  |  | &OTS001 | TUN_MAR01_OTS_OTS001 |  |  |  | YES | TUNMAR01OTSOTS001 | 17
B2.1 | Y |  |  |  | Outdoor temperature sensor 2 | TUN:MAR01 | OTS | OTS | OTS002 | MAR01_RTU |  |  |  |  | 22 |  |  |  |  | &OTS002 | TUN_MAR01_OTS_OTS002 |  |  |  | YES | TUNMAR01OTSOTS002 | 17
B0.9 | Y |  |  |  |  | Tunnel ventilation fan (TVF)
B2.1 | Y |  |  |  | North ShaftTunnel ventilation fan 1 | TUN:MAR01 | NS01:TVF | TVF | VT1-TVF01 | MAR01_RTU |  |  |  |  | 23 |  |  |  |  | &VT1-TVF01 | TUN_MAR01_NS01_TVF_VT1-TVF01 |  |  |  | YES | TUNMAR01NS01TVFVT1-TVF01 | 24
B2.1 | Y |  |  |  | North ShaftTunnel ventilation fan 2 | TUN:MAR01 | NS01:TVF | TVF | VT2-TVF01 | MAR01_RTU |  |  |  |  | 24 |  |  |  |  | &VT2-TVF01 | TUN_MAR01_NS01_TVF_VT2-TVF01 |  |  |  | YES | TUNMAR01NS01TVFVT2-TVF01 | 24
B2.1 | Y |  |  |  | South ShaftTunnel ventilation fan 3 | TUN:MAR01 | SS01:TVF | TVF | VT3-TVF01 | MAR01_RTU |  |  |  |  | 25 |  |  |  |  | &VT3-TVF01 | TUN_MAR01_SS01_TVF_VT3-TVF01 |  |  |  | YES | TUNMAR01SS01TVFVT3-TVF01 | 24
B2.1 | Y |  |  |  | SouthShaftTunnel ventilation fan 4 | TUN:MAR01 | SS01:TVF | TVF | VT4-TVF01 | MAR01_RTU |  |  |  |  | 26 |  |  |  |  | &VT4-TVF01 | TUN_MAR01_SS01_TVF_VT4-TVF01 |  |  |  | YES | TUNMAR01SS01TVFVT4-TVF01 | 24
B0.9 | Y |  |  |  |  | Tunnel temperature & humidity sensor (TTS)
B2.1 | Y |  |  |  | North Tunnel temperature sensor 1 | TUN:MAR01 | NS01:SENSOR | TTS | TS100269 | MAR01_RTU |  |  |  |  | 27 |  |  |  |  | &TS100269 | TUN_MAR01_NS01_SENSOR_TS100269 |  |  |  | YES | TUNMAR01NS01SENSORTS100269 | 26
B2.1 | Y |  |  |  | North Tunnel temperature sensor 2 | TUN:MAR01 | NS01:SENSOR | TTS | TS100222 | MAR01_RTU |  |  |  |  | 28 |  |  |  |  | &TS100222 | TUN_MAR01_NS01_SENSOR_TS100222 |  |  |  | YES | TUNMAR01NS01SENSORTS100222 | 26
B2.1 | Y |  |  |  | South Tunnel temperature sensor 1 | TUN:MAR01 | SS01:SENSOR | TTS | TS099914 | MAR01_RTU |  |  |  |  | 29 |  |  |  |  | &TS099914 | TUN_MAR01_SS01_SENSOR_TS099914 |  |  |  | YES | TUNMAR01SS01SENSORTS099914 | 26
B2.1 | Y |  |  |  | South Tunnel temperature sensor 2 | TUN:MAR01 | SS01:SENSOR | TTS | TS099816 | MAR01_RTU |  |  |  |  | 30 |  |  |  |  | &TS099816 | TUN_MAR01_SS01_SENSOR_TS099816 |  |  |  | YES | TUNMAR01SS01SENSORTS099816 | 26
B0.9 | Y |  |  |  |  | Air velocity sensor (VS)
B2.1 | Y |  |  |  | North Air velocity sensor 1 | TUN:MAR01 | NS01:SENSOR | VS | VS100253 | MAR01_RTU |  |  |  |  | 31 |  |  |  |  | &VS100253 | TUN_MAR01_NS01_SENSOR_VS100253 |  |  |  | YES | TUNMAR01NS01SENSORVS100253 | 26
B2.1 | Y |  |  |  | South Air velocity sensor 1 | TUN:MAR01 | SS01:SENSOR | VS | VS099848 | MAR01_RTU |  |  |  |  | 32 |  |  |  |  | &VS099848 | TUN_MAR01_SS01_SENSOR_VS099848 |  |  |  | YES | TUNMAR01SS01SENSORVS099848 | 26
B0.9 | Y |  |  |  |  | TVS Damper : Tunnel damper (TDP)
B2.1 | Y |  |  |  | North Shaft Tunnel damper 1 | TUN:MAR01 | NS01:DAMPER | TVD | VT5-TDP01 | MAR01_RTU |  |  |  |  | 33 |  |  |  |  | &VT5-TDP01 | TUN_MAR01_NS01_DAMPER_VT5-TDP01 |  |  |  | YES | TUNMAR01NS01DAMPERVT5-TDP01 | 27
B2.1 | Y |  |  |  | South Shaft Tunnel damper 2 | TUN:MAR01 | SS01:DAMPER | TVD | VT6-TDP01 | MAR01_RTU |  |  |  |  | 34 |  |  |  |  | &VT6-TDP01 | TUN_MAR01_SS01_DAMPER_VT6-TDP01 |  |  |  | YES | TUNMAR01SS01DAMPERVT6-TDP01 | 27
B0.9 | Y |  |  |  |  | TVS Damper : Isolation damper (IDP)
B2.1 | N |  |  |  | Isolation damper 1 | TUN:MAR01 | NS01:DAMPER | IDP | VT1-IDP01 | MAR01_RTU |  |  |  |  | 35 |  |  |  |  | &VT1-IDP01 | TUN_MAR01_NS01_DAMPER_VT1-IDP01 |  |  |  | YES | TUNMAR01NS01DAMPERVT1-IDP01 | 27
B2.1 | N |  |  |  | Isolation damper 2 | TUN:MAR01 | NS01:DAMPER | IDP | VT2-IDP01 | MAR01_RTU |  |  |  |  | 36 |  |  |  |  | &VT2-IDP01 | TUN_MAR01_NS01_DAMPER_VT2-IDP01 |  |  |  | YES | TUNMAR01NS01DAMPERVT2-IDP01 | 27
B2.1 | N |  |  |  | Isolation damper 3 | TUN:MAR01 | SS01:DAMPER | IDP | VT3-IDP01 | MAR01_RTU |  |  |  |  | 37 |  |  |  |  | &VT3-IDP01 | TUN_MAR01_SS01_DAMPER_VT3-IDP01 |  |  |  | YES | TUNMAR01SS01DAMPERVT3-IDP01 | 27
B2.1 | N |  |  |  | Isolation damper 4 | TUN:MAR01 | SS01:DAMPER | IDP | VT4-IDP01 | MAR01_RTU |  |  |  |  | 38 |  |  |  |  | &VT4-IDP01 | TUN_MAR01_SS01_DAMPER_VT4-IDP01 |  |  |  | YES | TUNMAR01SS01DAMPERVT4-IDP01 | 27
B0.9 | Y |  |  |  |  | TVS Damper : Bypass damper (BDP)
B2.1 | Y |  |  |  | North Shaft Bypass damper 1 | TUN:MAR01 | NS01:DAMPER | TVD | FR1-BDP01 | MAR01_RTU |  |  |  |  | 39 |  |  |  |  | &FR1-BDP01 | TUN_MAR01_NS01_DAMPER_FR1-BDP01 |  |  |  | YES | TUNMAR01NS01DAMPERFR1-BDP01 | 27
B2.1 | Y |  |  |  | South Shaft Bypass damper 2 | TUN:MAR01 | SS01:DAMPER | TVD | FR2-BDP01 | MAR01_RTU |  |  |  |  | 40 |  |  |  |  | &FR2-BDP01 | TUN_MAR01_SS01_DAMPER_FR2-BDP01 |  |  |  | YES | TUNMAR01SS01DAMPERFR2-BDP01 | 27
B0.9 | Y |  |  |  |  | MEP Damper : Tunnel Cooling damper (TCDP)
B2.1 | N |  |  |  | North Shaft Tunnel Cooling damper 1 | TUN:MAR01 | NS01:DAMPER | MSFD | CON-54 | MAR01_RTU |  |  |  |  | 41 |  |  |  |  | &CON-54 | TUN_MAR01_NS01_DAMPER_CON-54 |  |  |  | YES | TUNMAR01NS01DAMPERCON-54 | 24
B2.1 | N |  |  |  | South Shaft Tunnel Cooling damper 2 | TUN:MAR01 | SS01:DAMPER | MSFD | CON-63 | MAR01_RTU |  |  |  |  | 42 |  |  |  |  | &CON-63 | TUN_MAR01_SS01_DAMPER_CON-63 |  |  |  | YES | TUNMAR01SS01DAMPERCON-63 | 24
B0.9 | Y |  |  |  |  | MEP damper : Station to exhaust duct Damper (SEDD)
B2.1 | N |  |  |  | North Shaft Station to exhaust duct damper 1 | TUN:MAR01 | NS01:DAMPER | MSFD | CON-51 | MAR01_RTU |  |  |  |  | 43 |  |  |  |  | &CON-51 | TUN_MAR01_NS01_DAMPER_CON-51 |  |  |  | YES | TUNMAR01NS01DAMPERCON-51 | 24
B2.1 | N |  |  |  | North Shaft Station to exhaust duct damper 2 | TUN:MAR01 | NS01:DAMPER | MSFD | CON-56 | MAR01_RTU |  |  |  |  | 44 |  |  |  |  | &CON-56 | TUN_MAR01_NS01_DAMPER_CON-56 |  |  |  | YES | TUNMAR01NS01DAMPERCON-56 | 24
B2.1 | N |  |  |  | South Shaft Station to exhaust duct damper 3 | TUN:MAR01 | SS01:DAMPER | MSFD | CON-61 | MAR01_RTU |  |  |  |  | 45 |  |  |  |  | &CON-61 | TUN_MAR01_SS01_DAMPER_CON-61 |  |  |  | YES | TUNMAR01SS01DAMPERCON-61 | 24
B2.1 | N |  |  |  | South Shaft Station to exhaust duct damper 4 | TUN:MAR01 | SS01:DAMPER | MSFD | CON-66 | MAR01_RTU |  |  |  |  | 46 |  |  |  |  | &CON-66 | TUN_MAR01_SS01_DAMPER_CON-66 |  |  |  | YES | TUNMAR01SS01DAMPERCON-66 | 24
B0.9 | Y |  |  |  |  | MEP damper : Station Cooling damper (SCD)
B2.1 | N |  |  |  | North Shaft Station Cooling damper 1 | TUN:MAR01 | NS01:DAMPER | MSFD | CON-52 | MAR01_RTU |  |  |  |  | 47 |  |  |  |  | &CON-52 | TUN_MAR01_NS01_DAMPER_CON-52 |  |  |  | YES | TUNMAR01NS01DAMPERCON-52 | 24
B2.1 | N |  |  |  | North Shaft Station Cooling damper 2 | TUN:MAR01 | NS01:DAMPER | MSFD | CON-58 | MAR01_RTU |  |  |  |  | 48 |  |  |  |  | &CON-58 | TUN_MAR01_NS01_DAMPER_CON-58 |  |  |  | YES | TUNMAR01NS01DAMPERCON-58 | 24
B2.1 | N |  |  |  | South Shaft Station Cooling damper 3 | TUN:MAR01 | SS01:DAMPER | MSFD | CON-59 | MAR01_RTU |  |  |  |  | 49 |  |  |  |  | &CON-59 | TUN_MAR01_SS01_DAMPER_CON-59 |  |  |  | YES | TUNMAR01SS01DAMPERCON-59 | 24
B2.1 | N |  |  |  | South Shaft Station Cooling damper 4 | TUN:MAR01 | SS01:DAMPER | MSFD | CON-67 | MAR01_RTU |  |  |  |  | 50 |  |  |  |  | &CON-67 | TUN_MAR01_SS01_DAMPER_CON-67 |  |  |  | YES | TUNMAR01SS01DAMPERCON-67 | 24
B0.9 | Y |  |  |  |  | Tunnel AIR HANDLING UNIT
B2.1 | Y |  |  |  | North ShaftTunnel Air Handling Unit 1 | TUN:MAR01 | NS01:AHU | AHU | CON-05 | MAR01_RTU |  |  |  |  | 51 |  |  |  |  | &CON-05 | TUN_MAR01_NS01_AHU_CON-05 |  |  |  | YES | TUNMAR01NS01AHUCON-05 | 21
B2.1 | Y |  |  |  | North ShaftTunnel Air Handling Unit 2 | TUN:MAR01 | NS01:AHU | AHU | CON-06 | MAR01_RTU |  |  |  |  | 52 |  |  |  |  | &CON-06 | TUN_MAR01_NS01_AHU_CON-06 |  |  |  | YES | TUNMAR01NS01AHUCON-06 | 21
B2.1 | Y |  |  |  | South ShaftTunnel Air Handling Unit 1 | TUN:MAR01 | SS01:AHU | AHU | CON-07 | MAR01_RTU |  |  |  |  | 53 |  |  |  |  | &CON-07 | TUN_MAR01_SS01_AHU_CON-07 |  |  |  | YES | TUNMAR01SS01AHUCON-07 | 21
B2.1 | Y |  |  |  | South ShaftTunnel Air Handling Unit 2 | TUN:MAR01 | SS01:AHU | AHU | CON-08 | MAR01_RTU |  |  |  |  | 54 |  |  |  |  | &CON-08 | TUN_MAR01_SS01_AHU_CON-08 |  |  |  | YES | TUNMAR01SS01AHUCON-08 | 21
B1.6 | Y |  |  |  |  | MMS Equipment
B2.1 | N |  |  |  | Station PLC (MMS) | TUN:MAR01 | MMS | SPLCMMS | SPLC01 | MAR01_RTU |  |  |  |  | 55 |  |  |  |  | &SPLC01 | TUN_MAR01_MMS_SPLC01 |  |  |  | YES | TUNMAR01MMSSPLC01 | 17
B1.6 | Y |  |  |  |  | Electrical Equipment
B2.1 | N |  |  |  | MAR01-EL2-LBS01 | TUN:MAR01 | MMS | ADS | EL2-LBS01 | MAR01_RTU |  |  |  |  | 56 |  |  |  |  | &EL2-LBS01 | TUN_MAR01_MMS_EL2-LBS01 |  |  |  | YES | TUNMAR01MMSEL2-LBS01 | 20
B2.1 | N |  |  |  | MAR01-EL2-LBS02 | TUN:MAR01 | MMS | ADS | EL2-LBS02 | MAR01_RTU |  |  |  |  | 57 |  |  |  |  | &EL2-LBS02 | TUN_MAR01_MMS_EL2-LBS02 |  |  |  | YES | TUNMAR01MMSEL2-LBS02 | 20
B2.1 | N |  |  |  | MAR01-MV-TRF01 | TUN:MAR01 | MMS | TRF | MV-TRF01 | MAR01_RTU |  |  |  |  | 58 |  |  |  |  | &MV-TRF01 | TUN_MAR01_MMS_MV-TRF01 |  |  |  | YES | TUNMAR01MMSMV-TRF01 | 19
B2.1 | N |  |  |  | MAR01-MV-TRF02 | TUN:MAR01 | MMS | TRF | MV-TRF02 | MAR01_RTU |  |  |  |  | 59 |  |  |  |  | &MV-TRF02 | TUN_MAR01_MMS_MV-TRF02 |  |  |  | YES | TUNMAR01MMSMV-TRF02 | 19
B2.1 | N |  |  |  | MAR01-EL2-CBC01 | TUN:MAR01 | MMS | ACB | EL2-CBC01 | MAR01_RTU |  |  |  |  | 60 |  |  |  |  | &EL2-CBC01 | TUN_MAR01_MMS_EL2-CBC01 |  |  |  | YES | TUNMAR01MMSEL2-CBC01 | 20
B2.1 | N |  |  |  | MAR01-EL2-CBC02 | TUN:MAR01 | MMS | ACB | EL2-CBC02 | MAR01_RTU |  |  |  |  | 61 |  |  |  |  | &EL2-CBC02 | TUN_MAR01_MMS_EL2-CBC02 |  |  |  | YES | TUNMAR01MMSEL2-CBC02 | 20
B2.1 | N |  |  |  | MAR01-LPS-MDB01 | TUN:MAR01 | MMS | MDB | LPS-MDB01 | MAR01_RTU |  |  |  |  | 62 |  |  |  |  | &LPS-MDB01 | TUN_MAR01_MMS_LPS-MDB01 |  |  |  | YES | TUNMAR01MMSLPS-MDB01 | 20
B2.1 | N |  |  |  | MAR01-LPS-MDB02 | TUN:MAR01 | MMS | MDB | LPS-MDB02 | MAR01_RTU |  |  |  |  | 63 |  |  |  |  | &LPS-MDB02 | TUN_MAR01_MMS_LPS-MDB02 |  |  |  | YES | TUNMAR01MMSLPS-MDB02 | 20
B1.6 | Y |  |  |  |  | Electrical Panel EL1 I/O 01
B2.1 | N |  |  |  | MAR01-EL1-IO01 | TUN:MAR01 | MMS | EL | EL1-IO01 | MAR01_RTU |  |  |  |  | 64 |  |  |  |  | &EL1-IO01 | TUN_MAR01_MMS_EL1-IO01 |  |  |  | YES | TUNMAR01MMSEL1-IO01 | 19
B2.1 | N |  |  |  | MCCB MAR01-EL1-VSD01/02 | TUN:MAR01 | MMS | MCCB | EL1-VSD0102 | MAR01_RTU |  |  |  |  | 65 |  |  |  |  | &EL1-VSD0102 | TUN_MAR01_MMS_EL1-VSD0102 |  |  |  | YES | TUNMAR01MMSEL1-VSD0102 | 22
B2.1 | N |  |  |  | LBS MAR01-EL1-VSD01/02 | TUN:MAR01 | MMS | LBS | EL1-VSD0102 | MAR01_RTU |  |  |  |  | 66 |  |  |  |  | &EL1-VSD0102 | TUN_MAR01_MMS_EL1-VSD0102 |  |  |  | YES | TUNMAR01MMSEL1-VSD0102 | 22
B2.1 | N |  |  |  | MCB MAR01-EL1-VSD01 | TUN:MAR01 | MMS | MCB | EL1-VSD01 | MAR01_RTU |  |  |  |  | 67 |  |  |  |  | &EL1-VSD01 | TUN_MAR01_MMS_EL1-VSD01 |  |  |  | YES | TUNMAR01MMSEL1-VSD01 | 20
B2.1 | N |  |  |  | MCB MAR01-EL1-VSD02 | TUN:MAR01 | MMS | MCB | EL1-VSD02 | MAR01_RTU |  |  |  |  | 68 |  |  |  |  | &EL1-VSD02 | TUN_MAR01_MMS_EL1-VSD02 |  |  |  | YES | TUNMAR01MMSEL1-VSD02 | 20
B2.1 | N |  |  |  | MCB 3P MAR01-VT3-IDP01 | TUN:MAR01 | MMS | MCB | 3P-VT3-IDP01 | MAR01_RTU |  |  |  |  | 69 |  |  |  |  | &3P-VT3-IDP01 | TUN_MAR01_MMS_3P-VT3-IDP01 |  |  |  | YES | TUNMAR01MMS3P-VT3-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P MAR01-VT3-IDP01 | TUN:MAR01 | MMS | MCB | 2P-VT3-IDP01 | MAR01_RTU |  |  |  |  | 70 |  |  |  |  | &2P-VT3-IDP01 | TUN_MAR01_MMS_2P-VT3-IDP01 |  |  |  | YES | TUNMAR01MMS2P-VT3-IDP01 | 23
B2.1 | N |  |  |  | MCB 3P MAR01-VT4-IDP01 | TUN:MAR01 | MMS | MCB | 3P-VT4-IDP01 | MAR01_RTU |  |  |  |  | 71 |  |  |  |  | &3P-VT4-IDP01 | TUN_MAR01_MMS_3P-VT4-IDP01 |  |  |  | YES | TUNMAR01MMS3P-VT4-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P MAR01-VT4-IDP01 | TUN:MAR01 | MMS | MCB | 2P-VT4-IDP01 | MAR01_RTU |  |  |  |  | 72 |  |  |  |  | &2P-VT4-IDP01 | TUN_MAR01_MMS_2P-VT4-IDP01 |  |  |  | YES | TUNMAR01MMS2P-VT4-IDP01 | 23
B2.1 | N |  |  |  | MCB 3P MAR01-VT6-IDP01-01 | TUN:MAR01 | MMS | MCB | 3P-VT6-IDP01-01 | MAR01_RTU |  |  |  |  | 73 |  |  |  |  | &3P-VT6-IDP01-01 | TUN_MAR01_MMS_3P-VT6-IDP01-01 |  |  |  | YES | TUNMAR01MMS3P-VT6-IDP01-01 | 26
B2.1 | N |  |  |  | MCB 2P MAR01-VT6-IDP01-01 | TUN:MAR01 | MMS | MCB | 2P-VT6-IDP01-01 | MAR01_RTU |  |  |  |  | 74 |  |  |  |  | &2P-VT6-IDP01-01 | TUN_MAR01_MMS_2P-VT6-IDP01-01 |  |  |  | YES | TUNMAR01MMS2P-VT6-IDP01-01 | 26
B2.1 | N |  |  |  | MCB 3P MAR01-VT6-IDP01-02 | TUN:MAR01 | MMS | MCB | 3P-VT6-IDP01-02 | MAR01_RTU |  |  |  |  | 75 |  |  |  |  | &3P-VT6-IDP01-02 | TUN_MAR01_MMS_3P-VT6-IDP01-02 |  |  |  | YES | TUNMAR01MMS3P-VT6-IDP01-02 | 26
B2.1 | N |  |  |  | MCB 2P MAR01-VT6-IDP01-02 | TUN:MAR01 | MMS | MCB | 2P-VT6-IDP01-02 | MAR01_RTU |  |  |  |  | 76 |  |  |  |  | &2P-VT6-IDP01-02 | TUN_MAR01_MMS_2P-VT6-IDP01-02 |  |  |  | YES | TUNMAR01MMS2P-VT6-IDP01-02 | 26
B2.1 | N |  |  |  | MCB 3P MAR01-VT6-IDP01-03 | TUN:MAR01 | MMS | MCB | 3P-VT6-IDP01-03 | MAR01_RTU |  |  |  |  | 77 |  |  |  |  | &3P-VT6-IDP01-03 | TUN_MAR01_MMS_3P-VT6-IDP01-03 |  |  |  | YES | TUNMAR01MMS3P-VT6-IDP01-03 | 26
B2.1 | N |  |  |  | MCB 2P MAR01-VT6-IDP01-03 | TUN:MAR01 | MMS | MCB | 2P-VT6-IDP01-03 | MAR01_RTU |  |  |  |  | 78 |  |  |  |  | &2P-VT6-IDP01-03 | TUN_MAR01_MMS_2P-VT6-IDP01-03 |  |  |  | YES | TUNMAR01MMS2P-VT6-IDP01-03 | 26
B2.1 | N |  |  |  | MCB 3P MAR01-FR2-BDP01-01 | TUN:MAR01 | MMS | MCB | 3P-FR2-BDP01-01 | MAR01_RTU |  |  |  |  | 79 |  |  |  |  | &3P-FR2-BDP01-01 | TUN_MAR01_MMS_3P-FR2-BDP01-01 |  |  |  | YES | TUNMAR01MMS3P-FR2-BDP01-01 | 26
B2.1 | N |  |  |  | MCB 2P MAR01-FR2-BDP01-01 | TUN:MAR01 | MMS | MCB | 2P-FR2-BDP01-01 | MAR01_RTU |  |  |  |  | 80 |  |  |  |  | &2P-FR2-BDP01-01 | TUN_MAR01_MMS_2P-FR2-BDP01-01 |  |  |  | YES | TUNMAR01MMS2P-FR2-BDP01-01 | 26
B2.1 | N |  |  |  | MCB 3P MAR01-FR2-BDP01-02 | TUN:MAR01 | MMS | MCB | 3P-FR2-BDP01-02 | MAR01_RTU |  |  |  |  | 81 |  |  |  |  | &3P-FR2-BDP01-02 | TUN_MAR01_MMS_3P-FR2-BDP01-02 |  |  |  | YES | TUNMAR01MMS3P-FR2-BDP01-02 | 26
B2.1 | N |  |  |  | MCB 2P MAR01-FR2-BDP01-02 | TUN:MAR01 | MMS | MCB | 2P-FR2-BDP01-02 | MAR01_RTU |  |  |  |  | 82 |  |  |  |  | &2P-FR2-BDP01-02 | TUN_MAR01_MMS_2P-FR2-BDP01-02 |  |  |  | YES | TUNMAR01MMS2P-FR2-BDP01-02 | 26
B2.1 | N |  |  |  | MCB MAR01-MSFD-CON-63 | TUN:MAR01 | MMS | MCB | MSFD-CON-63 | MAR01_RTU |  |  |  |  | 83 |  |  |  |  | &MSFD-CON-63 | TUN_MAR01_MMS_MSFD-CON-63 |  |  |  | YES | TUNMAR01MMSMSFD-CON-63 | 22
B2.1 | N |  |  |  | MCB MAR01-MSFD-CON-59 | TUN:MAR01 | MMS | MCB | MSFD-CON-59 | MAR01_RTU |  |  |  |  | 84 |  |  |  |  | &MSFD-CON-59 | TUN_MAR01_MMS_MSFD-CON-59 |  |  |  | YES | TUNMAR01MMSMSFD-CON-59 | 22
B2.1 | N |  |  |  | MCB MAR01-MSFD-CON-67 | TUN:MAR01 | MMS | MCB | MSFD-CON-67 | MAR01_RTU |  |  |  |  | 85 |  |  |  |  | &MSFD-CON-67 | TUN_MAR01_MMS_MSFD-CON-67 |  |  |  | YES | TUNMAR01MMSMSFD-CON-67 | 22
B1.6 | Y |  |  |  |  | Electrical Panel EL2 I/O 01
B2.1 | N |  |  |  | MAR01-EL2-IO01 | TUN:MAR01 | MMS | EL | EL2-IO01 | MAR01_RTU |  |  |  |  | 86 |  |  |  |  | &EL2-IO01 | TUN_MAR01_MMS_EL2-IO01 |  |  |  | YES | TUNMAR01MMSEL2-IO01 | 19
B2.1 | N |  |  |  | MCB MAR01-EL2-LBS01 | TUN:MAR01 | MMS | MCB | EL2-LBS01 | MAR01_RTU |  |  |  |  | 87 |  |  |  |  | &EL2-LBS01 | TUN_MAR01_MMS_EL2-LBS01 |  |  |  | YES | TUNMAR01MMSEL2-LBS01 | 20
B2.1 | N |  |  |  | MCB MAR01-EL2-LBS02 | TUN:MAR01 | MMS | MCB | EL2-LBS02 | MAR01_RTU |  |  |  |  | 88 |  |  |  |  | &EL2-LBS02 | TUN_MAR01_MMS_EL2-LBS02 |  |  |  | YES | TUNMAR01MMSEL2-LBS02 | 20
B2.1 | N |  |  |  | MCB MAR01-EL2-CBC01 | TUN:MAR01 | MMS | MCB | EL2-CBC01 | MAR01_RTU |  |  |  |  | 89 |  |  |  |  | &EL2-CBC01 | TUN_MAR01_MMS_EL2-CBC01 |  |  |  | YES | TUNMAR01MMSEL2-CBC01 | 20
B2.1 | N |  |  |  | MCB MAR01-EL2-CBC02 | TUN:MAR01 | MMS | MCB | EL2-CBC02 | MAR01_RTU |  |  |  |  | 90 |  |  |  |  | &EL2-CBC02 | TUN_MAR01_MMS_EL2-CBC02 |  |  |  | YES | TUNMAR01MMSEL2-CBC02 | 20
B2.1 | N |  |  |  | MCCB 2P MAR01-EL2 | TUN:MAR01 | MMS | MCCB | EL2-2P | MAR01_RTU |  |  |  |  | 91 |  |  |  |  | &EL2-2P | TUN_MAR01_MMS_EL2-2P |  |  |  | YES | TUNMAR01MMSEL2-2P | 17
B2.1 | N |  |  |  | LBS 2P MAR01-EL2 | TUN:MAR01 | MMS | LBS | EL2-2P | MAR01_RTU |  |  |  |  | 92 |  |  |  |  | &EL2-2P | TUN_MAR01_MMS_EL2-2P |  |  |  | YES | TUNMAR01MMSEL2-2P | 17
B2.1 | N |  |  |  | MCB MAR01-EL2-CBC01 | TUN:MAR01 | MMS | MCB | EL2-CBC01 | MAR01_RTU |  |  |  |  | 93 |  |  |  |  | &EL2-CBC01 | TUN_MAR01_MMS_EL2-CBC01 |  |  |  | YES | TUNMAR01MMSEL2-CBC01 | 20
B2.1 | N |  |  |  | MCB MAR01-EL2-CBC02 | TUN:MAR01 | MMS | MCB | EL2-CBC02 | MAR01_RTU |  |  |  |  | 94 |  |  |  |  | &EL2-CBC02 | TUN_MAR01_MMS_EL2-CBC02 |  |  |  | YES | TUNMAR01MMSEL2-CBC02 | 20
B2.1 | N |  |  |  | MCB MAR01-EL2-VSD01 | TUN:MAR01 | MMS | MCB | EL2-VSD01 | MAR01_RTU |  |  |  |  | 95 |  |  |  |  | &EL2-VSD01 | TUN_MAR01_MMS_EL2-VSD01 |  |  |  | YES | TUNMAR01MMSEL2-VSD01 | 20
B2.1 | N |  |  |  | MCB MAR01-EL2-VSD02 | TUN:MAR01 | MMS | MCB | EL2-VSD02 | MAR01_RTU |  |  |  |  | 96 |  |  |  |  | &EL2-VSD02 | TUN_MAR01_MMS_EL2-VSD02 |  |  |  | YES | TUNMAR01MMSEL2-VSD02 | 20
B2.1 | N |  |  |  | MCB MAR01-EL2-LBS01 | TUN:MAR01 | MMS | MCB | EL2-LBS01 | MAR01_RTU |  |  |  |  | 97 |  |  |  |  | &EL2-LBS01 | TUN_MAR01_MMS_EL2-LBS01 |  |  |  | YES | TUNMAR01MMSEL2-LBS01 | 20
B2.1 | N |  |  |  | MCB MAR01-EL2-LBS02 | TUN:MAR01 | MMS | MCB | EL2-LBS02 | MAR01_RTU |  |  |  |  | 98 |  |  |  |  | &EL2-LBS02 | TUN_MAR01_MMS_EL2-LBS02 |  |  |  | YES | TUNMAR01MMSEL2-LBS02 | 20
B2.1 | N |  |  |  | MCB 3P MAR01-VT1-IDP01 | TUN:MAR01 | MMS | MCB | 3P-VT1-IDP01 | MAR01_RTU |  |  |  |  | 99 |  |  |  |  | &3P-VT1-IDP01 | TUN_MAR01_MMS_3P-VT1-IDP01 |  |  |  | YES | TUNMAR01MMS3P-VT1-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P MAR01-VT1-IDP01 | TUN:MAR01 | MMS | MCB | 2P-VT1-IDP01 | MAR01_RTU |  |  |  |  | 100 |  |  |  |  | &2P-VT1-IDP01 | TUN_MAR01_MMS_2P-VT1-IDP01 |  |  |  | YES | TUNMAR01MMS2P-VT1-IDP01 | 23
B2.1 | N |  |  |  | MCB 3P MAR01-VT2-IDP01 | TUN:MAR01 | MMS | MCB | 3P-VT2-IDP01 | MAR01_RTU |  |  |  |  | 101 |  |  |  |  | &3P-VT2-IDP01 | TUN_MAR01_MMS_3P-VT2-IDP01 |  |  |  | YES | TUNMAR01MMS3P-VT2-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P MAR01-VT2-IDP01 | TUN:MAR01 | MMS | MCB | 2P-VT2-IDP01 | MAR01_RTU |  |  |  |  | 102 |  |  |  |  | &2P-VT2-IDP01 | TUN_MAR01_MMS_2P-VT2-IDP01 |  |  |  | YES | TUNMAR01MMS2P-VT2-IDP01 | 23
B2.1 | N |  |  |  | MCB 3P MAR01-VT5-IDP01-01 | TUN:MAR01 | MMS | MCB | 3P-VT5-IDP01-01 | MAR01_RTU |  |  |  |  | 103 |  |  |  |  | &3P-VT5-IDP01-01 | TUN_MAR01_MMS_3P-VT5-IDP01-01 |  |  |  | YES | TUNMAR01MMS3P-VT5-IDP01-01 | 26
B2.1 | N |  |  |  | MCB 2P MAR01-VT5-IDP01-01 | TUN:MAR01 | MMS | MCB | 2P-VT5-IDP01-01 | MAR01_RTU |  |  |  |  | 104 |  |  |  |  | &2P-VT5-IDP01-01 | TUN_MAR01_MMS_2P-VT5-IDP01-01 |  |  |  | YES | TUNMAR01MMS2P-VT5-IDP01-01 | 26
B2.1 | N |  |  |  | MCB 3P MAR01-VT5-IDP01-02 | TUN:MAR01 | MMS | MCB | 3P-VT5-IDP01-02 | MAR01_RTU |  |  |  |  | 105 |  |  |  |  | &3P-VT5-IDP01-02 | TUN_MAR01_MMS_3P-VT5-IDP01-02 |  |  |  | YES | TUNMAR01MMS3P-VT5-IDP01-02 | 26
B2.1 | N |  |  |  | MCB 2P MAR01-VT5-IDP01-02 | TUN:MAR01 | MMS | MCB | 2P-VT5-IDP01-02 | MAR01_RTU |  |  |  |  | 106 |  |  |  |  | &2P-VT5-IDP01-02 | TUN_MAR01_MMS_2P-VT5-IDP01-02 |  |  |  | YES | TUNMAR01MMS2P-VT5-IDP01-02 | 26
B2.1 | N |  |  |  | MCB 3P MAR01-VT5-IDP01-03 | TUN:MAR01 | MMS | MCB | 3P-VT5-IDP01-03 | MAR01_RTU |  |  |  |  | 107 |  |  |  |  | &3P-VT5-IDP01-03 | TUN_MAR01_MMS_3P-VT5-IDP01-03 |  |  |  | YES | TUNMAR01MMS3P-VT5-IDP01-03 | 26
B2.1 | N |  |  |  | MCB 2P MAR01-VT5-IDP01-03 | TUN:MAR01 | MMS | MCB | 2P-VT5-IDP01-03 | MAR01_RTU |  |  |  |  | 108 |  |  |  |  | &2P-VT5-IDP01-03 | TUN_MAR01_MMS_2P-VT5-IDP01-03 |  |  |  | YES | TUNMAR01MMS2P-VT5-IDP01-03 | 26
B2.1 | N |  |  |  | MCB 3P MAR01-FR1-BDP01-01 | TUN:MAR01 | MMS | MCB | 3P-FR1-BDP01-01 | MAR01_RTU |  |  |  |  | 109 |  |  |  |  | &3P-FR1-BDP01-01 | TUN_MAR01_MMS_3P-FR1-BDP01-01 |  |  |  | YES | TUNMAR01MMS3P-FR1-BDP01-01 | 26
B2.1 | N |  |  |  | MCB 2P MAR01-FR1-BDP01-01 | TUN:MAR01 | MMS | MCB | 2P-FR1-BDP01-01 | MAR01_RTU |  |  |  |  | 110 |  |  |  |  | &2P-FR1-BDP01-01 | TUN_MAR01_MMS_2P-FR1-BDP01-01 |  |  |  | YES | TUNMAR01MMS2P-FR1-BDP01-01 | 26
B2.1 | N |  |  |  | MCB 3P MAR01-FR1-BDP01-02 | TUN:MAR01 | MMS | MCB | 3P-FR1-BDP01-02 | MAR01_RTU |  |  |  |  | 111 |  |  |  |  | &3P-FR1-BDP01-02 | TUN_MAR01_MMS_3P-FR1-BDP01-02 |  |  |  | YES | TUNMAR01MMS3P-FR1-BDP01-02 | 26
B2.1 | N |  |  |  | MCB 2P MAR01-FR1-BDP01-02 | TUN:MAR01 | MMS | MCB | 2P-FR1-BDP01-02 | MAR01_RTU |  |  |  |  | 112 |  |  |  |  | &2P-FR1-BDP01-02 | TUN_MAR01_MMS_2P-FR1-BDP01-02 |  |  |  | YES | TUNMAR01MMS2P-FR1-BDP01-02 | 26
B2.1 | N |  |  |  | MCB MAR01-MSFD-CON-54 | TUN:MAR01 | MMS | MCB | MSFD-CON-54 | MAR01_RTU |  |  |  |  | 113 |  |  |  |  | &MSFD-CON-54 | TUN_MAR01_MMS_MSFD-CON-54 |  |  |  | YES | TUNMAR01MMSMSFD-CON-54 | 22
B2.1 | N |  |  |  | MCB MAR01-MSFD-CON-52 | TUN:MAR01 | MMS | MCB | MSFD-CON-52 | MAR01_RTU |  |  |  |  | 114 |  |  |  |  | &MSFD-CON-52 | TUN_MAR01_MMS_MSFD-CON-52 |  |  |  | YES | TUNMAR01MMSMSFD-CON-52 | 22
B2.1 | N |  |  |  | MCB MAR01-MSFD-CON-58 | TUN:MAR01 | MMS | MCB | MSFD-CON-58 | MAR01_RTU |  |  |  |  | 115 |  |  |  |  | &MSFD-CON-58 | TUN_MAR01_MMS_MSFD-CON-58 |  |  |  | YES | TUNMAR01MMSMSFD-CON-58 | 22
B1.5 | Y |  |  |  |  | MAR-0A SHAFT
B1.5 | Y |  |  |  |  | LOCAL CONTROL PANEL (LCP) [STATION HMI]
B2.1 | Y |  |  |  | Local control panel | TUN:MAR0A | SCR | LCP | LCP01 | MAR0A_RTU |  |  |  |  | 1 |  |  |  |  | &LCP01 | TUN_MAR0A_SCR_LCP01 |  |  |  | YES | TUNMAR0ASCRLCP01 | 16
B1.5 | Y |  |  |  |  | FIRE MANUAL OVERRIDE PANEL (FMOP)
B2.1 | Y |  |  |  | Fire control panel | TUN:MAR0A | SCR | FMOP | FMOP01 | MAR0A_RTU |  |  |  |  | 2 |  |  |  |  | &FMOP01 | TUN_MAR0A_SCR_FMOP01 |  |  |  | YES | TUNMAR0ASCRFMOP01 | 17
B1.5 | Y |  |  |  |  | Station PLC (SPLC)
B2.1 | Y |  |  |  | Station PLC | TUN:MAR0A | TEL | SPLC | PLC01 | MAR0A_RTU |  |  |  |  | 3 |  |  |  |  | &PLC01 | TUN_MAR0A_TEL_PLC01 |  |  |  | YES | TUNMAR0ATELPLC01 | 16
B1.5 | Y |  |  |  |  | Switch (SWI)
B2.1 | Y |  |  |  | Switch | TUN:MAR0A | TEL | SWI | SWI01 | MAR0A_RTU |  |  |  |  | 4 |  |  |  |  | &SWI01 | TUN_MAR0A_TEL_SWI01 |  |  |  | YES | TUNMAR0ATELSWI01 | 16
B1.5 | Y |  |  |  |  | Outdoor temperature sensor (OTS)
B2.1 | Y |  |  |  | Outdoor temperature sensor 1 | TUN:MAR0A | OTS | OTS | OTS001 | MAR0A_RTU |  |  |  |  | 5 |  |  |  |  | &OTS001 | TUN_MAR0A_OTS_OTS001 |  |  |  | YES | TUNMAR0AOTSOTS001 | 17
B1.5 | Y |  |  |  |  | Tunnel temperature & humidity sensor (TTS)
B2.1 | Y |  |  |  | Tunnel temperature sensor 1 | TUN:MAR0A | SENSOR | TTS | TS099152 | MAR0A_RTU |  |  |  |  | 6 |  |  |  |  | &TS099152 | TUN_MAR0A_SENSOR_TS099152 |  |  |  | YES | TUNMAR0ASENSORTS099152 | 23
B2.1 | Y |  |  |  | Tunnel temperature sensor 2 | TUN:MAR0A | SENSOR | TTS | TS099343 | MAR0A_RTU |  |  |  |  | 7 |  |  |  |  | &TS099343 | TUN_MAR0A_SENSOR_TS099343 |  |  |  | YES | TUNMAR0ASENSORTS099343 | 22
B2.1 | Y |  |  |  | Tunnel temperature sensor 3 | TUN:MAR0A | SENSOR | TTS | TS099620 | MAR0A_RTU |  |  |  |  | 8 |  |  |  |  | &TS099620 | TUN_MAR0A_SENSOR_TS099620 |  |  |  | YES | TUNMAR0ASENSORTS099620 | 22
B2.1 | Y |  |  |  | Tunnel temperature sensor 4 | TUN:MAR0A | SENSOR | TTS | TS099718 | MAR0A_RTU |  |  |  |  | 9 |  |  |  |  | &TS099718 | TUN_MAR0A_SENSOR_TS099718 |  |  |  | YES | TUNMAR0ASENSORTS099718 | 22
B1.5 | Y |  |  |  |  | Air velocity sensor (VS)
B2.1 | Y |  |  |  | Air velocity sensor 1 -099216 | TUN:MAR0A | SENSOR | VS | VS099216 | MAR0A_RTU |  |  |  |  | 10 |  |  |  |  | &VS099216 | TUN_MAR0A_SENSOR_VS099216 |  |  |  | YES | TUNMAR0ASENSORVS099216 | 22
B2.1 | Y |  |  |  | Air velocity sensor 2 -099685 | TUN:MAR0A | SENSOR | VS | VS099685 | MAR0A_RTU |  |  |  |  | 11 |  |  |  |  | &VS099685 | TUN_MAR0A_SENSOR_VS099685 |  |  |  | YES | TUNMAR0ASENSORVS099685 | 22
B1.5 | Y |  |  |  |  | Tunnel ventilation fan (TVF)
B2.1 | Y |  |  |  | Shaft Tunnel ventilation fan 1 | TUN:MAR0A | TVF | TVF | VT1-TVF01 | MAR0A_RTU |  |  |  |  | 12 |  |  |  |  | &VT1-TVF01 | TUN_MAR0A_TVF_VT1-TVF01 |  |  |  | YES | TUNMAR0ATVFVT1-TVF01 | 20
B2.1 | Y |  |  |  | Shaft Tunnel ventilation fan 2 | TUN:MAR0A | TVF | TVF | VT2-TVF01 | MAR0A_RTU |  |  |  |  | 13 |  |  |  |  | &VT2-TVF01 | TUN_MAR0A_TVF_VT2-TVF01 |  |  |  | YES | TUNMAR0ATVFVT2-TVF01 | 20
B1.5 | Y |  |  |  |  | TVS Damper : Isolation damper (IDP)
B2.1 | N |  |  |  | Isolation damper 1 | TUN:MAR0A | DAMPER | IDP | VT1-IDP01 | MAR0A_RTU |  |  |  |  | 14 |  |  |  |  | &VT1-IDP01 | TUN_MAR0A_DAMPER_VT1-IDP01 |  |  |  | YES | TUNMAR0ADAMPERVT1-IDP01 | 23
B2.1 | N |  |  |  | Isolation damper 2 | TUN:MAR0A | DAMPER | IDP | VT2-IDP01 | MAR0A_RTU |  |  |  |  | 15 |  |  |  |  | &VT2-IDP01 | TUN_MAR0A_DAMPER_VT2-IDP01 |  |  |  | YES | TUNMAR0ADAMPERVT2-IDP01 | 23
B1.5 | Y |  |  |  |  | PRESSURIZATION FAN (PFA)
B2.1 | Y |  |  |  | Pressurization fan Lobby | TUN:MAR0A | PFA | PFA | GRD-01 | MAR0A_RTU |  |  |  |  | 16 |  |  |  |  | &GRD-01 | TUN_MAR0A_PFA_GRD-01 |  |  |  | YES | TUNMAR0APFAGRD-01 | 17
B2.1 | Y |  |  |  | Pressurization fan Staircase | TUN:MAR0A | PFA | PFA | GRD-02 | MAR0A_RTU |  |  |  |  | 17 |  |  |  |  | &GRD-02 | TUN_MAR0A_PFA_GRD-02 |  |  |  | YES | TUNMAR0APFAGRD-02 | 17
B1.6 | Y |  |  |  |  | MMS Equipment
B2.1 | N |  |  |  | Station PLC (MMS) | TUN:MAR0A | MMS | SPLCMMS | SPLC01 | MAR0A_RTU |  |  |  |  | 18 |  |  |  |  | &SPLC01 | TUN_MAR0A_MMS_SPLC01 |  |  |  | YES | TUNMAR0AMMSSPLC01 | 17
B1.6 | Y |  |  |  |  | Electrical Equipment
B2.1 | N |  |  |  | MAR0A-EL3-LBW01 | TUN:MAR0A | MMS | ADS | EL3-LBW01 | MAR0A_RTU |  |  |  |  | 19 |  |  |  |  | &EL3-LBW01 | TUN_MAR0A_MMS_EL3-LBW01 |  |  |  | YES | TUNMAR0AMMSEL3-LBW01 | 20
B2.1 | N |  |  |  | MAR0A-EL3-LBW02 | TUN:MAR0A | MMS | ADS | EL3-LBW02 | MAR0A_RTU |  |  |  |  | 20 |  |  |  |  | &EL3-LBW02 | TUN_MAR0A_MMS_EL3-LBW02 |  |  |  | YES | TUNMAR0AMMSEL3-LBW02 | 20
B2.1 | N |  |  |  | MAR0A-EL3-TRF01 | TUN:MAR0A | MMS | TRF | EL3-TRF01 | MAR0A_RTU |  |  |  |  | 21 |  |  |  |  | &EL3-TRF01 | TUN_MAR0A_MMS_EL3-TRF01 |  |  |  | YES | TUNMAR0AMMSEL3-TRF01 | 20
B2.1 | N |  |  |  | MAR0A-EL3-TRF02 | TUN:MAR0A | MMS | TRF | EL3-TRF02 | MAR0A_RTU |  |  |  |  | 22 |  |  |  |  | &EL3-TRF02 | TUN_MAR0A_MMS_EL3-TRF02 |  |  |  | YES | TUNMAR0AMMSEL3-TRF02 | 20
B2.1 | N |  |  |  | MAR0A-EL3-MDB01 | TUN:MAR0A | MMS | MDB | EL3-MDB01 | MAR0A_RTU |  |  |  |  | 23 |  |  |  |  | &EL3-MDB01 | TUN_MAR0A_MMS_EL3-MDB01 |  |  |  | YES | TUNMAR0AMMSEL3-MDB01 | 20
B1.6 | Y |  |  |  |  | Electrical Panel EL3 PLC 01
B2.1 | N |  |  |  | MAR0A-EL3-PLC01 | TUN:MAR0A | MMS | EL | EL3-PLC01 | MAR0A_RTU |  |  |  |  | 24 |  |  |  |  | &EL3-PLC01 | TUN_MAR0A_MMS_EL3-PLC01 |  |  |  | YES | TUNMAR0AMMSEL3-PLC01 | 20
B2.1 | N |  |  |  | LBS 4P MAR0A-EL3 | TUN:MAR0A | MMS | LBS | EL3-4P | MAR0A_RTU |  |  |  |  | 25 |  |  |  |  | &EL3-4P | TUN_MAR0A_MMS_EL3-4P |  |  |  | YES | TUNMAR0AMMSEL3-4P | 17
B2.1 | N |  |  |  | MCB MAR0A-EL3-LBW01 | TUN:MAR0A | MMS | MCB | EL3-LBW01 | MAR0A_RTU |  |  |  |  | 26 |  |  |  |  | &EL3-LBW01 | TUN_MAR0A_MMS_EL3-LBW01 |  |  |  | YES | TUNMAR0AMMSEL3-LBW01 | 20
B2.1 | N |  |  |  | MCB MAR0A-EL3-LBW02 | TUN:MAR0A | MMS | MCB | EL3-LBW02 | MAR0A_RTU |  |  |  |  | 27 |  |  |  |  | &EL3-LBW02 | TUN_MAR0A_MMS_EL3-LBW02 |  |  |  | YES | TUNMAR0AMMSEL3-LBW02 | 20
B2.1 | N |  |  |  | MCCB 2P MAR0A-EL3 | TUN:MAR0A | MMS | MCCB | EL3-2P | MAR0A_RTU |  |  |  |  | 28 |  |  |  |  | &EL3-2P | TUN_MAR0A_MMS_EL3-2P |  |  |  | YES | TUNMAR0AMMSEL3-2P | 17
B2.1 | N |  |  |  | LBS 2P MAR0A-EL3 | TUN:MAR0A | MMS | LBS | EL3-2P | MAR0A_RTU |  |  |  |  | 29 |  |  |  |  | &EL3-2P | TUN_MAR0A_MMS_EL3-2P |  |  |  | YES | TUNMAR0AMMSEL3-2P | 17
B2.1 | N |  |  |  | MCB MAR0A-EL3-VSD01 | TUN:MAR0A | MMS | MCB | EL3-VSD01 | MAR0A_RTU |  |  |  |  | 30 |  |  |  |  | &EL3-VSD01 | TUN_MAR0A_MMS_EL3-VSD01 |  |  |  | YES | TUNMAR0AMMSEL3-VSD01 | 20
B2.1 | N |  |  |  | MCB MAR0A-EL3-VSD02 | TUN:MAR0A | MMS | MCB | EL3-VSD02 | MAR0A_RTU |  |  |  |  | 31 |  |  |  |  | &EL3-VSD02 | TUN_MAR0A_MMS_EL3-VSD02 |  |  |  | YES | TUNMAR0AMMSEL3-VSD02 | 20
B2.1 | N |  |  |  | MCB MAR0A-EL3-LBW01 | TUN:MAR0A | MMS | MCB | EL3-LBW01 | MAR0A_RTU |  |  |  |  | 32 |  |  |  |  | &EL3-LBW01 | TUN_MAR0A_MMS_EL3-LBW01 |  |  |  | YES | TUNMAR0AMMSEL3-LBW01 | 20
B2.1 | N |  |  |  | MCB MAR0A-EL3-LBW02 | TUN:MAR0A | MMS | MCB | EL3-LBW02 | MAR0A_RTU |  |  |  |  | 33 |  |  |  |  | &EL3-LBW02 | TUN_MAR0A_MMS_EL3-LBW02 |  |  |  | YES | TUNMAR0AMMSEL3-LBW02 | 20
B2.1 | N |  |  |  | MCB MAR0A-EL3-MDB01 | TUN:MAR0A | MMS | MCB | EL3-MDB01 | MAR0A_RTU |  |  |  |  | 34 |  |  |  |  | &EL3-MDB01 | TUN_MAR0A_MMS_EL3-MDB01 |  |  |  | YES | TUNMAR0AMMSEL3-MDB01 | 20
B2.1 | N |  |  |  | MCB 3P MAR0A-VT1-IDP01 | TUN:MAR0A | MMS | MCB | 3P-VT1-IDP01 | MAR0A_RTU |  |  |  |  | 35 |  |  |  |  | &3P-VT1-IDP01 | TUN_MAR0A_MMS_3P-VT1-IDP01 |  |  |  | YES | TUNMAR0AMMS3P-VT1-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P MAR0A-VT1-IDP01 | TUN:MAR0A | MMS | MCB | 2P-VT1-IDP01 | MAR0A_RTU |  |  |  |  | 36 |  |  |  |  | &2P-VT1-IDP01 | TUN_MAR0A_MMS_2P-VT1-IDP01 |  |  |  | YES | TUNMAR0AMMS2P-VT1-IDP01 | 23
B2.1 | N |  |  |  | MCB 3P MAR0A-VT2-IDP01 | TUN:MAR0A | MMS | MCB | 3P-VT2-IDP01 | MAR0A_RTU |  |  |  |  | 37 |  |  |  |  | &3P-VT2-IDP01 | TUN_MAR0A_MMS_3P-VT2-IDP01 |  |  |  | YES | TUNMAR0AMMS3P-VT2-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P MAR0A-VT2-IDP01 | TUN:MAR0A | MMS | MCB | 2P-VT2-IDP01 | MAR0A_RTU |  |  |  |  | 38 |  |  |  |  | &2P-VT2-IDP01 | TUN_MAR0A_MMS_2P-VT2-IDP01 |  |  |  | YES | TUNMAR0AMMS2P-VT2-IDP01 | 23
B1.8 | Y |  |  |  |  | EC1-01
B1.8 | Y |  |  |  |  | LOCAL CONTROL PANEL (LCP) [STATION HMI]
B2.1 | Y |  |  |  | Local control panel | TUN:EC101 | SCR | LCP | LCP01 | EC101_RTU |  |  |  |  | 1 |  |  |  |  | &LCP01 | TUN_EC101_SCR_LCP01 |  |  |  | YES | TUNEC101SCRLCP01 | 16
B1.8 | Y |  |  |  |  | FIRE MANUAL OVERRIDE PANEL (FMOP)
B2.1 | Y |  |  |  | Fire control panel | TUN:EC101 | SCR | FMOP | FMOP01 | EC101_RTU |  |  |  |  | 2 |  |  |  |  | &FMOP01 | TUN_EC101_SCR_FMOP01 |  |  |  | YES | TUNEC101SCRFMOP01 | 17
B1.8 | Y |  |  |  |  | Station PLC (SPLC)
B2.1 | Y |  |  |  | Station PLC | TUN:EC101 | TEL | SPLC | PLC01 | EC101_RTU |  |  |  |  | 3 |  |  |  |  | &PLC01 | TUN_EC101_TEL_PLC01 |  |  |  | YES | TUNEC101TELPLC01 | 16
B1.8 | Y |  |  |  |  | Switch (SWI)
B2.1 | Y |  |  |  | Switch | TUN:EC101 | TEL | SWI | SWI01 | EC101_RTU |  |  |  |  | 4 |  |  |  |  | &SWI01 | TUN_EC101_TEL_SWI01 |  |  |  | YES | TUNEC101TELSWI01 | 16
B1.8 | Y |  |  |  |  | PRESSURIZATION FAN (PFA)
B2.1 | Y |  |  |  | Pressurization fan Lobby 1 | TUN:EC101 | WS01:PFA | PFA | CON-06 | EC101_RTU |  |  |  |  | 5 |  |  |  |  | &CON-06 | TUN_EC101_WS01_PFA_CON-06 |  |  |  | YES | TUNEC101WS01PFACON-06 | 21
B2.1 | Y |  |  |  | Pressurization fan Escape Staircase 1 | TUN:EC101 | WS01:PFA | PFA | GRD-01 | EC101_RTU |  |  |  |  | 6 |  |  |  |  | &GRD-01 | TUN_EC101_WS01_PFA_GRD-01 |  |  |  | YES | TUNEC101WS01PFAGRD-01 | 21
B2.1 | Y |  |  |  | Pressurization fan Lobby 2 | TUN:EC101 | ES01:PFA | PFA | CON-03 | EC101_RTU |  |  |  |  | 7 |  |  |  |  | &CON-03 | TUN_EC101_ES01_PFA_CON-03 |  |  |  | YES | TUNEC101ES01PFACON-03 | 21
B2.1 | Y |  |  |  | Pressurization fan Escape Staircase 2 | TUN:EC101 | ES01:PFA | PFA | CON-04 | EC101_RTU |  |  |  |  | 8 |  |  |  |  | &CON-04 | TUN_EC101_ES01_PFA_CON-04 |  |  |  | YES | TUNEC101ES01PFACON-04 | 21
B2.1 | Y |  |  |  | Pressurization fan Lobby 3 & Corridor 2 | TUN:EC101 | WS01:PFA | PFA | CON-07 | EC101_RTU |  |  |  |  | 9 |  |  |  |  | &CON-07 | TUN_EC101_WS01_PFA_CON-07 |  |  |  | YES | TUNEC101WS01PFACON-07 | 21
B2.1 | Y |  |  |  | Pressurization fan Staircase 4 | TUN:EC101 | WS01:PFA | PFA | PLA-01 | EC101_RTU |  |  |  |  | 10 |  |  |  |  | &PLA-01 | TUN_EC101_WS01_PFA_PLA-01 |  |  |  | YES | TUNEC101WS01PFAPLA-01 | 21
B1.8 | Y |  |  |  |  | SMOKE CURTAINS (SMC)
B2.1 | Y |  |  |  | Smoke Curtains 1 | TUN:EC101 | SMC | SMC | SMC01 | EC101_RTU |  |  |  |  | 11 |  |  |  |  | &SMC01 | TUN_EC101_SMC_SMC01 |  |  |  | YES | TUNEC101SMCSMC01 | 16
B2.1 | Y |  |  |  | Smoke Curtains 2 | TUN:EC101 | SMC | SMC | SMC02 | EC101_RTU |  |  |  |  | 12 |  |  |  |  | &SMC02 | TUN_EC101_SMC_SMC02 |  |  |  | YES | TUNEC101SMCSMC02 | 16
B2.1 | Y |  |  |  | Smoke Curtains 3 | TUN:EC101 | SMC | SMC | SMC03 | EC101_RTU |  |  |  |  | 13 |  |  |  |  | &SMC03 | TUN_EC101_SMC_SMC03 |  |  |  | YES | TUNEC101SMCSMC03 | 16
B2.1 | Y |  |  |  | Smoke Curtains 4 | TUN:EC101 | SMC | SMC | SMC04 | EC101_RTU |  |  |  |  | 14 |  |  |  |  | &SMC04 | TUN_EC101_SMC_SMC04 |  |  |  | YES | TUNEC101SMCSMC04 | 16
B2.1 | Y |  |  |  | Smoke Curtains 5 | TUN:EC101 | SMC | SMC | SMC05 | EC101_RTU |  |  |  |  | 15 |  |  |  |  | &SMC05 | TUN_EC101_SMC_SMC05 |  |  |  | YES | TUNEC101SMCSMC05 | 16
B2.1 | Y |  |  |  | Smoke Curtains 6 | TUN:EC101 | SMC | SMC | SMC06 | EC101_RTU |  |  |  |  | 16 |  |  |  |  | &SMC06 | TUN_EC101_SMC_SMC06 |  |  |  | YES | TUNEC101SMCSMC06 | 16
B2.1 | Y |  |  |  | Smoke Curtains 7 | TUN:EC101 | SMC | SMC | SMC07 | EC101_RTU |  |  |  |  | 17 |  |  |  |  | &SMC07 | TUN_EC101_SMC_SMC07 |  |  |  | YES | TUNEC101SMCSMC07 | 16
B2.1 | Y |  |  |  | Smoke Curtains 8 | TUN:EC101 | SMC | SMC | SMC08 | EC101_RTU |  |  |  |  | 18 |  |  |  |  | &SMC08 | TUN_EC101_SMC_SMC08 |  |  |  | YES | TUNEC101SMCSMC08 | 16
B2.1 | Y |  |  |  | Smoke Curtains 9 | TUN:EC101 | SMC | SMC | SMC09 | EC101_RTU |  |  |  |  | 19 |  |  |  |  | &SMC09 | TUN_EC101_SMC_SMC09 |  |  |  | YES | TUNEC101SMCSMC09 | 16
B2.1 | Y |  |  |  | Smoke Curtains 10 | TUN:EC101 | SMC | SMC | SMC10 | EC101_RTU |  |  |  |  | 20 |  |  |  |  | &SMC10 | TUN_EC101_SMC_SMC10 |  |  |  | YES | TUNEC101SMCSMC10 | 16
B1.8 | Y |  |  |  |  | STATION ENTRANCE DOOR (SED)
B2.1 | Y |  |  |  | Station entrance door 1 | TUN:EC101 | SED | SED | SED01 | EC101_RTU |  |  |  |  | 21 |  |  |  |  | &SED01 | TUN_EC101_SED_SED01 |  |  |  | YES | TUNEC101SEDSED01 | 16
B2.1 | Y |  |  |  | Station entrance door 2 | TUN:EC101 | SED | SED | SED02 | EC101_RTU |  |  |  |  | 22 |  |  |  |  | &SED02 | TUN_EC101_SED_SED02 |  |  |  | YES | TUNEC101SEDSED02 | 16
B2.1 | Y |  |  |  | Station entrance door 3 | TUN:EC101 | SED | SED | SED03 | EC101_RTU |  |  |  |  | 23 |  |  |  |  | &SED03 | TUN_EC101_SED_SED03 |  |  |  | YES | TUNEC101SEDSED03 | 16
B2.1 | Y |  |  |  | Station entrance door 4 | TUN:EC101 | SED | SED | SED04 | EC101_RTU |  |  |  |  | 24 |  |  |  |  | &SED04 | TUN_EC101_SED_SED04 |  |  |  | YES | TUNEC101SEDSED04 | 16
B1.8 | Y |  |  |  |  | Outdoor temperature sensor (OTS)
B2.1 | Y |  |  |  | Outdoor temperature sensor 1 | TUN:EC101 | OTS | OTS | OTS001 | EC101_RTU |  |  |  |  | 25 |  |  |  |  | &OTS001 | TUN_EC101_OTS_OTS001 |  |  |  | YES | TUNEC101OTSOTS001 | 17
B2.1 | Y |  |  |  | Outdoor temperature sensor 2 | TUN:EC101 | OTS | OTS | OTS002 | EC101_RTU |  |  |  |  | 26 |  |  |  |  | &OTS002 | TUN_EC101_OTS_OTS002 |  |  |  | YES | TUNEC101OTSOTS002 | 17
B1.8 | Y |  |  |  |  | Tunnel ventilation fan (TVF)
B2.1 | Y |  |  |  | West ShaftTunnel ventilation fan 1 | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | EC101_RTU |  |  |  |  | 27 |  |  |  |  | &VT1-TVF01 | TUN_EC101_WS01_TVF_VT1-TVF01 |  |  |  | YES | TUNEC101WS01TVFVT1-TVF01 | 24
B2.1 | Y |  |  |  | West ShaftTunnel ventilation fan 2 | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | EC101_RTU |  |  |  |  | 28 |  |  |  |  | &VT2-TVF01 | TUN_EC101_WS01_TVF_VT2-TVF01 |  |  |  | YES | TUNEC101WS01TVFVT2-TVF01 | 24
B2.1 | Y |  |  |  | East ShaftTunnel ventilation fan 3 | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | EC101_RTU |  |  |  |  | 29 |  |  |  |  | &VT3-TVF01 | TUN_EC101_ES01_TVF_VT3-TVF01 |  |  |  | YES | TUNEC101ES01TVFVT3-TVF01 | 24
B2.1 | Y |  |  |  | EastShaftTunnel ventilation fan 4 | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | EC101_RTU |  |  |  |  | 30 |  |  |  |  | &VT4-TVF01 | TUN_EC101_ES01_TVF_VT4-TVF01 |  |  |  | YES | TUNEC101ES01TVFVT4-TVF01 | 24
B1.8 | Y |  |  |  |  | Tunnel temperature & humidity sensor (TTS)
B2.1 | Y |  |  |  | West Tunnel temperature sensor 1 | TUN:EC101 | WS01:SENSOR | TTS | TS101561 | EC101_RTU |  |  |  |  | 31 |  |  |  |  | &TS101561 | TUN_EC101_WS01_SENSOR_TS101561 |  |  |  | YES | TUNEC101WS01SENSORTS101561 | 26
B2.1 | Y |  |  |  | West Tunnel temperature sensor 2 | TUN:EC101 | WS01:SENSOR | TTS | TS101647 | EC101_RTU |  |  |  |  | 32 |  |  |  |  | &TS101647 | TUN_EC101_WS01_SENSOR_TS101647 |  |  |  | YES | TUNEC101WS01SENSORTS101647 | 26
B2.1 | Y |  |  |  | East Tunnel temperature sensor 1 | TUN:EC101 | ES01:SENSOR | TTS | TS101045 | EC101_RTU |  |  |  |  | 33 |  |  |  |  | &TS101045 | TUN_EC101_ES01_SENSOR_TS101045 |  |  |  | YES | TUNEC101ES01SENSORTS101045 | 26
B2.1 | Y |  |  |  | East Tunnel temperature sensor 2 | TUN:EC101 | ES01:SENSOR | TTS | TS101184 | EC101_RTU |  |  |  |  | 34 |  |  |  |  | &TS101184 | TUN_EC101_ES01_SENSOR_TS101184 |  |  |  | YES | TUNEC101ES01SENSORTS101184 | 26
B1.8 | Y |  |  |  |  | Air velocity sensor (VS)
B2.1 | Y |  |  |  | West Air velocity sensor 1 | TUN:EC101 | WS01:SENSOR | VS | VS101618 | EC101_RTU |  |  |  |  | 35 |  |  |  |  | &VS101618 | TUN_EC101_WS01_SENSOR_VS101618 |  |  |  | YES | TUNEC101WS01SENSORVS101618 | 26
B2.1 | Y |  |  |  | East Air velocity sensor 1 | TUN:EC101 | ES01:SENSOR | VS | VS101094 | EC101_RTU |  |  |  |  | 36 |  |  |  |  | &VS101094 | TUN_EC101_ES01_SENSOR_VS101094 |  |  |  | YES | TUNEC101ES01SENSORVS101094 | 26
B1.8 | Y |  |  |  |  | TVS Damper : Tunnel damper (TDP)
B2.1 | Y |  |  |  | West Shaft Tunnel damper 1 | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | EC101_RTU |  |  |  |  | 37 |  |  |  |  | &VT5-TDP01 | TUN_EC101_WS01_DAMPER_VT5-TDP01 |  |  |  | YES | TUNEC101WS01DAMPERVT5-TDP01 | 27
B2.1 | Y |  |  |  | East Shaft Tunnel damper 2 | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | EC101_RTU |  |  |  |  | 38 |  |  |  |  | &VT6-TDP01 | TUN_EC101_ES01_DAMPER_VT6-TDP01 |  |  |  | YES | TUNEC101ES01DAMPERVT6-TDP01 | 27
B1.8 | Y |  |  |  |  | TVS Damper : Isolation damper (IDP)
B2.1 | N |  |  |  | Isolation damper 1 | TUN:EC101 | WS01:DAMPER | IDP | VT1-IDP01 | EC101_RTU |  |  |  |  | 39 |  |  |  |  | &VT1-IDP01 | TUN_EC101_WS01_DAMPER_VT1-IDP01 |  |  |  | YES | TUNEC101WS01DAMPERVT1-IDP01 | 27
B2.1 | N |  |  |  | Isolation damper 2 | TUN:EC101 | WS01:DAMPER | IDP | VT2-IDP01 | EC101_RTU |  |  |  |  | 40 |  |  |  |  | &VT2-IDP01 | TUN_EC101_WS01_DAMPER_VT2-IDP01 |  |  |  | YES | TUNEC101WS01DAMPERVT2-IDP01 | 27
B2.1 | N |  |  |  | Isolation damper 3 | TUN:EC101 | ES01:DAMPER | IDP | VT3-IDP01 | EC101_RTU |  |  |  |  | 41 |  |  |  |  | &VT3-IDP01 | TUN_EC101_ES01_DAMPER_VT3-IDP01 |  |  |  | YES | TUNEC101ES01DAMPERVT3-IDP01 | 27
B2.1 | N |  |  |  | Isolation damper 4 | TUN:EC101 | ES01:DAMPER | IDP | VT4-IDP01 | EC101_RTU |  |  |  |  | 42 |  |  |  |  | &VT4-IDP01 | TUN_EC101_ES01_DAMPER_VT4-IDP01 |  |  |  | YES | TUNEC101ES01DAMPERVT4-IDP01 | 27
B1.8 | Y |  |  |  |  | TVS Damper : Bypass damper (BDP)
B2.1 | Y |  |  |  | West Shaft Bypass damper 1 | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | EC101_RTU |  |  |  |  | 43 |  |  |  |  | &FR1-BDP01 | TUN_EC101_WS01_DAMPER_FR1-BDP01 |  |  |  | YES | TUNEC101WS01DAMPERFR1-BDP01 | 27
B2.1 | Y |  |  |  | East Shaft Bypass damper 2 | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | EC101_RTU |  |  |  |  | 44 |  |  |  |  | &FR2-BDP01 | TUN_EC101_ES01_DAMPER_FR2-BDP01 |  |  |  | YES | TUNEC101ES01DAMPERFR2-BDP01 | 27
B1.8 | Y |  |  |  |  | MEP Damper : Tunnel Cooling damper (TCDP)
B2.1 | N |  |  |  | West Shaft Tunnel Cooling damper 1 | TUN:EC101 | WS01:DAMPER | MSFD | PLA-68 | EC101_RTU |  |  |  |  | 45 |  |  |  |  | &PLA-68 | TUN_EC101_WS01_DAMPER_PLA-68 |  |  |  | YES | TUNEC101WS01DAMPERPLA-68 | 24
B2.1 | N |  |  |  | East Shaft Tunnel Cooling damper 2 | TUN:EC101 | ES01:DAMPER | MSFD | PLA-33 | EC101_RTU |  |  |  |  | 46 |  |  |  |  | &PLA-33 | TUN_EC101_ES01_DAMPER_PLA-33 |  |  |  | YES | TUNEC101ES01DAMPERPLA-33 | 24
B1.8 | Y |  |  |  |  | MEP damper : Station to exhaust duct Damper (SEDD)
B2.1 | N |  |  |  | West Shaft Station to exhaust duct damper 1 | TUN:EC101 | WS01:DAMPER | MSFD | CON-80 | EC101_RTU |  |  |  |  | 47 |  |  |  |  | &CON-80 | TUN_EC101_WS01_DAMPER_CON-80 |  |  |  | YES | TUNEC101WS01DAMPERCON-80 | 24
B2.1 | N |  |  |  | West Shaft Station to exhaust duct damper 2 | TUN:EC101 | WS01:DAMPER | MSFD | CON-72 | EC101_RTU |  |  |  |  | 48 |  |  |  |  | &CON-72 | TUN_EC101_WS01_DAMPER_CON-72 |  |  |  | YES | TUNEC101WS01DAMPERCON-72 | 24
B2.1 | N |  |  |  | East Shaft Station to exhaust duct damper 3 | TUN:EC101 | ES01:DAMPER | MSFD | CON-25 | EC101_RTU |  |  |  |  | 49 |  |  |  |  | &CON-25 | TUN_EC101_ES01_DAMPER_CON-25 |  |  |  | YES | TUNEC101ES01DAMPERCON-25 | 24
B2.1 | N |  |  |  | East Shaft Station to exhaust duct damper 4 | TUN:EC101 | ES01:DAMPER | MSFD | CON-26 | EC101_RTU |  |  |  |  | 50 |  |  |  |  | &CON-26 | TUN_EC101_ES01_DAMPER_CON-26 |  |  |  | YES | TUNEC101ES01DAMPERCON-26 | 24
B1.8 | Y |  |  |  |  | MEP damper : Station Cooling damper (SCD)
B2.1 | N |  |  |  | West Shaft Station Cooling damper 1 | TUN:EC101 | WS01:DAMPER | MSFD | CON-79 | EC101_RTU |  |  |  |  | 51 |  |  |  |  | &CON-79 | TUN_EC101_WS01_DAMPER_CON-79 |  |  |  | YES | TUNEC101WS01DAMPERCON-79 | 24
B2.1 | N |  |  |  | West Shaft Station Cooling damper 2 | TUN:EC101 | WS01:DAMPER | MSFD | CON-34 | EC101_RTU |  |  |  |  | 52 |  |  |  |  | &CON-34 | TUN_EC101_WS01_DAMPER_CON-34 |  |  |  | YES | TUNEC101WS01DAMPERCON-34 | 24
B2.1 | N |  |  |  | East Shaft Station Cooling damper 3 | TUN:EC101 | ES01:DAMPER | MSFD | CON-24 | EC101_RTU |  |  |  |  | 53 |  |  |  |  | &CON-24 | TUN_EC101_ES01_DAMPER_CON-24 |  |  |  | YES | TUNEC101ES01DAMPERCON-24 | 24
B2.1 | N |  |  |  | East Shaft Station Cooling damper 4 | TUN:EC101 | ES01:DAMPER | MSFD | CON-42 | EC101_RTU |  |  |  |  | 54 |  |  |  |  | &CON-42 | TUN_EC101_ES01_DAMPER_CON-42 |  |  |  | YES | TUNEC101ES01DAMPERCON-42 | 24
B1.8 | Y |  |  |  |  | Tunnel AIR HANDLING UNIT
B2.1 | Y |  |  |  | West ShaftTunnel Air Handling Unit 1 | TUN:EC101 | WS01:AHU | AHU | PLA-01 | EC101_RTU |  |  |  |  | 55 |  |  |  |  | &PLA-01 | TUN_EC101_WS01_AHU_PLA-01 |  |  |  | YES | TUNEC101WS01AHUPLA-01 | 21
B2.1 | Y |  |  |  | East ShaftTunnel Air Handling Unit 2 | TUN:EC101 | ES01:AHU | AHU | PLA-02 | EC101_RTU |  |  |  |  | 56 |  |  |  |  | &PLA-02 | TUN_EC101_ES01_AHU_PLA-02 |  |  |  | YES | TUNEC101ES01AHUPLA-02 | 21
B1.8 | Y |  |  |  |  | MMS Equipment
B2.1 | N |  |  |  | Station PLC (MMS) | TUN:EC101 | MMS | SPLCMMS | SPLC01 | EC101_RTU |  |  |  |  | 57 |  |  |  |  | &SPLC01 | TUN_EC101_MMS_SPLC01 |  |  |  | YES | TUNEC101MMSSPLC01 | 17
B1.8 | Y |  |  |  |  | Electrical Equipment
B2.1 | N |  |  |  | EC101-EL0-LBS01 | TUN:EC101 | MMS | ADS | EL0-LBS01 | EC101_RTU |  |  |  |  | 58 |  |  |  |  | &EL0-LBS01 | TUN_EC101_MMS_EL0-LBS01 |  |  |  | YES | TUNEC101MMSEL0-LBS01 | 20
B2.1 | N |  |  |  | EC101-EL0-LBS02 | TUN:EC101 | MMS | ADS | EL0-LBS02 | EC101_RTU |  |  |  |  | 59 |  |  |  |  | &EL0-LBS02 | TUN_EC101_MMS_EL0-LBS02 |  |  |  | YES | TUNEC101MMSEL0-LBS02 | 20
B2.1 | N |  |  |  | EC101-MV-TRF01 | TUN:EC101 | MMS | TRF | MV-TRF01 | EC101_RTU |  |  |  |  | 60 |  |  |  |  | &MV-TRF01 | TUN_EC101_MMS_MV-TRF01 |  |  |  | YES | TUNEC101MMSMV-TRF01 | 19
B2.1 | N |  |  |  | EC101-MV-TRF02 | TUN:EC101 | MMS | TRF | MV-TRF02 | EC101_RTU |  |  |  |  | 61 |  |  |  |  | &MV-TRF02 | TUN_EC101_MMS_MV-TRF02 |  |  |  | YES | TUNEC101MMSMV-TRF02 | 19
B2.1 | N |  |  |  | EC101-EL0-CBC01 | TUN:EC101 | MMS | ACB | EL0-CBC01 | EC101_RTU |  |  |  |  | 62 |  |  |  |  | &EL0-CBC01 | TUN_EC101_MMS_EL0-CBC01 |  |  |  | YES | TUNEC101MMSEL0-CBC01 | 20
B2.1 | N |  |  |  | EC101-EL0-CBC02 | TUN:EC101 | MMS | ACB | EL0-CBC02 | EC101_RTU |  |  |  |  | 63 |  |  |  |  | &EL0-CBC02 | TUN_EC101_MMS_EL0-CBC02 |  |  |  | YES | TUNEC101MMSEL0-CBC02 | 20
B2.1 | N |  |  |  | EC101-LPS-MDB01 | TUN:EC101 | MMS | MDB | LPS-MDB01 | EC101_RTU |  |  |  |  | 64 |  |  |  |  | &LPS-MDB01 | TUN_EC101_MMS_LPS-MDB01 |  |  |  | YES | TUNEC101MMSLPS-MDB01 | 20
B2.1 | N |  |  |  | EC101-LPS-MDB02 | TUN:EC101 | MMS | MDB | LPS-MDB02 | EC101_RTU |  |  |  |  | 65 |  |  |  |  | &LPS-MDB02 | TUN_EC101_MMS_LPS-MDB02 |  |  |  | YES | TUNEC101MMSLPS-MDB02 | 20
B1.8 | Y |  |  |  |  | Electrical Panel EL1 I/O 01
B2.1 | N |  |  |  | EC101-EL1-IO01 | TUN:EC101 | MMS | EL | EL1-IO01 | EC101_RTU |  |  |  |  | 66 |  |  |  |  | &EL1-IO01 | TUN_EC101_MMS_EL1-IO01 |  |  |  | YES | TUNEC101MMSEL1-IO01 | 19
B2.1 | N |  |  |  | MCB EC101-EL0-LBS01 | TUN:EC101 | MMS | MCB | EL0-LBS01 | EC101_RTU |  |  |  |  | 67 |  |  |  |  | &EL0-LBS01 | TUN_EC101_MMS_EL0-LBS01 |  |  |  | YES | TUNEC101MMSEL0-LBS01 | 20
B2.1 | N |  |  |  | MCB EC101-EL0-LBS02 | TUN:EC101 | MMS | MCB | EL0-LBS02 | EC101_RTU |  |  |  |  | 68 |  |  |  |  | &EL0-LBS02 | TUN_EC101_MMS_EL0-LBS02 |  |  |  | YES | TUNEC101MMSEL0-LBS02 | 20
B2.1 | N |  |  |  | MCB EC101-EL0-CBC01 | TUN:EC101 | MMS | MCB | EL0-CBC01 | EC101_RTU |  |  |  |  | 69 |  |  |  |  | &EL0-CBC01 | TUN_EC101_MMS_EL0-CBC01 |  |  |  | YES | TUNEC101MMSEL0-CBC01 | 20
B2.1 | N |  |  |  | MCB EC101-EL0-CBC02 | TUN:EC101 | MMS | MCB | EL0-CBC02 | EC101_RTU |  |  |  |  | 70 |  |  |  |  | &EL0-CBC02 | TUN_EC101_MMS_EL0-CBC02 |  |  |  | YES | TUNEC101MMSEL0-CBC02 | 20
B2.1 | N |  |  |  | MCCB EC101-EL1-UPS | TUN:EC101 | MMS | MCCB | EL1-UPS | EC101_RTU |  |  |  |  | 71 |  |  |  |  | &EL1-UPS | TUN_EC101_MMS_EL1-UPS |  |  |  | YES | TUNEC101MMSEL1-UPS | 18
B2.1 | N |  |  |  | MCB UPS EC101-EL0-LBS01 | TUN:EC101 | MMS | MCB | UPS_EL0-LBS01 | EC101_RTU |  |  |  |  | 72 |  |  |  |  | &UPS-EL0-LBS01 | TUN_EC101_MMS_UPS_EL0-LBS01 |  |  |  | YES | TUNEC101MMSUPS_EL0-LBS01 | 24
B2.1 | N |  |  |  | MCB UPS EC101-EL0-LBS02 | TUN:EC101 | MMS | MCB | UPS_EL0-LBS02 | EC101_RTU |  |  |  |  | 73 |  |  |  |  | &UPS-EL0-LBS02 | TUN_EC101_MMS_UPS_EL0-LBS02 |  |  |  | YES | TUNEC101MMSUPS_EL0-LBS02 | 24
B2.1 | N |  |  |  | MCB UPS EC101-EL0-CBC01 | TUN:EC101 | MMS | MCB | UPS_EL0-CBC01 | EC101_RTU |  |  |  |  | 74 |  |  |  |  | &UPS-EL0-CBC01 | TUN_EC101_MMS_UPS_EL0-CBC01 |  |  |  | YES | TUNEC101MMSUPS_EL0-CBC01 | 24
B2.1 | N |  |  |  | MCB UPS EC101-EL0-CBC02 | TUN:EC101 | MMS | MCB | UPS_EL0-CBC02 | EC101_RTU |  |  |  |  | 75 |  |  |  |  | &UPS-EL0-CBC02 | TUN_EC101_MMS_UPS_EL0-CBC02 |  |  |  | YES | TUNEC101MMSUPS_EL0-CBC02 | 24
B2.1 | N |  |  |  | MCB UPS EC101-EL1-VSD01 | TUN:EC101 | MMS | MCB | UPS_EL1-VSD01 | EC101_RTU |  |  |  |  | 76 |  |  |  |  | &UPS-EL1-VSD01 | TUN_EC101_MMS_UPS_EL1-VSD01 |  |  |  | YES | TUNEC101MMSUPS_EL1-VSD01 | 24
B2.1 | N |  |  |  | MCB UPS EC101-EL1-VSD02 | TUN:EC101 | MMS | MCB | UPS_EL1-VSD02 | EC101_RTU |  |  |  |  | 77 |  |  |  |  | &UPS-EL1-VSD02 | TUN_EC101_MMS_UPS_EL1-VSD02 |  |  |  | YES | TUNEC101MMSUPS_EL1-VSD02 | 24
B2.1 | N |  |  |  | MCB 3P EC101-VT3-IDP01 | TUN:EC101 | MMS | MCB | 3P-VT3-IDP01 | EC101_RTU |  |  |  |  | 78 |  |  |  |  | &3P-VT3-IDP01 | TUN_EC101_MMS_3P-VT3-IDP01 |  |  |  | YES | TUNEC101MMS3P-VT3-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P EC101-VT3-IDP01 | TUN:EC101 | MMS | MCB | 2P-VT3-IDP01 | EC101_RTU |  |  |  |  | 79 |  |  |  |  | &2P-VT3-IDP01 | TUN_EC101_MMS_2P-VT3-IDP01 |  |  |  | YES | TUNEC101MMS2P-VT3-IDP01 | 23
B2.1 | N |  |  |  | MCB 3P EC101-VT4-IDP01 | TUN:EC101 | MMS | MCB | 3P-VT4-IDP01 | EC101_RTU |  |  |  |  | 80 |  |  |  |  | &3P-VT4-IDP01 | TUN_EC101_MMS_3P-VT4-IDP01 |  |  |  | YES | TUNEC101MMS3P-VT4-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P EC101-VT4-IDP01 | TUN:EC101 | MMS | MCB | 2P-VT4-IDP01 | EC101_RTU |  |  |  |  | 81 |  |  |  |  | &2P-VT4-IDP01 | TUN_EC101_MMS_2P-VT4-IDP01 |  |  |  | YES | TUNEC101MMS2P-VT4-IDP01 | 23
B2.1 | N |  |  |  | MCB 3P EC101-VT6-TDP01-01 | TUN:EC101 | MMS | MCB | 3P-VT6-TDP01-01 | EC101_RTU |  |  |  |  | 82 |  |  |  |  | &3P-VT6-TDP01-01 | TUN_EC101_MMS_3P-VT6-TDP01-01 |  |  |  | YES | TUNEC101MMS3P-VT6-TDP01-01 | 26
B2.1 | N |  |  |  | MCB 2P EC101-VT6-TDP01-01 | TUN:EC101 | MMS | MCB | 2P-VT6-TDP01-01 | EC101_RTU |  |  |  |  | 83 |  |  |  |  | &2P-VT6-TDP01-01 | TUN_EC101_MMS_2P-VT6-TDP01-01 |  |  |  | YES | TUNEC101MMS2P-VT6-TDP01-01 | 26
B2.1 | N |  |  |  | MCB 3P EC101-VT6-TDP01-02 | TUN:EC101 | MMS | MCB | 3P-VT6-TDP01-02 | EC101_RTU |  |  |  |  | 84 |  |  |  |  | &3P-VT6-TDP01-02 | TUN_EC101_MMS_3P-VT6-TDP01-02 |  |  |  | YES | TUNEC101MMS3P-VT6-TDP01-02 | 26
B2.1 | N |  |  |  | MCB 2P EC101-VT6-TDP01-02 | TUN:EC101 | MMS | MCB | 2P-VT6-TDP01-02 | EC101_RTU |  |  |  |  | 85 |  |  |  |  | &2P-VT6-TDP01-02 | TUN_EC101_MMS_2P-VT6-TDP01-02 |  |  |  | YES | TUNEC101MMS2P-VT6-TDP01-02 | 26
B2.1 | N |  |  |  | MCB 3P EC101-VT6-TDP01-03 | TUN:EC101 | MMS | MCB | 3P-VT6-TDP01-03 | EC101_RTU |  |  |  |  | 86 |  |  |  |  | &3P-VT6-TDP01-03 | TUN_EC101_MMS_3P-VT6-TDP01-03 |  |  |  | YES | TUNEC101MMS3P-VT6-TDP01-03 | 26
B2.1 | N |  |  |  | MCB 2P EC101-VT6-TDP01-03 | TUN:EC101 | MMS | MCB | 2P-VT6-TDP01-03 | EC101_RTU |  |  |  |  | 87 |  |  |  |  | &2P-VT6-TDP01-03 | TUN_EC101_MMS_2P-VT6-TDP01-03 |  |  |  | YES | TUNEC101MMS2P-VT6-TDP01-03 | 26
B2.1 | N |  |  |  | MCB 3P EC101-FR2-BDP01-01 | TUN:EC101 | MMS | MCB | 3P--FR2-BDP01-01 | EC101_RTU |  |  |  |  | 88 |  |  |  |  | &3P--FR2-BDP01-01 | TUN_EC101_MMS_3P--FR2-BDP01-01 |  |  |  | YES | TUNEC101MMS3P--FR2-BDP01-01 | 27
B2.1 | N |  |  |  | MCB 2P EC101-FR2-BDP01-01 | TUN:EC101 | MMS | MCB | 2P--FR2-BDP01-01 | EC101_RTU |  |  |  |  | 89 |  |  |  |  | &2P--FR2-BDP01-01 | TUN_EC101_MMS_2P--FR2-BDP01-01 |  |  |  | YES | TUNEC101MMS2P--FR2-BDP01-01 | 27
B2.1 | N |  |  |  | MCB 3P EC101-FR2-BDP01-02 | TUN:EC101 | MMS | MCB | 3P--FR2-BDP01-02 | EC101_RTU |  |  |  |  | 90 |  |  |  |  | &3P--FR2-BDP01-02 | TUN_EC101_MMS_3P--FR2-BDP01-02 |  |  |  | YES | TUNEC101MMS3P--FR2-BDP01-02 | 27
B2.1 | N |  |  |  | MCB 2P EC101-FR2-BDP01-02 | TUN:EC101 | MMS | MCB | 2P--FR2-BDP01-02 | EC101_RTU |  |  |  |  | 91 |  |  |  |  | &2P--FR2-BDP01-02 | TUN_EC101_MMS_2P--FR2-BDP01-02 |  |  |  | YES | TUNEC101MMS2P--FR2-BDP01-02 | 27
B2.1 | N |  |  |  | MCB EC101-MSFD-CON-24 | TUN:EC101 | MMS | MCB | MSFD-CON-24 | EC101_RTU |  |  |  |  | 92 |  |  |  |  | &MSFD-CON-24 | TUN_EC101_MMS_MSFD-CON-24 |  |  |  | YES | TUNEC101MMSMSFD-CON-24 | 22
B2.1 | N |  |  |  | MCB EC101-MSFD-CON-42 | TUN:EC101 | MMS | MCB | MSFD-CON-42 | EC101_RTU |  |  |  |  | 93 |  |  |  |  | &MSFD-CON-42 | TUN_EC101_MMS_MSFD-CON-42 |  |  |  | YES | TUNEC101MMSMSFD-CON-42 | 22
B2.1 | N |  |  |  | MCB EC101-MSFD-CON-33 | TUN:EC101 | MMS | MCB | MSFD-CON-33 | EC101_RTU |  |  |  |  | 94 |  |  |  |  | &MSFD-CON-33 | TUN_EC101_MMS_MSFD-CON-33 |  |  |  | YES | TUNEC101MMSMSFD-CON-33 | 22
B1.8 | Y |  |  |  |  | Electrical Panel EL2 I/O 01
B2.1 | N |  |  |  | EC101-EL2-IO01 | TUN:EC101 | MMS | EL | EL2-IO01 | EC101_RTU |  |  |  |  | 95 |  |  |  |  | &EL2-IO01 | TUN_EC101_MMS_EL2-IO01 |  |  |  | YES | TUNEC101MMSEL2-IO01 | 19
B2.1 | N |  |  |  | MCCB EC101-EL2-UPS | TUN:EC101 | MMS | MCCB | EL2-UPS | EC101_RTU |  |  |  |  | 96 |  |  |  |  | &EL2-UPS | TUN_EC101_MMS_EL2-UPS |  |  |  | YES | TUNEC101MMSEL2-UPS | 18
B2.1 | N |  |  |  | LBS EC101-EL2-UPS | TUN:EC101 | MMS | LBS | EL2-UPS | EC101_RTU |  |  |  |  | 97 |  |  |  |  | &EL2-UPS | TUN_EC101_MMS_EL2-UPS |  |  |  | YES | TUNEC101MMSEL2-UPS | 18
B2.1 | N |  |  |  | MCB UPS EC101-EL2-VSD01 | TUN:EC101 | MMS | MCB | UPS_EL2-VSD01 | EC101_RTU |  |  |  |  | 98 |  |  |  |  | &UPS-EL2-VSD01 | TUN_EC101_MMS_UPS_EL2-VSD01 |  |  |  | YES | TUNEC101MMSUPS_EL2-VSD01 | 24
B2.1 | N |  |  |  | MCB UPS EC101-EL2-VSD02 | TUN:EC101 | MMS | MCB | UPS_EL2-VSD02 | EC101_RTU |  |  |  |  | 99 |  |  |  |  | &UPS-EL2-VSD02 | TUN_EC101_MMS_UPS_EL2-VSD02 |  |  |  | YES | TUNEC101MMSUPS_EL2-VSD02 | 24
B2.1 | N |  |  |  | MCB 3P EC101-VT1-IDP01 | TUN:EC101 | MMS | MCB | 3P-VT1-IDP01 | EC101_RTU |  |  |  |  | 100 |  |  |  |  | &3P-VT1-IDP01 | TUN_EC101_MMS_3P-VT1-IDP01 |  |  |  | YES | TUNEC101MMS3P-VT1-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P EC101-VT1-IDP01 | TUN:EC101 | MMS | MCB | 2P-VT1-IDP01 | EC101_RTU |  |  |  |  | 101 |  |  |  |  | &2P-VT1-IDP01 | TUN_EC101_MMS_2P-VT1-IDP01 |  |  |  | YES | TUNEC101MMS2P-VT1-IDP01 | 23
B2.1 | N |  |  |  | MCB 3P EC101-VT2-IDP01 | TUN:EC101 | MMS | MCB | 3P-VT2-IDP01 | EC101_RTU |  |  |  |  | 102 |  |  |  |  | &3P-VT2-IDP01 | TUN_EC101_MMS_3P-VT2-IDP01 |  |  |  | YES | TUNEC101MMS3P-VT2-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P EC101-VT2-IDP01 | TUN:EC101 | MMS | MCB | 2P-VT2-IDP01 | EC101_RTU |  |  |  |  | 103 |  |  |  |  | &2P-VT2-IDP01 | TUN_EC101_MMS_2P-VT2-IDP01 |  |  |  | YES | TUNEC101MMS2P-VT2-IDP01 | 23
B2.1 | N |  |  |  | MCB 3P EC101-VT5-IDP01-01 | TUN:EC101 | MMS | MCB | 3P-VT5-IDP01-01 | EC101_RTU |  |  |  |  | 104 |  |  |  |  | &3P-VT5-IDP01-01 | TUN_EC101_MMS_3P-VT5-IDP01-01 |  |  |  | YES | TUNEC101MMS3P-VT5-IDP01-01 | 26
B2.1 | N |  |  |  | MCB 2P EC101-VT5-IDP01-01 | TUN:EC101 | MMS | MCB | 2P-VT5-IDP01-01 | EC101_RTU |  |  |  |  | 105 |  |  |  |  | &2P-VT5-IDP01-01 | TUN_EC101_MMS_2P-VT5-IDP01-01 |  |  |  | YES | TUNEC101MMS2P-VT5-IDP01-01 | 26
B2.1 | N |  |  |  | MCB 3P EC101-VT5-IDP01-02 | TUN:EC101 | MMS | MCB | 3P-VT5-IDP01-02 | EC101_RTU |  |  |  |  | 106 |  |  |  |  | &3P-VT5-IDP01-02 | TUN_EC101_MMS_3P-VT5-IDP01-02 |  |  |  | YES | TUNEC101MMS3P-VT5-IDP01-02 | 26
B2.1 | N |  |  |  | MCB 2P EC101-VT5-IDP01-02 | TUN:EC101 | MMS | MCB | 2P-VT5-IDP01-02 | EC101_RTU |  |  |  |  | 107 |  |  |  |  | &2P-VT5-IDP01-02 | TUN_EC101_MMS_2P-VT5-IDP01-02 |  |  |  | YES | TUNEC101MMS2P-VT5-IDP01-02 | 26
B2.1 | N |  |  |  | MCB 3P EC101-VT5-IDP01-03 | TUN:EC101 | MMS | MCB | 3P-VT5-IDP01-03 | EC101_RTU |  |  |  |  | 108 |  |  |  |  | &3P-VT5-IDP01-03 | TUN_EC101_MMS_3P-VT5-IDP01-03 |  |  |  | YES | TUNEC101MMS3P-VT5-IDP01-03 | 26
B2.1 | N |  |  |  | MCB 2P EC101-VT5-IDP01-03 | TUN:EC101 | MMS | MCB | 2P-VT5-IDP01-03 | EC101_RTU |  |  |  |  | 109 |  |  |  |  | &2P-VT5-IDP01-03 | TUN_EC101_MMS_2P-VT5-IDP01-03 |  |  |  | YES | TUNEC101MMS2P-VT5-IDP01-03 | 26
B2.1 | N |  |  |  | MCB 3P EC101-FR1-BDP01-01 | TUN:EC101 | MMS | MCB | 3P-FR1-BDP01-01 | EC101_RTU |  |  |  |  | 110 |  |  |  |  | &3P-FR1-BDP01-01 | TUN_EC101_MMS_3P-FR1-BDP01-01 |  |  |  | YES | TUNEC101MMS3P-FR1-BDP01-01 | 26
B2.1 | N |  |  |  | MCB 2P EC101-FR1-BDP01-01 | TUN:EC101 | MMS | MCB | 2P-FR1-BDP01-01 | EC101_RTU |  |  |  |  | 111 |  |  |  |  | &2P-FR1-BDP01-01 | TUN_EC101_MMS_2P-FR1-BDP01-01 |  |  |  | YES | TUNEC101MMS2P-FR1-BDP01-01 | 26
B2.1 | N |  |  |  | MCB 3P EC101-FR1-BDP01-02 | TUN:EC101 | MMS | MCB | 3P-FR1-BDP01-02 | EC101_RTU |  |  |  |  | 112 |  |  |  |  | &3P-FR1-BDP01-02 | TUN_EC101_MMS_3P-FR1-BDP01-02 |  |  |  | YES | TUNEC101MMS3P-FR1-BDP01-02 | 26
B2.1 | N |  |  |  | MCB 2P EC101-FR1-BDP01-02 | TUN:EC101 | MMS | MCB | 2P-FR1-BDP01-02 | EC101_RTU |  |  |  |  | 113 |  |  |  |  | &2P-FR1-BDP01-02 | TUN_EC101_MMS_2P-FR1-BDP01-02 |  |  |  | YES | TUNEC101MMS2P-FR1-BDP01-02 | 26
B2.1 | N |  |  |  | MCB EC101-MSFD-CON-79 | TUN:EC101 | MMS | MCB | MSFD-CON-79 | EC101_RTU |  |  |  |  | 114 |  |  |  |  | &MSFD-CON-79 | TUN_EC101_MMS_MSFD-CON-79 |  |  |  | YES | TUNEC101MMSMSFD-CON-79 | 22
B2.1 | N |  |  |  | MCB EC101-MSFD-CON-34 | TUN:EC101 | MMS | MCB | MSFD-CON-34 | EC101_RTU |  |  |  |  | 115 |  |  |  |  | &MSFD-CON-34 | TUN_EC101_MMS_MSFD-CON-34 |  |  |  | YES | TUNEC101MMSMSFD-CON-34 | 22
B2.1 | N |  |  |  | MCB EC101-MSFD-CON-68 | TUN:EC101 | MMS | MCB | MSFD-CON-68 | EC101_RTU |  |  |  |  | 116 |  |  |  |  | &MSFD-CON-68 | TUN_EC101_MMS_MSFD-CON-68 |  |  |  | YES | TUNEC101MMSMSFD-CON-68 | 22
B1.8 | Y |  |  |  |  | EC1-0A SHAFT
B1.8 | Y |  |  |  |  | LOCAL CONTROL PANEL (LCP) [STATION HMI]
B2.1 | Y |  |  |  | Local control panel | TUN:EC10A | SCR | LCP | LCP01 | EC10A_RTU |  |  |  |  | 1 |  |  |  |  | &LCP01 | TUN_EC10A_SCR_LCP01 |  |  |  | YES | TUNEC10ASCRLCP01 | 16
B1.8 | Y |  |  |  |  | FIRE MANUAL OVERRIDE PANEL (FMOP)
B2.1 | Y |  |  |  | Fire control panel | TUN:EC10A | SCR | FMOP | FMOP01 | EC10A_RTU |  |  |  |  | 2 |  |  |  |  | &FMOP01 | TUN_EC10A_SCR_FMOP01 |  |  |  | YES | TUNEC10ASCRFMOP01 | 17
B1.8 | Y |  |  |  |  | Station PLC (SPLC)
B2.1 | Y |  |  |  | Station PLC | TUN:EC10A | TEL | SPLC | PLC01 | EC10A_RTU |  |  |  |  | 3 |  |  |  |  | &PLC01 | TUN_EC10A_TEL_PLC01 |  |  |  | YES | TUNEC10ATELPLC01 | 16
B1.8 | Y |  |  |  |  | Switch (SWI)
B2.1 | Y |  |  |  | Switch | TUN:EC10A | TEL | SWI | SWI01 | EC10A_RTU |  |  |  |  | 4 |  |  |  |  | &SWI01 | TUN_EC10A_TEL_SWI01 |  |  |  | YES | TUNEC10ATELSWI01 | 16
B1.8 | Y |  |  |  |  | Outdoor temperature sensor (OTS)
B2.1 | Y |  |  |  | Outdoor temperature sensor 1 | TUN:EC10A | OTS | OTS | OTS001 | EC10A_RTU |  |  |  |  | 5 |  |  |  |  | &OTS001 | TUN_EC10A_OTS_OTS001 |  |  |  | YES | TUNEC10AOTSOTS001 | 17
B1.8 | Y |  |  |  |  | Tunnel temperature & humidity sensor (TTS)
B2.1 | Y |  |  |  | Tunnel to QEC-01 temperature sensor 1 | TUN:EC10A | SENSOR | TTS | TS100421 | EC10A_RTU |  |  |  |  | 6 |  |  |  |  | &TS100421 | TUN_EC10A_SENSOR_TS100421 |  |  |  | YES | TUNEC10ASENSORTS100421 | 22
B2.1 | Y |  |  |  | Tunnel to QEC-01 temperature sensor 2 | TUN:EC10A | SENSOR | TTS | TS100521 | EC10A_RTU |  |  |  |  | 7 |  |  |  |  | &TS100521 | TUN_EC10A_SENSOR_TS100521 |  |  |  | YES | TUNEC10ASENSORTS100521 | 22
B2.1 | Y |  |  |  | Tunnel to EC1-01 temperature sensor 1 | TUN:EC10A | SENSOR | TTS | TS100767 | EC10A_RTU |  |  |  |  | 8 |  |  |  |  | &TS100767 | TUN_EC10A_SENSOR_TS100767 |  |  |  | YES | TUNEC10ASENSORTS100767 | 22
B2.1 | Y |  |  |  | Tunnel to EC1-01 temperature sensor 2 | TUN:EC10A | SENSOR | TTS | TS100906 | EC10A_RTU |  |  |  |  | 9 |  |  |  |  | &TS100906 | TUN_EC10A_SENSOR_TS100906 |  |  |  | YES | TUNEC10ASENSORTS100906 | 22
B1.8 | Y |  |  |  |  | Air velocity sensor (VS)
B2.1 | Y |  |  |  | Tunnel to QEC-01 Air velocity sensor | TUN:EC10A | SENSOR | VS | VS100456 | EC10A_RTU |  |  |  |  | 10 |  |  |  |  | &VS100456 | TUN_EC10A_SENSOR_VS100456 |  |  |  | YES | TUNEC10ASENSORVS100456 | 22
B2.1 | Y |  |  |  | Tunnel to EC1-01 Air velocity sensor | TUN:EC10A | SENSOR | VS | VS100862 | EC10A_RTU |  |  |  |  | 11 |  |  |  |  | &VS100862 | TUN_EC10A_SENSOR_VS100862 |  |  |  | YES | TUNEC10ASENSORVS100862 | 22
B1.8 | Y |  |  |  |  | Tunnel ventilation fan (TVF)
B2.1 | Y |  |  |  | Shaft Tunnel ventilation fan 1 | TUN:EC10A | TVF | TVF | VT1-TVF01 | EC10A_RTU |  |  |  |  | 12 |  |  |  |  | &VT1-TVF01 | TUN_EC10A_TVF_VT1-TVF01 |  |  |  | YES | TUNEC10ATVFVT1-TVF01 | 20
B2.1 | Y |  |  |  | Shaft Tunnel ventilation fan 2 | TUN:EC10A | TVF | TVF | VT2-TVF01 | EC10A_RTU |  |  |  |  | 13 |  |  |  |  | &VT2-TVF01 | TUN_EC10A_TVF_VT2-TVF01 |  |  |  | YES | TUNEC10ATVFVT2-TVF01 | 20
B1.8 | Y |  |  |  |  | TVS Damper : Isolation damper (IDP)
B2.1 | N |  |  |  | Isolation damper 1 | TUN:EC10A | DAMPER | IDP | VT1-IDP01 | EC10A_RTU |  |  |  |  | 14 |  |  |  |  | &VT1-IDP01 | TUN_EC10A_DAMPER_VT1-IDP01 |  |  |  | YES | TUNEC10ADAMPERVT1-IDP01 | 23
B2.1 | N |  |  |  | Isolation damper 2 | TUN:EC10A | DAMPER | IDP | VT2-IDP01 | EC10A_RTU |  |  |  |  | 15 |  |  |  |  | &VT2-IDP01 | TUN_EC10A_DAMPER_VT2-IDP01 |  |  |  | YES | TUNEC10ADAMPERVT2-IDP01 | 23
B1.8 | Y |  |  |  |  | PRESSURIZATION FAN (PFA)
B2.1 | Y |  |  |  | Pressurization fan Stair 1 Lobby | TUN:EC10A | PFA | PFA | LPF-01 | EC10A_RTU |  |  |  |  | 16 |  |  |  |  | &LPF-01 | TUN_EC10A_PFA_LPF-01 |  |  |  | YES | TUNEC10APFALPF-01 | 17
B2.1 | Y |  |  |  | Pressurization fan Escape Stair | TUN:EC10A | PFA | PFA | SPF-01 | EC10A_RTU |  |  |  |  | 17 |  |  |  |  | &SPF-01 | TUN_EC10A_PFA_SPF-01 |  |  |  | YES | TUNEC10APFASPF-01 | 17
B1.8 | Y |  |  |  |  | MMS Equipment
B2.1 | N |  |  |  | Station PLC (MMS) | TUN:EC10A | MMS | SPLCMMS | SPLC01 | EC10A_RTU |  |  |  |  | 18 |  |  |  |  | &SPLC01 | TUN_EC10A_MMS_SPLC01 |  |  |  | YES | TUNEC10AMMSSPLC01 | 17
B1.8 | Y |  |  |  |  | Electrical Equipment
B2.1 | N |  |  |  | EC10A-EL3-LBW01 | TUN:EC10A | MMS | ADS | EL3-LBW01 | EC10A_RTU |  |  |  |  | 19 |  |  |  |  | &EL3-LBW01 | TUN_EC10A_MMS_EL3-LBW01 |  |  |  | YES | TUNEC10AMMSEL3-LBW01 | 20
B2.1 | N |  |  |  | EC10A-EL3-LBW02 | TUN:EC10A | MMS | ADS | EL3-LBW02 | EC10A_RTU |  |  |  |  | 20 |  |  |  |  | &EL3-LBW02 | TUN_EC10A_MMS_EL3-LBW02 |  |  |  | YES | TUNEC10AMMSEL3-LBW02 | 20
B2.1 | N |  |  |  | EC10A-EL3-TRF01 | TUN:EC10A | MMS | TRF | EL3-TRF01 | EC10A_RTU |  |  |  |  | 21 |  |  |  |  | &EL3-TRF01 | TUN_EC10A_MMS_EL3-TRF01 |  |  |  | YES | TUNEC10AMMSEL3-TRF01 | 20
B2.1 | N |  |  |  | EC10A-EL3-TRF02 | TUN:EC10A | MMS | TRF | EL3-TRF02 | EC10A_RTU |  |  |  |  | 22 |  |  |  |  | &EL3-TRF02 | TUN_EC10A_MMS_EL3-TRF02 |  |  |  | YES | TUNEC10AMMSEL3-TRF02 | 20
B2.1 | N |  |  |  | EC10A-EL3-MDB01 | TUN:EC10A | MMS | MDB | EL3-MDB01 | EC10A_RTU |  |  |  |  | 23 |  |  |  |  | &EL3-MDB01 | TUN_EC10A_MMS_EL3-MDB01 |  |  |  | YES | TUNEC10AMMSEL3-MDB01 | 20
B1.8 | Y |  |  |  |  | Electrical Panel EL3 PLC 01
B2.1 | N |  |  |  | EC10A-EL3-PLC01 | TUN:EC10A | MMS | EL | EL3-PLC01 | EC10A_RTU |  |  |  |  | 24 |  |  |  |  | &EL3-PLC01 | TUN_EC10A_MMS_EL3-PLC01 |  |  |  | YES | TUNEC10AMMSEL3-PLC01 | 20
B2.1 | N |  |  |  | MCB EC10A-EL3-LBW01 | TUN:EC10A | MMS | MCB | EL3-LBW01 | EC10A_RTU |  |  |  |  | 25 |  |  |  |  | &EL3-LBW01 | TUN_EC10A_MMS_EL3-LBW01 |  |  |  | YES | TUNEC10AMMSEL3-LBW01 | 20
B2.1 | N |  |  |  | MCB EC10A-EL3-LBW02 | TUN:EC10A | MMS | MCB | EL3-LBW02 | EC10A_RTU |  |  |  |  | 26 |  |  |  |  | &EL3-LBW02 | TUN_EC10A_MMS_EL3-LBW02 |  |  |  | YES | TUNEC10AMMSEL3-LBW02 | 20
B2.1 | N |  |  |  | MCCB EC10A-EL3-UPS | TUN:EC10A | MMS | MCCB | EL3-UPS | EC10A_RTU |  |  |  |  | 27 |  |  |  |  | &EL3-UPS | TUN_EC10A_MMS_EL3-UPS |  |  |  | YES | TUNEC10AMMSEL3-UPS | 18
B2.1 | N |  |  |  | LBS EC10A-EL3-UPS | TUN:EC10A | MMS | LBS | EL3-UPS | EC10A_RTU |  |  |  |  | 28 |  |  |  |  | &EL3-UPS | TUN_EC10A_MMS_EL3-UPS |  |  |  | YES | TUNEC10AMMSEL3-UPS | 18
B2.1 | N |  |  |  | MCB UPS EC10A-EL3-VSD01 | TUN:EC10A | MMS | MCB | UPS_EL3-VSD01 | EC10A_RTU |  |  |  |  | 29 |  |  |  |  | &UPS-EL3-VSD01 | TUN_EC10A_MMS_UPS_EL3-VSD01 |  |  |  | YES | TUNEC10AMMSUPS_EL3-VSD01 | 24
B2.1 | N |  |  |  | MCB UPS EC10A-EL3-VSD02 | TUN:EC10A | MMS | MCB | UPS_EL3-VSD02 | EC10A_RTU |  |  |  |  | 30 |  |  |  |  | &UPS-EL3-VSD02 | TUN_EC10A_MMS_UPS_EL3-VSD02 |  |  |  | YES | TUNEC10AMMSUPS_EL3-VSD02 | 24
B2.1 | N |  |  |  | MCB UPS EC10A-EL3-LBW01 | TUN:EC10A | MMS | MCB | UPS_EL3-LBW01 | EC10A_RTU |  |  |  |  | 31 |  |  |  |  | &UPS-EL3-LBW01 | TUN_EC10A_MMS_UPS_EL3-LBW01 |  |  |  | YES | TUNEC10AMMSUPS_EL3-LBW01 | 24
B2.1 | N |  |  |  | MCB UPS EC10A-EL3-LBW02 | TUN:EC10A | MMS | MCB | UPS_EL3-LBW02 | EC10A_RTU |  |  |  |  | 32 |  |  |  |  | &UPS-EL3-LBW02 | TUN_EC10A_MMS_UPS_EL3-LBW02 |  |  |  | YES | TUNEC10AMMSUPS_EL3-LBW02 | 24
B2.1 | N |  |  |  | MCB UPS EC10A-EL3-MDB01 | TUN:EC10A | MMS | MCB | UPS_EL3-MDB01 | EC10A_RTU |  |  |  |  | 33 |  |  |  |  | &UPS-EL3-MDB01 | TUN_EC10A_MMS_UPS_EL3-MDB01 |  |  |  | YES | TUNEC10AMMSUPS_EL3-MDB01 | 24
B2.1 | N |  |  |  | MCB 3P EC10A-VT1-IDP01 | TUN:EC10A | MMS | MCB | 3P-VT1-IDP01 | EC10A_RTU |  |  |  |  | 34 |  |  |  |  | &3P-VT1-IDP01 | TUN_EC10A_MMS_3P-VT1-IDP01 |  |  |  | YES | TUNEC10AMMS3P-VT1-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P EC10A-VT1-IDP01 | TUN:EC10A | MMS | MCB | 2P-VT1-IDP01 | EC10A_RTU |  |  |  |  | 35 |  |  |  |  | &2P-VT1-IDP01 | TUN_EC10A_MMS_2P-VT1-IDP01 |  |  |  | YES | TUNEC10AMMS2P-VT1-IDP01 | 23
B2.1 | N |  |  |  | MCB 3P EC10A-VT2-IDP01 | TUN:EC10A | MMS | MCB | 3P-VT2-IDP01 | EC10A_RTU |  |  |  |  | 36 |  |  |  |  | &3P-VT2-IDP01 | TUN_EC10A_MMS_3P-VT2-IDP01 |  |  |  | YES | TUNEC10AMMS3P-VT2-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P EC10A-VT2-IDP01 | TUN:EC10A | MMS | MCB | 2P-VT2-IDP01 | EC10A_RTU |  |  |  |  | 37 |  |  |  |  | &2P-VT2-IDP01 | TUN_EC10A_MMS_2P-VT2-IDP01 |  |  |  | YES | TUNEC10AMMS2P-VT2-IDP01 | 23
B1.8 | Y |  |  |  |  | QAP-01
B1.8 | Y |  |  |  |  | LOCAL CONTROL PANEL (LCP) [STATION HMI]
B2.1 | Y |  |  |  | Local control panel | TUN:QAP01 | SCR | LCP | LCP01 | QAP01_RTU |  |  |  |  | 1 |  |  |  |  | &LCP01 | TUN_QAP01_SCR_LCP01 |  |  |  | YES | TUNQAP01SCRLCP01 | 16
B1.8 | Y |  |  |  |  | FIRE MANUAL OVERRIDE PANEL (FMOP)
B2.1 | Y |  |  |  | Fire control panel | TUN:QAP01 | SCR | FMOP | FMOP01 | QAP01_RTU |  |  |  |  | 2 |  |  |  |  | &FMOP01 | TUN_QAP01_SCR_FMOP01 |  |  |  | YES | TUNQAP01SCRFMOP01 | 17
B1.8 | Y |  |  |  |  | Station PLC (SPLC)
B2.1 | Y |  |  |  | Station PLC | TUN:QAP01 | TEL | SPLC | PLC01 | QAP01_RTU |  |  |  |  | 3 |  |  |  |  | &PLC01 | TUN_QAP01_TEL_PLC01 |  |  |  | YES | TUNQAP01TELPLC01 | 16
B1.8 | Y |  |  |  |  | Switch (SWI)
B2.1 | Y |  |  |  | Switch | TUN:QAP01 | TEL | SWI | SWI01 | QAP01_RTU |  |  |  |  | 4 |  |  |  |  | &SWI01 | TUN_QAP01_TEL_SWI01 |  |  |  | YES | TUNQAP01TELSWI01 | 16
B1.8 | Y |  |  |  |  | PRESSURIZATION FAN (PFA)
B2.1 | Y |  |  |  | Pressurization fan Lobby 1 | TUN:QAP01 | SS01:PFA | PFA | CON-03 | QAP01_RTU |  |  |  |  | 5 |  |  |  |  | &CON-03 | TUN_QAP01_SS01_PFA_CON-03 |  |  |  | YES | TUNQAP01SS01PFACON-03 | 21
B2.1 | Y |  |  |  | Pressurization fan Escape Stair 3 | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | QAP01_RTU |  |  |  |  | 6 |  |  |  |  | &GRD-01 | TUN_QAP01_SS01_PFA_GRD-01 |  |  |  | YES | TUNQAP01SS01PFAGRD-01 | 21
B2.1 | Y |  |  |  | Pressurization fan Lobby 2 | TUN:QAP01 | NS01:PFA | PFA | CON-02 | QAP01_RTU |  |  |  |  | 7 |  |  |  |  | &CON-02 | TUN_QAP01_NS01_PFA_CON-02 |  |  |  | YES | TUNQAP01NS01PFACON-02 | 21
B2.1 | Y |  |  |  | Pressurization fan Escape Stair 4 | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | QAP01_RTU |  |  |  |  | 8 |  |  |  |  | &GRD-03 | TUN_QAP01_NS01_PFA_GRD-03 |  |  |  | YES | TUNQAP01NS01PFAGRD-03 | 21
B2.1 | Y |  |  |  | Pressurization fan Stair 1 | TUN:QAP01 | NS01:PFA | PFA | CON-04 | QAP01_RTU |  |  |  |  | 9 |  |  |  |  | &CON-04 | TUN_QAP01_NS01_PFA_CON-04 |  |  |  | YES | TUNQAP01NS01PFACON-04 | 21
B2.1 | Y |  |  |  | Pressurization fan Corridor 6 | TUN:QAP01 | NS01:PFA | PFA | CON-05 | QAP01_RTU |  |  |  |  | 10 |  |  |  |  | &CON-05 | TUN_QAP01_NS01_PFA_CON-05 |  |  |  | YES | TUNQAP01NS01PFACON-05 | 21
B1.8 | Y |  |  |  |  | SMOKE CURTAINS (SMC)
B2.1 | Y |  |  |  | Smoke Curtains 1 | TUN:QAP01 | SMC | SMC | SMC01 | QAP01_RTU |  |  |  |  | 11 |  |  |  |  | &SMC01 | TUN_QAP01_SMC_SMC01 |  |  |  | YES | TUNQAP01SMCSMC01 | 16
B2.1 | Y |  |  |  | Smoke Curtains 2 | TUN:QAP01 | SMC | SMC | SMC02 | QAP01_RTU |  |  |  |  | 12 |  |  |  |  | &SMC02 | TUN_QAP01_SMC_SMC02 |  |  |  | YES | TUNQAP01SMCSMC02 | 16
B2.1 | Y |  |  |  | Smoke Curtains 3 | TUN:QAP01 | SMC | SMC | SMC03 | QAP01_RTU |  |  |  |  | 13 |  |  |  |  | &SMC03 | TUN_QAP01_SMC_SMC03 |  |  |  | YES | TUNQAP01SMCSMC03 | 16
B2.1 | Y |  |  |  | Smoke Curtains 4 | TUN:QAP01 | SMC | SMC | SMC04 | QAP01_RTU |  |  |  |  | 14 |  |  |  |  | &SMC04 | TUN_QAP01_SMC_SMC04 |  |  |  | YES | TUNQAP01SMCSMC04 | 16
B2.1 | Y |  |  |  | Smoke Curtains 5 | TUN:QAP01 | SMC | SMC | SMC05 | QAP01_RTU |  |  |  |  | 15 |  |  |  |  | &SMC05 | TUN_QAP01_SMC_SMC05 |  |  |  | YES | TUNQAP01SMCSMC05 | 16
B2.1 | Y |  |  |  | Smoke Curtains 6 | TUN:QAP01 | SMC | SMC | SMC06 | QAP01_RTU |  |  |  |  | 16 |  |  |  |  | &SMC06 | TUN_QAP01_SMC_SMC06 |  |  |  | YES | TUNQAP01SMCSMC06 | 16
B2.1 | Y |  |  |  | Smoke Curtains 7 | TUN:QAP01 | SMC | SMC | SMC07 | QAP01_RTU |  |  |  |  | 17 |  |  |  |  | &SMC07 | TUN_QAP01_SMC_SMC07 |  |  |  | YES | TUNQAP01SMCSMC07 | 16
B2.1 | Y |  |  |  | Smoke Curtains 8 | TUN:QAP01 | SMC | SMC | SMC08 | QAP01_RTU |  |  |  |  | 18 |  |  |  |  | &SMC08 | TUN_QAP01_SMC_SMC08 |  |  |  | YES | TUNQAP01SMCSMC08 | 16
B2.1 | Y |  |  |  | Smoke Curtains 9 | TUN:QAP01 | SMC | SMC | SMC09 | QAP01_RTU |  |  |  |  | 19 |  |  |  |  | &SMC09 | TUN_QAP01_SMC_SMC09 |  |  |  | YES | TUNQAP01SMCSMC09 | 16
B2.1 | Y |  |  |  | Smoke Curtains 10 | TUN:QAP01 | SMC | SMC | SMC10 | QAP01_RTU |  |  |  |  | 20 |  |  |  |  | &SMC10 | TUN_QAP01_SMC_SMC10 |  |  |  | YES | TUNQAP01SMCSMC10 | 16
B1.8 | Y |  |  |  |  | STATION ENTRANCE DOOR (SED)
B2.1 | Y |  |  |  | Station entrance door 1 | TUN:QAP01 | SED | SED | SED01 | QAP01_RTU |  |  |  |  | 21 |  |  |  |  | &SED01 | TUN_QAP01_SED_SED01 |  |  |  | YES | TUNQAP01SEDSED01 | 16
B2.1 | Y |  |  |  | Station entrance door 2 | TUN:QAP01 | SED | SED | SED02 | QAP01_RTU |  |  |  |  | 22 |  |  |  |  | &SED02 | TUN_QAP01_SED_SED02 |  |  |  | YES | TUNQAP01SEDSED02 | 16
B2.1 | Y |  |  |  | Station entrance door 3 | TUN:QAP01 | SED | SED | SED03 | QAP01_RTU |  |  |  |  | 23 |  |  |  |  | &SED03 | TUN_QAP01_SED_SED03 |  |  |  | YES | TUNQAP01SEDSED03 | 16
B2.1 | Y |  |  |  | Station entrance door 4 | TUN:QAP01 | SED | SED | SED04 | QAP01_RTU |  |  |  |  | 24 |  |  |  |  | &SED04 | TUN_QAP01_SED_SED04 |  |  |  | YES | TUNQAP01SEDSED04 | 16
B1.8 | Y |  |  |  |  | Outdoor temperature sensor (OTS)
B2.1 | Y |  |  |  | Outdoor temperature sensor 1 | TUN:QAP01 | OTS | OTS | OTS001 | QAP01_RTU |  |  |  |  | 25 |  |  |  |  | &OTS001 | TUN_QAP01_OTS_OTS001 |  |  |  | YES | TUNQAP01OTSOTS001 | 17
B2.1 | Y |  |  |  | Outdoor temperature sensor 2 | TUN:QAP01 | OTS | OTS | OTS002 | QAP01_RTU |  |  |  |  | 26 |  |  |  |  | &OTS002 | TUN_QAP01_OTS_OTS002 |  |  |  | YES | TUNQAP01OTSOTS002 | 17
B1.8 | Y |  |  |  |  | Tunnel ventilation fan (TVF)
B2.1 | Y |  |  |  | South ShaftTunnel ventilation fan 1 | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | QAP01_RTU |  |  |  |  | 27 |  |  |  |  | &VT1-TVF01 | TUN_QAP01_SS01_TVF_VT1-TVF01 |  |  |  | YES | TUNQAP01SS01TVFVT1-TVF01 | 24
B2.1 | Y |  |  |  | South ShaftTunnel ventilation fan 2 | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | QAP01_RTU |  |  |  |  | 28 |  |  |  |  | &VT2-TVF01 | TUN_QAP01_SS01_TVF_VT2-TVF01 |  |  |  | YES | TUNQAP01SS01TVFVT2-TVF01 | 24
B2.1 | Y |  |  |  | North ShaftTunnel ventilation fan 3 | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | QAP01_RTU |  |  |  |  | 29 |  |  |  |  | &VT3-TVF01 | TUN_QAP01_NS01_TVF_VT3-TVF01 |  |  |  | YES | TUNQAP01NS01TVFVT3-TVF01 | 24
B2.1 | Y |  |  |  | NorthShaftTunnel ventilation fan 4 | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | QAP01_RTU |  |  |  |  | 30 |  |  |  |  | &VT4-TVF01 | TUN_QAP01_NS01_TVF_VT4-TVF01 |  |  |  | YES | TUNQAP01NS01TVFVT4-TVF01 | 24
B1.8 | Y |  |  |  |  | Tunnel temperature & humidity sensor (TTS)
B2.1 | Y |  |  |  | Tunnel to EC1-01 temperature sensor 1 | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | QAP01_RTU |  |  |  |  | 31 |  |  |  |  | &TS101733 | TUN_QAP01_SS01_SENSOR_TS101733 |  |  |  | YES | TUNQAP01SS01SENSORTS101733 | 26
B2.1 | Y |  |  |  | Tunnel to EC1-01 temperature sensor 2 | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | QAP01_RTU |  |  |  |  | 32 |  |  |  |  | &TS101817 | TUN_QAP01_SS01_SENSOR_TS101817 |  |  |  | YES | TUNQAP01SS01SENSORTS101817 | 26
B2.1 | Y |  |  |  | Tunnel to QAP-1B temperature sensor 1 | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | QAP01_RTU |  |  |  |  | 33 |  |  |  |  | &TS102057 | TUN_QAP01_NS01_SENSOR_TS102057 |  |  |  | YES | TUNQAP01NS01SENSORTS102057 | 26
B2.1 | Y |  |  |  | Tunnel to QAP-1B temperature sensor 2 | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | QAP01_RTU |  |  |  |  | 34 |  |  |  |  | &TS102121 | TUN_QAP01_NS01_SENSOR_TS102121 |  |  |  | YES | TUNQAP01NS01SENSORTS102121 | 26
B1.8 | Y |  |  |  |  | Air velocity sensor (VS)
B2.1 | Y |  |  |  | Tunnel to EC1-01 Air velocity sensor | TUN:QAP01 | SS01:SENSOR | VS | VS101763 | QAP01_RTU |  |  |  |  | 35 |  |  |  |  | &VS101763 | TUN_QAP01_SS01_SENSOR_VS101763 |  |  |  | YES | TUNQAP01SS01SENSORVS101763 | 26
B2.1 | Y |  |  |  | Tunnel to QAP-1B Air velocity sensor | TUN:QAP01 | NS01:SENSOR | VS | VS102092 | QAP01_RTU |  |  |  |  | 36 |  |  |  |  | &VS102092 | TUN_QAP01_NS01_SENSOR_VS102092 |  |  |  | YES | TUNQAP01NS01SENSORVS102092 | 26
B1.8 | Y |  |  |  |  | TVS Damper : Tunnel damper (TDP)
B2.1 | Y |  |  |  | South Shaft Tunnel damper 1 | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | QAP01_RTU |  |  |  |  | 37 |  |  |  |  | &VT5-TDP01 | TUN_QAP01_SS01_DAMPER_VT5-TDP01 |  |  |  | YES | TUNQAP01SS01DAMPERVT5-TDP01 | 27
B2.1 | Y |  |  |  | North Shaft Tunnel damper 2 | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | QAP01_RTU |  |  |  |  | 38 |  |  |  |  | &VT6-TDP01 | TUN_QAP01_NS01_DAMPER_VT6-TDP01 |  |  |  | YES | TUNQAP01NS01DAMPERVT6-TDP01 | 27
B1.8 | Y |  |  |  |  | TVS Damper : Isolation damper (IDP)
B2.1 | N |  |  |  | Isolation damper 1 | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | QAP01_RTU |  |  |  |  | 39 |  |  |  |  | &VT1-IDP01 | TUN_QAP01_SS01_DAMPER_VT1-IDP01 |  |  |  | YES | TUNQAP01SS01DAMPERVT1-IDP01 | 27
B2.1 | N |  |  |  | Isolation damper 2 | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | QAP01_RTU |  |  |  |  | 40 |  |  |  |  | &VT2-IDP01 | TUN_QAP01_SS01_DAMPER_VT2-IDP01 |  |  |  | YES | TUNQAP01SS01DAMPERVT2-IDP01 | 27
B2.1 | N |  |  |  | Isolation damper 3 | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | QAP01_RTU |  |  |  |  | 41 |  |  |  |  | &VT3-IDP01 | TUN_QAP01_NS01_DAMPER_VT3-IDP01 |  |  |  | YES | TUNQAP01NS01DAMPERVT3-IDP01 | 27
B2.1 | N |  |  |  | Isolation damper 4 | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | QAP01_RTU |  |  |  |  | 42 |  |  |  |  | &VT4-IDP01 | TUN_QAP01_NS01_DAMPER_VT4-IDP01 |  |  |  | YES | TUNQAP01NS01DAMPERVT4-IDP01 | 27
B1.8 | Y |  |  |  |  | TVS Damper : Bypass damper (BDP)
B2.1 | Y |  |  |  | South Shaft Bypass damper 1 | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | QAP01_RTU |  |  |  |  | 43 |  |  |  |  | &FR1-BDP01 | TUN_QAP01_SS01_DAMPER_FR1-BDP01 |  |  |  | YES | TUNQAP01SS01DAMPERFR1-BDP01 | 27
B2.1 | Y |  |  |  | North Shaft Bypass damper 2 | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | QAP01_RTU |  |  |  |  | 44 |  |  |  |  | &FR2-BDP01 | TUN_QAP01_NS01_DAMPER_FR2-BDP01 |  |  |  | YES | TUNQAP01NS01DAMPERFR2-BDP01 | 27
B1.8 | Y |  |  |  |  | MEP Damper : Tunnel Cooling damper (TCDP)
B2.1 | N |  |  |  | South Shaft Tunnel Cooling damper 1 | TUN:QAP01 | SS01:DAMPER | MSFD | CON-63 | QAP01_RTU |  |  |  |  | 45 |  |  |  |  | &CON-63 | TUN_QAP01_SS01_DAMPER_CON-63 |  |  |  | YES | TUNQAP01SS01DAMPERCON-63 | 24
B2.1 | N |  |  |  | North Shaft Tunnel Cooling damper 2 | TUN:QAP01 | NS01:DAMPER | MSFD | CON-54 | QAP01_RTU |  |  |  |  | 46 |  |  |  |  | &CON-54 | TUN_QAP01_NS01_DAMPER_CON-54 |  |  |  | YES | TUNQAP01NS01DAMPERCON-54 | 24
B1.8 | Y |  |  |  |  | MEP damper : Station to exhaust duct Damper (SEDD)
B2.1 | N |  |  |  | South Shaft Station to exhaust duct damper 1 | TUN:QAP01 | SS01:DAMPER | MSFD | CON-66 | QAP01_RTU |  |  |  |  | 47 |  |  |  |  | &CON-66 | TUN_QAP01_SS01_DAMPER_CON-66 |  |  |  | YES | TUNQAP01SS01DAMPERCON-66 | 24
B2.1 | N |  |  |  | South Shaft Station to exhaust duct damper 2 | TUN:QAP01 | SS01:DAMPER | MSFD | CON-61 | QAP01_RTU |  |  |  |  | 48 |  |  |  |  | &CON-61 | TUN_QAP01_SS01_DAMPER_CON-61 |  |  |  | YES | TUNQAP01SS01DAMPERCON-61 | 24
B2.1 | N |  |  |  | North Shaft Station to exhaust duct damper 3 | TUN:QAP01 | NS01:DAMPER | MSFD | CON-56 | QAP01_RTU |  |  |  |  | 49 |  |  |  |  | &CON-56 | TUN_QAP01_NS01_DAMPER_CON-56 |  |  |  | YES | TUNQAP01NS01DAMPERCON-56 | 24
B2.1 | N |  |  |  | North Shaft Station to exhaust duct damper 4 | TUN:QAP01 | NS01:DAMPER | MSFD | CON-51 | QAP01_RTU |  |  |  |  | 50 |  |  |  |  | &CON-51 | TUN_QAP01_NS01_DAMPER_CON-51 |  |  |  | YES | TUNQAP01NS01DAMPERCON-51 | 24
B1.8 | Y |  |  |  |  | MEP damper : Station Cooling damper (SCD)
B2.1 | N |  |  |  | South Shaft Station Cooling damper 1 | TUN:QAP01 | SS01:DAMPER | MSFD | CON-67 | QAP01_RTU |  |  |  |  | 51 |  |  |  |  | &CON-67 | TUN_QAP01_SS01_DAMPER_CON-67 |  |  |  | YES | TUNQAP01SS01DAMPERCON-67 | 24
B2.1 | N |  |  |  | South Shaft Station Cooling damper 2 | TUN:QAP01 | SS01:DAMPER | MSFD | CON-59 | QAP01_RTU |  |  |  |  | 52 |  |  |  |  | &CON-59 | TUN_QAP01_SS01_DAMPER_CON-59 |  |  |  | YES | TUNQAP01SS01DAMPERCON-59 | 24
B2.1 | N |  |  |  | North Shaft Station Cooling damper 3 | TUN:QAP01 | NS01:DAMPER | MSFD | CON-58 | QAP01_RTU |  |  |  |  | 53 |  |  |  |  | &CON-58 | TUN_QAP01_NS01_DAMPER_CON-58 |  |  |  | YES | TUNQAP01NS01DAMPERCON-58 | 24
B2.1 | N |  |  |  | North Shaft Station Cooling damper 4 | TUN:QAP01 | NS01:DAMPER | MSFD | CON-52 | QAP01_RTU |  |  |  |  | 54 |  |  |  |  | &CON-52 | TUN_QAP01_NS01_DAMPER_CON-52 |  |  |  | YES | TUNQAP01NS01DAMPERCON-52 | 24
B1.8 | Y |  |  |  |  | Tunnel AIR HANDLING UNIT
B2.1 | Y |  |  |  | South ShaftTunnel Air Handling Unit 1 (AHU room 3) | TUN:QAP01 | SS01:AHU | AHU | CON-08 | QAP01_RTU |  |  |  |  | 55 |  |  |  |  | &CON-08 | TUN_QAP01_SS01_AHU_CON-08 |  |  |  | YES | TUNQAP01SS01AHUCON-08 | 21
B2.1 | Y |  |  |  | South ShaftTunnel Air Handling Unit 2 (AHU room 2) | TUN:QAP01 | SS01:AHU | AHU | CON-07 | QAP01_RTU |  |  |  |  | 56 |  |  |  |  | &CON-07 | TUN_QAP01_SS01_AHU_CON-07 |  |  |  | YES | TUNQAP01SS01AHUCON-07 | 21
B2.1 | Y |  |  |  | North ShaftTunnel Air Handling Unit 1 (AHU room 4) | TUN:QAP01 | NS01:AHU | AHU | CON-06 | QAP01_RTU |  |  |  |  | 57 |  |  |  |  | &CON-06 | TUN_QAP01_NS01_AHU_CON-06 |  |  |  | YES | TUNQAP01NS01AHUCON-06 | 21
B2.1 | Y |  |  |  | North ShaftTunnel Air Handling Unit 2 (AHU room 1) | TUN:QAP01 | NS01:AHU | AHU | CON-05 | QAP01_RTU |  |  |  |  | 58 |  |  |  |  | &CON-05 | TUN_QAP01_NS01_AHU_CON-05 |  |  |  | YES | TUNQAP01NS01AHUCON-05 | 21
B1.8 | Y |  |  |  |  | MMS Equipment
B2.1 | N |  |  |  | Station PLC (MMS) | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | QAP01_RTU |  |  |  |  | 59 |  |  |  |  | &SPLC01 | TUN_QAP01_MMS_SPLC01 |  |  |  | YES | TUNQAP01MMSSPLC01 | 17
B1.8 | Y |  |  |  |  | Electrical Equipment
B2.1 | N |  |  |  | QAP01-LPS-MDB01 | TUN:QAP01 | MMS | MDB | LPS-MDB01 | QAP01_RTU |  |  |  |  | 60 |  |  |  |  | &LPS-MDB01 | TUN_QAP01_MMS_LPS-MDB01 |  |  |  | YES | TUNQAP01MMSLPS-MDB01 | 20
B2.1 | N |  |  |  | QAP01-LPS-MDB02 | TUN:QAP01 | MMS | MDB | LPS-MDB02 | QAP01_RTU |  |  |  |  | 61 |  |  |  |  | &LPS-MDB02 | TUN_QAP01_MMS_LPS-MDB02 |  |  |  | YES | TUNQAP01MMSLPS-MDB02 | 20
B1.8 | Y |  |  |  |  | Electrical Panel EL1 I/O 01
B2.1 | N |  |  |  | QAP01-EL1-IO01 | TUN:QAP01 | MMS | EL | EL1-IO01 | QAP01_RTU |  |  |  |  | 62 |  |  |  |  | &EL1-IO01 | TUN_QAP01_MMS_EL1-IO01 |  |  |  | YES | TUNQAP01MMSEL1-IO01 | 19
B2.1 | N |  |  |  | MCCB QAP01-EL1-UPS | TUN:QAP01 | MMS | MCCB | EL1-UPS | QAP01_RTU |  |  |  |  | 63 |  |  |  |  | &EL1-UPS | TUN_QAP01_MMS_EL1-UPS |  |  |  | YES | TUNQAP01MMSEL1-UPS | 18
B2.1 | N |  |  |  | LBS QAP01-EL1-UPS | TUN:QAP01 | MMS | LBS | EL1-UPS | QAP01_RTU |  |  |  |  | 64 |  |  |  |  | &EL1-UPS | TUN_QAP01_MMS_EL1-UPS |  |  |  | YES | TUNQAP01MMSEL1-UPS | 18
B2.1 | N |  |  |  | MCB UPS QAP01-EL1-VSD01 | TUN:QAP01 | MMS | MCB | UPS_EL1-VSD01 | QAP01_RTU |  |  |  |  | 65 |  |  |  |  | &UPS-EL1-VSD01 | TUN_QAP01_MMS_UPS_EL1-VSD01 |  |  |  | YES | TUNQAP01MMSUPS_EL1-VSD01 | 24
B2.1 | N |  |  |  | MCB UPS QAP01-EL1-VSD02 | TUN:QAP01 | MMS | MCB | UPS_EL1-VSD02 | QAP01_RTU |  |  |  |  | 66 |  |  |  |  | &UPS-EL1-VSD02 | TUN_QAP01_MMS_UPS_EL1-VSD02 |  |  |  | YES | TUNQAP01MMSUPS_EL1-VSD02 | 24
B2.1 | N |  |  |  | MCB 3P QAP01-VT3-IDP01 | TUN:QAP01 | MMS | MCB | 3P-VT3-IDP01 | QAP01_RTU |  |  |  |  | 67 |  |  |  |  | &3P-VT3-IDP01 | TUN_QAP01_MMS_3P-VT3-IDP01 |  |  |  | YES | TUNQAP01MMS3P-VT3-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P QAP01-VT3-IDP01 | TUN:QAP01 | MMS | MCB | 2P-VT3-IDP01 | QAP01_RTU |  |  |  |  | 68 |  |  |  |  | &2P-VT3-IDP01 | TUN_QAP01_MMS_2P-VT3-IDP01 |  |  |  | YES | TUNQAP01MMS2P-VT3-IDP01 | 23
B2.1 | N |  |  |  | MCB 3P QAP01-VT4-IDP01 | TUN:QAP01 | MMS | MCB | 3P-VT4-IDP01 | QAP01_RTU |  |  |  |  | 69 |  |  |  |  | &3P-VT4-IDP01 | TUN_QAP01_MMS_3P-VT4-IDP01 |  |  |  | YES | TUNQAP01MMS3P-VT4-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P QAP01-VT4-IDP01 | TUN:QAP01 | MMS | MCB | 2P-VT4-IDP01 | QAP01_RTU |  |  |  |  | 70 |  |  |  |  | &2P-VT4-IDP01 | TUN_QAP01_MMS_2P-VT4-IDP01 |  |  |  | YES | TUNQAP01MMS2P-VT4-IDP01 | 23
B2.1 | N |  |  |  | MCB 3P QAP01-VT6-TDP01-01 | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-01 | QAP01_RTU |  |  |  |  | 71 |  |  |  |  | &3P-VT6-TDP01-01 | TUN_QAP01_MMS_3P-VT6-TDP01-01 |  |  |  | YES | TUNQAP01MMS3P-VT6-TDP01-01 | 26
B2.1 | N |  |  |  | MCB 2P QAP01-VT6-TDP01-01 | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-01 | QAP01_RTU |  |  |  |  | 72 |  |  |  |  | &2P-VT6-TDP01-01 | TUN_QAP01_MMS_2P-VT6-TDP01-01 |  |  |  | YES | TUNQAP01MMS2P-VT6-TDP01-01 | 26
B2.1 | N |  |  |  | MCB 3P QAP01-VT6-TDP01-02 | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-02 | QAP01_RTU |  |  |  |  | 73 |  |  |  |  | &3P-VT6-TDP01-02 | TUN_QAP01_MMS_3P-VT6-TDP01-02 |  |  |  | YES | TUNQAP01MMS3P-VT6-TDP01-02 | 26
B2.1 | N |  |  |  | MCB 2P QAP01-VT6-TDP01-02 | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-02 | QAP01_RTU |  |  |  |  | 74 |  |  |  |  | &2P-VT6-TDP01-02 | TUN_QAP01_MMS_2P-VT6-TDP01-02 |  |  |  | YES | TUNQAP01MMS2P-VT6-TDP01-02 | 26
B2.1 | N |  |  |  | MCB 3P QAP01-VT6-TDP01-03 | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-03 | QAP01_RTU |  |  |  |  | 75 |  |  |  |  | &3P-VT6-TDP01-03 | TUN_QAP01_MMS_3P-VT6-TDP01-03 |  |  |  | YES | TUNQAP01MMS3P-VT6-TDP01-03 | 26
B2.1 | N |  |  |  | MCB 2P QAP01-VT6-TDP01-03 | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-03 | QAP01_RTU |  |  |  |  | 76 |  |  |  |  | &2P-VT6-TDP01-03 | TUN_QAP01_MMS_2P-VT6-TDP01-03 |  |  |  | YES | TUNQAP01MMS2P-VT6-TDP01-03 | 26
B2.1 | N |  |  |  | MCB 3P QAP01-FR2-BDP01-01 | TUN:QAP01 | MMS | MCB | 3P--FR2-BDP01-01 | QAP01_RTU |  |  |  |  | 77 |  |  |  |  | &3P--FR2-BDP01-01 | TUN_QAP01_MMS_3P--FR2-BDP01-01 |  |  |  | YES | TUNQAP01MMS3P--FR2-BDP01-01 | 27
B2.1 | N |  |  |  | MCB 2P QAP01-FR2-BDP01-01 | TUN:QAP01 | MMS | MCB | 2P--FR2-BDP01-01 | QAP01_RTU |  |  |  |  | 78 |  |  |  |  | &2P--FR2-BDP01-01 | TUN_QAP01_MMS_2P--FR2-BDP01-01 |  |  |  | YES | TUNQAP01MMS2P--FR2-BDP01-01 | 27
B2.1 | N |  |  |  | MCB 3P QAP01-FR2-BDP01-02 | TUN:QAP01 | MMS | MCB | 3P--FR2-BDP01-02 | QAP01_RTU |  |  |  |  | 79 |  |  |  |  | &3P--FR2-BDP01-02 | TUN_QAP01_MMS_3P--FR2-BDP01-02 |  |  |  | YES | TUNQAP01MMS3P--FR2-BDP01-02 | 27
B2.1 | N |  |  |  | MCB 2P QAP01-FR2-BDP01-02 | TUN:QAP01 | MMS | MCB | 2P--FR2-BDP01-02 | QAP01_RTU |  |  |  |  | 80 |  |  |  |  | &2P--FR2-BDP01-02 | TUN_QAP01_MMS_2P--FR2-BDP01-02 |  |  |  | YES | TUNQAP01MMS2P--FR2-BDP01-02 | 27
B2.1 | N |  |  |  | MCB QAP01-MSFD-CON-54 | TUN:QAP01 | MMS | MCB | MSFD-CON-54 | QAP01_RTU |  |  |  |  | 81 |  |  |  |  | &MSFD-CON-54 | TUN_QAP01_MMS_MSFD-CON-54 |  |  |  | YES | TUNQAP01MMSMSFD-CON-54 | 22
B2.1 | N |  |  |  | MCB QAP01-MSFD-CON-52 | TUN:QAP01 | MMS | MCB | MSFD-CON-52 | QAP01_RTU |  |  |  |  | 82 |  |  |  |  | &MSFD-CON-52 | TUN_QAP01_MMS_MSFD-CON-52 |  |  |  | YES | TUNQAP01MMSMSFD-CON-52 | 22
B2.1 | N |  |  |  | MCB QAP01-MSFD-CON-58 | TUN:QAP01 | MMS | MCB | MSFD-CON-58 | QAP01_RTU |  |  |  |  | 83 |  |  |  |  | &MSFD-CON-58 | TUN_QAP01_MMS_MSFD-CON-58 |  |  |  | YES | TUNQAP01MMSMSFD-CON-58 | 22
B1.8 | Y |  |  |  |  | Electrical Panel EL2 I/O 01
B2.1 | N |  |  |  | QAP01-EL2-IO01 | TUN:QAP01 | MMS | EL | EL2-IO01 | QAP01_RTU |  |  |  |  | 84 |  |  |  |  | &EL2-IO01 | TUN_QAP01_MMS_EL2-IO01 |  |  |  | YES | TUNQAP01MMSEL2-IO01 | 19
B2.1 | N |  |  |  | MCCB QAP01-EL2-UPS | TUN:QAP01 | MMS | MCCB | EL2-UPS | QAP01_RTU |  |  |  |  | 85 |  |  |  |  | &EL2-UPS | TUN_QAP01_MMS_EL2-UPS |  |  |  | YES | TUNQAP01MMSEL2-UPS | 18
B2.1 | N |  |  |  | LBS QAP01-EL2-UPS | TUN:QAP01 | MMS | LBS | EL2-UPS | QAP01_RTU |  |  |  |  | 86 |  |  |  |  | &EL2-UPS | TUN_QAP01_MMS_EL2-UPS |  |  |  | YES | TUNQAP01MMSEL2-UPS | 18
B2.1 | N |  |  |  | MCB UPS QAP01-EL2-VSD01 | TUN:QAP01 | MMS | MCB | UPS_EL2-VSD01 | QAP01_RTU |  |  |  |  | 87 |  |  |  |  | &UPS-EL2-VSD01 | TUN_QAP01_MMS_UPS_EL2-VSD01 |  |  |  | YES | TUNQAP01MMSUPS_EL2-VSD01 | 24
B2.1 | N |  |  |  | MCB UPS QAP01-EL2-VSD02 | TUN:QAP01 | MMS | MCB | UPS_EL2-VSD02 | QAP01_RTU |  |  |  |  | 88 |  |  |  |  | &UPS-EL2-VSD02 | TUN_QAP01_MMS_UPS_EL2-VSD02 |  |  |  | YES | TUNQAP01MMSUPS_EL2-VSD02 | 24
B2.1 | N |  |  |  | MCB 3P QAP01-VT1-IDP01 | TUN:QAP01 | MMS | MCB | 3P-VT1-IDP01 | QAP01_RTU |  |  |  |  | 89 |  |  |  |  | &3P-VT1-IDP01 | TUN_QAP01_MMS_3P-VT1-IDP01 |  |  |  | YES | TUNQAP01MMS3P-VT1-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P QAP01-VT1-IDP01 | TUN:QAP01 | MMS | MCB | 2P-VT1-IDP01 | QAP01_RTU |  |  |  |  | 90 |  |  |  |  | &2P-VT1-IDP01 | TUN_QAP01_MMS_2P-VT1-IDP01 |  |  |  | YES | TUNQAP01MMS2P-VT1-IDP01 | 23
B2.1 | N |  |  |  | MCB 3P QAP01-VT2-IDP01 | TUN:QAP01 | MMS | MCB | 3P-VT2-IDP01 | QAP01_RTU |  |  |  |  | 91 |  |  |  |  | &3P-VT2-IDP01 | TUN_QAP01_MMS_3P-VT2-IDP01 |  |  |  | YES | TUNQAP01MMS3P-VT2-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P QAP01-VT2-IDP01 | TUN:QAP01 | MMS | MCB | 2P-VT2-IDP01 | QAP01_RTU |  |  |  |  | 92 |  |  |  |  | &2P-VT2-IDP01 | TUN_QAP01_MMS_2P-VT2-IDP01 |  |  |  | YES | TUNQAP01MMS2P-VT2-IDP01 | 23
B2.1 | N |  |  |  | MCB 3P QAP01-VT5-TDP01-01 | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-01 | QAP01_RTU |  |  |  |  | 93 |  |  |  |  | &3P-VT5-TDP01-01 | TUN_QAP01_MMS_3P-VT5-TDP01-01 |  |  |  | YES | TUNQAP01MMS3P-VT5-TDP01-01 | 26
B2.1 | N |  |  |  | MCB 2P QAP01-VT5-TDP01-01 | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-01 | QAP01_RTU |  |  |  |  | 94 |  |  |  |  | &2P-VT5-TDP01-01 | TUN_QAP01_MMS_2P-VT5-TDP01-01 |  |  |  | YES | TUNQAP01MMS2P-VT5-TDP01-01 | 26
B2.1 | N |  |  |  | MCB 3P QAP01-VT5-TDP01-02 | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-02 | QAP01_RTU |  |  |  |  | 95 |  |  |  |  | &3P-VT5-TDP01-02 | TUN_QAP01_MMS_3P-VT5-TDP01-02 |  |  |  | YES | TUNQAP01MMS3P-VT5-TDP01-02 | 26
B2.1 | N |  |  |  | MCB 2P QAP01-VT5-TDP01-02 | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-02 | QAP01_RTU |  |  |  |  | 96 |  |  |  |  | &2P-VT5-TDP01-02 | TUN_QAP01_MMS_2P-VT5-TDP01-02 |  |  |  | YES | TUNQAP01MMS2P-VT5-TDP01-02 | 26
B2.1 | N |  |  |  | MCB 3P QAP01-VT5-TDP01-03 | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-03 | QAP01_RTU |  |  |  |  | 97 |  |  |  |  | &3P-VT5-TDP01-03 | TUN_QAP01_MMS_3P-VT5-TDP01-03 |  |  |  | YES | TUNQAP01MMS3P-VT5-TDP01-03 | 26
B2.1 | N |  |  |  | MCB 2P QAP01-VT5-TDP01-03 | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-03 | QAP01_RTU |  |  |  |  | 98 |  |  |  |  | &2P-VT5-TDP01-03 | TUN_QAP01_MMS_2P-VT5-TDP01-03 |  |  |  | YES | TUNQAP01MMS2P-VT5-TDP01-03 | 26
B2.1 | N |  |  |  | MCB 3P QAP01-FR1-BDP01-01 | TUN:QAP01 | MMS | MCB | 3P-FR1-BDP01-01 | QAP01_RTU |  |  |  |  | 99 |  |  |  |  | &3P-FR1-BDP01-01 | TUN_QAP01_MMS_3P-FR1-BDP01-01 |  |  |  | YES | TUNQAP01MMS3P-FR1-BDP01-01 | 26
B2.1 | N |  |  |  | MCB 2P QAP01-FR1-BDP01-01 | TUN:QAP01 | MMS | MCB | 2P-FR1-BDP01-01 | QAP01_RTU |  |  |  |  | 100 |  |  |  |  | &2P-FR1-BDP01-01 | TUN_QAP01_MMS_2P-FR1-BDP01-01 |  |  |  | YES | TUNQAP01MMS2P-FR1-BDP01-01 | 26
B2.1 | N |  |  |  | MCB 3P QAP01-FR1-BDP01-02 | TUN:QAP01 | MMS | MCB | 3P-FR1-BDP01-02 | QAP01_RTU |  |  |  |  | 101 |  |  |  |  | &3P-FR1-BDP01-02 | TUN_QAP01_MMS_3P-FR1-BDP01-02 |  |  |  | YES | TUNQAP01MMS3P-FR1-BDP01-02 | 26
B2.1 | N |  |  |  | MCB 2P QAP01-FR1-BDP01-02 | TUN:QAP01 | MMS | MCB | 2P-FR1-BDP01-02 | QAP01_RTU |  |  |  |  | 102 |  |  |  |  | &2P-FR1-BDP01-02 | TUN_QAP01_MMS_2P-FR1-BDP01-02 |  |  |  | YES | TUNQAP01MMS2P-FR1-BDP01-02 | 26
B2.1 | N |  |  |  | MCB QAP01-MSFD-CON-63 | TUN:QAP01 | MMS | MCB | MSFD-CON-63 | QAP01_RTU |  |  |  |  | 103 |  |  |  |  | &MSFD-CON-63 | TUN_QAP01_MMS_MSFD-CON-63 |  |  |  | YES | TUNQAP01MMSMSFD-CON-63 | 22
B2.1 | N |  |  |  | MCB QAP01-MSFD-CON-59 | TUN:QAP01 | MMS | MCB | MSFD-CON-59 | QAP01_RTU |  |  |  |  | 104 |  |  |  |  | &MSFD-CON-59 | TUN_QAP01_MMS_MSFD-CON-59 |  |  |  | YES | TUNQAP01MMSMSFD-CON-59 | 22
B2.1 | N |  |  |  | MCB QAP01-MSFD-CON-67 | TUN:QAP01 | MMS | MCB | MSFD-CON-67 | QAP01_RTU |  |  |  |  | 105 |  |  |  |  | &MSFD-CON-67 | TUN_QAP01_MMS_MSFD-CON-67 |  |  |  | YES | TUNQAP01MMSMSFD-CON-67 | 22
B1.8 | Y |  |  |  |  | QEC-01
B1.8 | Y |  |  |  |  | LOCAL CONTROL PANEL (LCP) [STATION HMI]
B2.1 | Y |  |  |  | Local control panel | TUN:QEC01 | SCR | LCP | LCP01 | QEC01_RTU |  |  |  |  | 1 |  |  |  |  | &LCP01 | TUN_QEC01_SCR_LCP01 |  |  |  | YES | TUNQEC01SCRLCP01 | 16
B1.8 | Y |  |  |  |  | FIRE MANUAL OVERRIDE PANEL (FMOP)
B2.1 | Y |  |  |  | Fire control panel | TUN:QEC01 | SCR | FMOP | FMOP01 | QEC01_RTU |  |  |  |  | 2 |  |  |  |  | &FMOP01 | TUN_QEC01_SCR_FMOP01 |  |  |  | YES | TUNQEC01SCRFMOP01 | 17
B1.8 | Y |  |  |  |  | Station PLC (SPLC)
B2.1 | Y |  |  |  | Station PLC | TUN:QEC01 | TEL | SPLC | PLC01 | QEC01_RTU |  |  |  |  | 3 |  |  |  |  | &PLC01 | TUN_QEC01_TEL_PLC01 |  |  |  | YES | TUNQEC01TELPLC01 | 16
B1.8 | Y |  |  |  |  | Switch (SWI)
B2.1 | Y |  |  |  | Switch | TUN:QEC01 | TEL | SWI | SWI01 | QEC01_RTU |  |  |  |  | 4 |  |  |  |  | &SWI01 | TUN_QEC01_TEL_SWI01 |  |  |  | YES | TUNQEC01TELSWI01 | 16
B1.8 | Y |  |  |  |  | PRESSURIZATION FAN (PFA)
B2.1 | Y |  |  |  | Pressurization fan Lobby 1 | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | QEC01_RTU |  |  |  |  | 5 |  |  |  |  | &PLA-01 | TUN_QEC01_SS01_PFA_PLA-01 |  |  |  | YES | TUNQEC01SS01PFAPLA-01 | 21
B2.1 | Y |  |  |  | Pressurization fan Escape Stair 1 | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | QEC01_RTU |  |  |  |  | 6 |  |  |  |  | &GRD-01 | TUN_QEC01_SS01_PFA_GRD-01 |  |  |  | YES | TUNQEC01SS01PFAGRD-01 | 21
B2.1 | Y |  |  |  | Pressurization fan Lobby 2 | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | QEC01_RTU |  |  |  |  | 7 |  |  |  |  | &PLA-02 | TUN_QEC01_NS01_PFA_PLA-02 |  |  |  | YES | TUNQEC01NS01PFAPLA-02 | 21
B2.1 | Y |  |  |  | Pressurization fan Stair 4 | TUN:QEC01 | NS01:PFA | PFA | CON-04 | QEC01_RTU |  |  |  |  | 8 |  |  |  |  | &CON-04 | TUN_QEC01_NS01_PFA_CON-04 |  |  |  | YES | TUNQEC01NS01PFACON-04 | 21
B2.1 | Y |  |  |  | Pressurization fan Lobby 3 & Corridor 4 | TUN:QEC01 | NS01:PFA | PFA | CON-03 | QEC01_RTU |  |  |  |  | 9 |  |  |  |  | &CON-03 | TUN_QEC01_NS01_PFA_CON-03 |  |  |  | YES | TUNQEC01NS01PFACON-03 | 21
B2.1 | Y |  |  |  | Pressurization fan Escape Stair 3 | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | QEC01_RTU |  |  |  |  | 10 |  |  |  |  | &GRD-03 | TUN_QEC01_NS01_PFA_GRD-03 |  |  |  | YES | TUNQEC01NS01PFAGRD-03 | 21
B1.8 | Y |  |  |  |  | SMOKE CURTAINS (SMC)
B2.1 | Y |  |  |  | Smoke Curtains 1 | TUN:QEC01 | SMC | SMC | SMC01 | QEC01_RTU |  |  |  |  | 11 |  |  |  |  | &SMC01 | TUN_QEC01_SMC_SMC01 |  |  |  | YES | TUNQEC01SMCSMC01 | 16
B2.1 | Y |  |  |  | Smoke Curtains 2 | TUN:QEC01 | SMC | SMC | SMC02 | QEC01_RTU |  |  |  |  | 12 |  |  |  |  | &SMC02 | TUN_QEC01_SMC_SMC02 |  |  |  | YES | TUNQEC01SMCSMC02 | 16
B2.1 | Y |  |  |  | Smoke Curtains 3 | TUN:QEC01 | SMC | SMC | SMC03 | QEC01_RTU |  |  |  |  | 13 |  |  |  |  | &SMC03 | TUN_QEC01_SMC_SMC03 |  |  |  | YES | TUNQEC01SMCSMC03 | 16
B2.1 | Y |  |  |  | Smoke Curtains 4 | TUN:QEC01 | SMC | SMC | SMC04 | QEC01_RTU |  |  |  |  | 14 |  |  |  |  | &SMC04 | TUN_QEC01_SMC_SMC04 |  |  |  | YES | TUNQEC01SMCSMC04 | 16
B2.1 | Y |  |  |  | Smoke Curtains 5 | TUN:QEC01 | SMC | SMC | SMC05 | QEC01_RTU |  |  |  |  | 15 |  |  |  |  | &SMC05 | TUN_QEC01_SMC_SMC05 |  |  |  | YES | TUNQEC01SMCSMC05 | 16
B2.1 | Y |  |  |  | Smoke Curtains 6 | TUN:QEC01 | SMC | SMC | SMC06 | QEC01_RTU |  |  |  |  | 16 |  |  |  |  | &SMC06 | TUN_QEC01_SMC_SMC06 |  |  |  | YES | TUNQEC01SMCSMC06 | 16
B2.1 | Y |  |  |  | Smoke Curtains 7 | TUN:QEC01 | SMC | SMC | SMC07 | QEC01_RTU |  |  |  |  | 17 |  |  |  |  | &SMC07 | TUN_QEC01_SMC_SMC07 |  |  |  | YES | TUNQEC01SMCSMC07 | 16
B2.1 | Y |  |  |  | Smoke Curtains 8 | TUN:QEC01 | SMC | SMC | SMC08 | QEC01_RTU |  |  |  |  | 18 |  |  |  |  | &SMC08 | TUN_QEC01_SMC_SMC08 |  |  |  | YES | TUNQEC01SMCSMC08 | 16
B2.1 | Y |  |  |  | Smoke Curtains 9 | TUN:QEC01 | SMC | SMC | SMC09 | QEC01_RTU |  |  |  |  | 19 |  |  |  |  | &SMC09 | TUN_QEC01_SMC_SMC09 |  |  |  | YES | TUNQEC01SMCSMC09 | 16
B2.1 | Y |  |  |  | Smoke Curtains 10 | TUN:QEC01 | SMC | SMC | SMC10 | QEC01_RTU |  |  |  |  | 20 |  |  |  |  | &SMC10 | TUN_QEC01_SMC_SMC10 |  |  |  | YES | TUNQEC01SMCSMC10 | 16
B1.8 | Y |  |  |  |  | STATION ENTRANCE DOOR (SED)
B2.1 | Y |  |  |  | Station entrance door 1 | TUN:QEC01 | SED | SED | SED01 | QEC01_RTU |  |  |  |  | 21 |  |  |  |  | &SED01 | TUN_QEC01_SED_SED01 |  |  |  | YES | TUNQEC01SEDSED01 | 16
B2.1 | Y |  |  |  | Station entrance door 2 | TUN:QEC01 | SED | SED | SED02 | QEC01_RTU |  |  |  |  | 22 |  |  |  |  | &SED02 | TUN_QEC01_SED_SED02 |  |  |  | YES | TUNQEC01SEDSED02 | 16
B2.1 | Y |  |  |  | Station entrance door 3 | TUN:QEC01 | SED | SED | SED03 | QEC01_RTU |  |  |  |  | 23 |  |  |  |  | &SED03 | TUN_QEC01_SED_SED03 |  |  |  | YES | TUNQEC01SEDSED03 | 16
B2.1 | Y |  |  |  | Station entrance door 4 | TUN:QEC01 | SED | SED | SED04 | QEC01_RTU |  |  |  |  | 24 |  |  |  |  | &SED04 | TUN_QEC01_SED_SED04 |  |  |  | YES | TUNQEC01SEDSED04 | 16
B1.8 | Y |  |  |  |  | Outdoor temperature sensor (OTS)
B2.1 | Y |  |  |  | Outdoor temperature sensor 1 | TUN:QEC01 | OTS | OTS | OTS001 | QEC01_RTU |  |  |  |  | 25 |  |  |  |  | &OTS001 | TUN_QEC01_OTS_OTS001 |  |  |  | YES | TUNQEC01OTSOTS001 | 17
B2.1 | Y |  |  |  | Outdoor temperature sensor 2 | TUN:QEC01 | OTS | OTS | OTS002 | QEC01_RTU |  |  |  |  | 26 |  |  |  |  | &OTS002 | TUN_QEC01_OTS_OTS002 |  |  |  | YES | TUNQEC01OTSOTS002 | 17
B1.8 | Y |  |  |  |  | Tunnel ventilation fan (TVF)
B2.1 | Y |  |  |  | South ShaftTunnel ventilation fan 1 | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | QEC01_RTU |  |  |  |  | 27 |  |  |  |  | &VT1-TVF01 | TUN_QEC01_SS01_TVF_VT1-TVF01 |  |  |  | YES | TUNQEC01SS01TVFVT1-TVF01 | 24
B2.1 | Y |  |  |  | South ShaftTunnel ventilation fan 2 | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | QEC01_RTU |  |  |  |  | 28 |  |  |  |  | &VT2-TVF01 | TUN_QEC01_SS01_TVF_VT2-TVF01 |  |  |  | YES | TUNQEC01SS01TVFVT2-TVF01 | 24
B2.1 | Y |  |  |  | North ShaftTunnel ventilation fan 3 | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | QEC01_RTU |  |  |  |  | 29 |  |  |  |  | &VT3-TVF01 | TUN_QEC01_NS01_TVF_VT3-TVF01 |  |  |  | YES | TUNQEC01NS01TVFVT3-TVF01 | 24
B2.1 | Y |  |  |  | NorthShaftTunnel ventilation fan 4 | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | QEC01_RTU |  |  |  |  | 30 |  |  |  |  | &VT4-TVF01 | TUN_QEC01_NS01_TVF_VT4-TVF01 |  |  |  | YES | TUNQEC01NS01TVFVT4-TVF01 | 24
B1.8 | Y |  |  |  |  | Tunnel temperature & humidity sensor (TTS)
B2.1 | Y |  |  |  | Tunnel to MAR-04 temperature sensor 1 | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | QEC01_RTU |  |  |  |  | 31 |  |  |  |  | &TS101871 | TUN_QEC01_SS01_SENSOR_TS101871 |  |  |  | YES | TUNQEC01SS01SENSORTS101871 | 26
B2.1 | Y |  |  |  | Tunnel to MAR-04 temperature sensor 2 | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | QEC01_RTU |  |  |  |  | 32 |  |  |  |  | &TS101984 | TUN_QEC01_SS01_SENSOR_TS101984 |  |  |  | YES | TUNQEC01SS01SENSORTS101984 | 26
B2.1 | Y |  |  |  | Tunnel to QEC-1A Niche temperature sensor 1 | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | QEC01_RTU |  |  |  |  | 33 |  |  |  |  | &TS102441 | TUN_QEC01_NS01_SENSOR_TS102441 |  |  |  | YES | TUNQEC01NS01SENSORTS102441 | 26
B2.1 | Y |  |  |  | Tunnel to QEC-1A Niche temperature sensor 2 | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | QEC01_RTU |  |  |  |  | 34 |  |  |  |  | &TS102499 | TUN_QEC01_NS01_SENSOR_TS102499 |  |  |  | YES | TUNQEC01NS01SENSORTS102499 | 26
B2.1 | Y |  |  |  | Tunnel to QEC-1B Niche temperature sensor 1 | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | QEC01_RTU |  |  |  |  | 35 |  |  |  |  | &TS102261 | TUN_QEC01_NS01_SENSOR_TS102261 |  |  |  | YES | TUNQEC01NS01SENSORTS102261 | 26
B2.1 | Y |  |  |  | Tunnel to QEC-1B Niche temperature sensor 2 | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | QEC01_RTU |  |  |  |  | 36 |  |  |  |  | &TS100023 | TUN_QEC01_NS01_SENSOR_TS100023 |  |  |  | YES | TUNQEC01NS01SENSORTS100023 | 26
B2.1 | Y |  |  |  | Tunnel to QEC-1B Niche temperature sensor 3 | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | QEC01_RTU |  |  |  |  | 37 |  |  |  |  | &TS100062 | TUN_QEC01_NS01_SENSOR_TS100062 |  |  |  | YES | TUNQEC01NS01SENSORTS100062 | 26
B2.1 | Y |  |  |  | Tunnel to QEC-1B Niche temperature sensor 4 | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | QEC01_RTU |  |  |  |  | 38 |  |  |  |  | &TS100108 | TUN_QEC01_NS01_SENSOR_TS100108 |  |  |  | YES | TUNQEC01NS01SENSORTS100108 | 26
B2.1 | Y |  |  |  | Tunnel to QEC-1B Niche temperature sensor 5 | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | QEC01_RTU |  |  |  |  | 39 |  |  |  |  | &TS100230 | TUN_QEC01_NS01_SENSOR_TS100230 |  |  |  | YES | TUNQEC01NS01SENSORTS100230 | 26
B2.1 | Y |  |  |  | Tunnel to QEC-1B Niche temperature sensor 6 | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | QEC01_RTU |  |  |  |  | 40 |  |  |  |  | &TS100335 | TUN_QEC01_NS01_SENSOR_TS100335 |  |  |  | YES | TUNQEC01NS01SENSORTS100335 | 26
B1.8 | Y |  |  |  |  | Air velocity sensor (VS)
B2.1 | Y |  |  |  | Tunnel to MAR-04 Air velocity sensor | TUN:QEC01 | SS01:SENSOR | VS | VS101909 | QEC01_RTU |  |  |  |  | 41 |  |  |  |  | &VS101909 | TUN_QEC01_SS01_SENSOR_VS101909 |  |  |  | YES | TUNQEC01SS01SENSORVS101909 | 26
B2.1 | Y |  |  |  | Tunnel to QEC-1A Niche Air velocity sensor 1 | TUN:QEC01 | NS01:SENSOR | VS | VS102357 | QEC01_RTU |  |  |  |  | 42 |  |  |  |  | &VS102357 | TUN_QEC01_NS01_SENSOR_VS102357 |  |  |  | YES | TUNQEC01NS01SENSORVS102357 | 26
B2.1 | Y |  |  |  | Tunnel to QEC-1A Niche Air velocity sensor 2 | TUN:QEC01 | NS01:SENSOR | VS | VS102467 | QEC01_RTU |  |  |  |  | 43 |  |  |  |  | &VS102467 | TUN_QEC01_NS01_SENSOR_VS102467 |  |  |  | YES | TUNQEC01NS01SENSORVS102467 | 26
B2.1 | Y |  |  |  | Tunnel to QEC-1B Niche Air velocity sensor 1 | TUN:QEC01 | NS01:SENSOR | VS | VS102276 | QEC01_RTU |  |  |  |  | 44 |  |  |  |  | &VS102276 | TUN_QEC01_NS01_SENSOR_VS102276 |  |  |  | YES | TUNQEC01NS01SENSORVS102276 | 26
B2.1 | Y |  |  |  | Tunnel to QEC-1B Niche Air velocity sensor 2 | TUN:QEC01 | NS01:SENSOR | VS | VS100080 | QEC01_RTU |  |  |  |  | 45 |  |  |  |  | &VS100080 | TUN_QEC01_NS01_SENSOR_VS100080 |  |  |  | YES | TUNQEC01NS01SENSORVS100080 | 26
B2.1 | Y |  |  |  | Tunnel to QEC-1B Niche Air velocity sensor 3 | TUN:QEC01 | NS01:SENSOR | VS | VS100285 | QEC01_RTU |  |  |  |  | 46 |  |  |  |  | &VS100285 | TUN_QEC01_NS01_SENSOR_VS100285 |  |  |  | YES | TUNQEC01NS01SENSORVS100285 | 26
B1.8 | Y |  |  |  |  | TVS Damper : Tunnel damper (TDP)
B2.1 | Y |  |  |  | South Shaft Tunnel damper 1 | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | QEC01_RTU |  |  |  |  | 47 |  |  |  |  | &VT5-TDP01 | TUN_QEC01_SS01_DAMPER_VT5-TDP01 |  |  |  | YES | TUNQEC01SS01DAMPERVT5-TDP01 | 27
B2.1 | Y |  |  |  | North Shaft Tunnel damper 2 | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | QEC01_RTU |  |  |  |  | 48 |  |  |  |  | &VT6-TDP01 | TUN_QEC01_NS01_DAMPER_VT6-TDP01 |  |  |  | YES | TUNQEC01NS01DAMPERVT6-TDP01 | 27
B1.8 | Y |  |  |  |  | TVS Damper : Isolation damper (IDP)
B2.1 | N |  |  |  | Isolation damper 1 | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | QEC01_RTU |  |  |  |  | 49 |  |  |  |  | &VT1-IDP01 | TUN_QEC01_SS01_DAMPER_VT1-IDP01 |  |  |  | YES | TUNQEC01SS01DAMPERVT1-IDP01 | 27
B2.1 | N |  |  |  | Isolation damper 2 | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | QEC01_RTU |  |  |  |  | 50 |  |  |  |  | &VT2-IDP01 | TUN_QEC01_SS01_DAMPER_VT2-IDP01 |  |  |  | YES | TUNQEC01SS01DAMPERVT2-IDP01 | 27
B2.1 | N |  |  |  | Isolation damper 3 | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | QEC01_RTU |  |  |  |  | 51 |  |  |  |  | &VT3-IDP01 | TUN_QEC01_NS01_DAMPER_VT3-IDP01 |  |  |  | YES | TUNQEC01NS01DAMPERVT3-IDP01 | 27
B2.1 | N |  |  |  | Isolation damper 4 | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | QEC01_RTU |  |  |  |  | 52 |  |  |  |  | &VT4-IDP01 | TUN_QEC01_NS01_DAMPER_VT4-IDP01 |  |  |  | YES | TUNQEC01NS01DAMPERVT4-IDP01 | 27
B1.8 | Y |  |  |  |  | TVS Damper : Bypass damper (BDP)
B2.1 | Y |  |  |  | South Shaft Bypass damper 1 | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | QEC01_RTU |  |  |  |  | 53 |  |  |  |  | &FR1-BDP01 | TUN_QEC01_SS01_DAMPER_FR1-BDP01 |  |  |  | YES | TUNQEC01SS01DAMPERFR1-BDP01 | 27
B2.1 | Y |  |  |  | North Shaft Bypass damper 2 | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | QEC01_RTU |  |  |  |  | 54 |  |  |  |  | &FR2-BDP01 | TUN_QEC01_NS01_DAMPER_FR2-BDP01 |  |  |  | YES | TUNQEC01NS01DAMPERFR2-BDP01 | 27
B1.8 | Y |  |  |  |  | MEP Damper : Tunnel Cooling damper (TCDP)
B2.1 | N |  |  |  | South Shaft Tunnel Cooling damper 1 | TUN:QEC01 | SS01:DAMPER | MSFD | CON-95 | QEC01_RTU |  |  |  |  | 55 |  |  |  |  | &CON-95 | TUN_QEC01_SS01_DAMPER_CON-95 |  |  |  | YES | TUNQEC01SS01DAMPERCON-95 | 24
B2.1 | N |  |  |  | North Shaft Tunnel Cooling damper 2 | TUN:QEC01 | NS01:DAMPER | MSFD | CON-94 | QEC01_RTU |  |  |  |  | 56 |  |  |  |  | &CON-94 | TUN_QEC01_NS01_DAMPER_CON-94 |  |  |  | YES | TUNQEC01NS01DAMPERCON-94 | 24
B1.8 | Y |  |  |  |  | MEP damper : Station to exhaust duct Damper (SEDD)
B2.1 | N |  |  |  | South Shaft Station to exhaust duct damper 1 | TUN:QEC01 | SS01:DAMPER | MSFD | CON-51 | QEC01_RTU |  |  |  |  | 57 |  |  |  |  | &CON-51 | TUN_QEC01_SS01_DAMPER_CON-51 |  |  |  | YES | TUNQEC01SS01DAMPERCON-51 | 24
B2.1 | N |  |  |  | South Shaft Station to exhaust duct damper 2 | TUN:QEC01 | SS01:DAMPER | MSFD | CON-49 | QEC01_RTU |  |  |  |  | 58 |  |  |  |  | &CON-49 | TUN_QEC01_SS01_DAMPER_CON-49 |  |  |  | YES | TUNQEC01SS01DAMPERCON-49 | 24
B2.1 | N |  |  |  | North Shaft Station to exhaust duct damper 3 | TUN:QEC01 | NS01:DAMPER | MSFD | CON-34 | QEC01_RTU |  |  |  |  | 59 |  |  |  |  | &CON-34 | TUN_QEC01_NS01_DAMPER_CON-34 |  |  |  | YES | TUNQEC01NS01DAMPERCON-34 | 24
B2.1 | N |  |  |  | North Shaft Station to exhaust duct damper 4 | TUN:QEC01 | NS01:DAMPER | MSFD | CON-53 | QEC01_RTU |  |  |  |  | 60 |  |  |  |  | &CON-53 | TUN_QEC01_NS01_DAMPER_CON-53 |  |  |  | YES | TUNQEC01NS01DAMPERCON-53 | 24
B1.8 | Y |  |  |  |  | MEP damper : Station Cooling damper (SCD)
B2.1 | N |  |  |  | South Shaft Station Cooling damper 1 | TUN:QEC01 | SS01:DAMPER | MSFD | CON-52 | QEC01_RTU |  |  |  |  | 61 |  |  |  |  | &CON-52 | TUN_QEC01_SS01_DAMPER_CON-52 |  |  |  | YES | TUNQEC01SS01DAMPERCON-52 | 24
B2.1 | N |  |  |  | South Shaft Station Cooling damper 2 | TUN:QEC01 | SS01:DAMPER | MSFD | CON-50 | QEC01_RTU |  |  |  |  | 62 |  |  |  |  | &CON-50 | TUN_QEC01_SS01_DAMPER_CON-50 |  |  |  | YES | TUNQEC01SS01DAMPERCON-50 | 24
B2.1 | N |  |  |  | North Shaft Station Cooling damper 3 | TUN:QEC01 | NS01:DAMPER | MSFD | CON-88 | QEC01_RTU |  |  |  |  | 63 |  |  |  |  | &CON-88 | TUN_QEC01_NS01_DAMPER_CON-88 |  |  |  | YES | TUNQEC01NS01DAMPERCON-88 | 24
B2.1 | N |  |  |  | North Shaft Station Cooling damper 4 | TUN:QEC01 | NS01:DAMPER | MSFD | CON-58 | QEC01_RTU |  |  |  |  | 64 |  |  |  |  | &CON-58 | TUN_QEC01_NS01_DAMPER_CON-58 |  |  |  | YES | TUNQEC01NS01DAMPERCON-58 | 24
B1.8 | Y |  |  |  |  | Tunnel AIR HANDLING UNIT
B2.1 | Y |  |  |  | South ShaftTunnel Air Handling Unit 1 (AHU room 3) | TUN:QEC01 | SS01:AHU | AHU | CON-02 | QEC01_RTU |  |  |  |  | 65 |  |  |  |  | &CON-02 | TUN_QEC01_SS01_AHU_CON-02 |  |  |  | YES | TUNQEC01SS01AHUCON-02 | 21
B2.1 | Y |  |  |  | North ShaftTunnel Air Handling Unit 2 (AHU room 1) | TUN:QEC01 | NS01:AHU | AHU | PLA-02 | QEC01_RTU |  |  |  |  | 66 |  |  |  |  | &PLA-02 | TUN_QEC01_NS01_AHU_PLA-02 |  |  |  | YES | TUNQEC01NS01AHUPLA-02 | 21
B1.8 | Y |  |  |  |  | JET FANS equipment
B2.1 | Y |  |  |  | QEC01 Jet Fans PLC | TUN:QEC01 | SCR | SPLC | JETPLC01 | QEC01_RTU |  |  |  |  | 67 |  |  |  |  | &JETPLC01 | TUN_QEC01_SCR_JETPLC01 |  |  |  | YES | TUNQEC01SCRJETPLC01 | 19
B1.8 | Y |  |  |  |  | Jet Fan Niche QEC-1A
B2.1 | Y |  |  |  | Jet Fan 100132 in tunnel between QEC-01 and EC1-0A (QEC-1B) | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | QEC01_RTU |  |  |  |  | 68 |  |  |  |  | &QEC1B-JET100132 | TUN_QEC01_QEC1B_JET_QEC1B-JET100132 |  |  |  | YES | TUNQEC01QEC1BJETQEC1B-JET100132 | 31
B2.1 | Y |  |  |  | Jet Fan 100133 in tunnel between QEC-01 and EC1-0A (QEC-1B) | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | QEC01_RTU |  |  |  |  | 69 |  |  |  |  | &QEC1B-JET100133 | TUN_QEC01_QEC1B_JET_QEC1B-JET100133 |  |  |  | YES | TUNQEC01QEC1BJETQEC1B-JET100133 | 31
B2.1 | Y |  |  |  | Jet Fan 100134 in tunnel between QEC-01 and EC1-0A (QEC-1B) | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | QEC01_RTU |  |  |  |  | 70 |  |  |  |  | &QEC1B-JET100134 | TUN_QEC01_QEC1B_JET_QEC1B-JET100134 |  |  |  | YES | TUNQEC01QEC1BJETQEC1B-JET100134 | 31
B1.8 | Y |  |  |  |  | Jet Fan Niche QEC-1B
B2.1 | Y |  |  |  | Jet Fan 102392 in tunnel between QEC-01 and QEC-02 (QEC-1A) | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | QEC01_RTU |  |  |  |  | 71 |  |  |  |  | &QEC1A-JET102392 | TUN_QEC01_QEC1A_JET_QEC1A-JET102392 |  |  |  | YES | TUNQEC01QEC1AJETQEC1A-JET102392 | 31
B2.1 | Y |  |  |  | Jet Fan 102393 in tunnel between QEC-01 and QEC-02 (QEC-1A) | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | QEC01_RTU |  |  |  |  | 72 |  |  |  |  | &QEC1A-JET102393 | TUN_QEC01_QEC1A_JET_QEC1A-JET102393 |  |  |  | YES | TUNQEC01QEC1AJETQEC1A-JET102393 | 31
B2.1 | Y |  |  |  | Jet Fan 102394 in tunnel between QEC-01 and QEC-02 (QEC-1A) | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | QEC01_RTU |  |  |  |  | 73 |  |  |  |  | &QEC1A-JET102394 | TUN_QEC01_QEC1A_JET_QEC1A-JET102394 |  |  |  | YES | TUNQEC01QEC1AJETQEC1A-JET102394 | 31
B1.8 | Y |  |  |  |  | MMS Equipment
B2.1 | N |  |  |  | Station PLC (MMS) | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | QEC01_RTU |  |  |  |  | 74 |  |  |  |  | &SPLC01 | TUN_QEC01_MMS_SPLC01 |  |  |  | YES | TUNQEC01MMSSPLC01 | 17
B1.8 | Y |  |  |  |  | Electrical Equipment
B2.1 | N |  |  |  | QEC01-LPS-MDB01 | TUN:QEC01 | MMS | MDB | LPS-MDB01 | QEC01_RTU |  |  |  |  | 75 |  |  |  |  | &LPS-MDB01 | TUN_QEC01_MMS_LPS-MDB01 |  |  |  | YES | TUNQEC01MMSLPS-MDB01 | 20
B2.1 | N |  |  |  | QEC01-LPS-MDB02 | TUN:QEC01 | MMS | MDB | LPS-MDB02 | QEC01_RTU |  |  |  |  | 76 |  |  |  |  | &LPS-MDB02 | TUN_QEC01_MMS_LPS-MDB02 |  |  |  | YES | TUNQEC01MMSLPS-MDB02 | 20
B1.8 | Y |  |  |  |  | Electrical Panel EL1 I/O 01
B2.1 | N |  |  |  | QEC01-EL1-IO01 | TUN:QEC01 | MMS | EL | EL1-IO01 | QEC01_RTU |  |  |  |  | 77 |  |  |  |  | &EL1-IO01 | TUN_QEC01_MMS_EL1-IO01 |  |  |  | YES | TUNQEC01MMSEL1-IO01 | 19
B2.1 | N |  |  |  | MCCB QEC01-EL1-UPS | TUN:QEC01 | MMS | MCCB | EL1-UPS | QEC01_RTU |  |  |  |  | 78 |  |  |  |  | &EL1-UPS | TUN_QEC01_MMS_EL1-UPS |  |  |  | YES | TUNQEC01MMSEL1-UPS | 18
B2.1 | N |  |  |  | LBS QEC01-EL1-UPS | TUN:QEC01 | MMS | LBS | EL1-UPS | QEC01_RTU |  |  |  |  | 79 |  |  |  |  | &EL1-UPS | TUN_QEC01_MMS_EL1-UPS |  |  |  | YES | TUNQEC01MMSEL1-UPS | 18
B2.1 | N |  |  |  | MCB UPS QEC01-EL1-VSD01 | TUN:QEC01 | MMS | MCB | UPS_EL1-VSD01 | QEC01_RTU |  |  |  |  | 80 |  |  |  |  | &UPS-EL1-VSD01 | TUN_QEC01_MMS_UPS_EL1-VSD01 |  |  |  | YES | TUNQEC01MMSUPS_EL1-VSD01 | 24
B2.1 | N |  |  |  | MCB UPS QEC01-EL1-VSD02 | TUN:QEC01 | MMS | MCB | UPS_EL1-VSD02 | QEC01_RTU |  |  |  |  | 81 |  |  |  |  | &UPS-EL1-VSD02 | TUN_QEC01_MMS_UPS_EL1-VSD02 |  |  |  | YES | TUNQEC01MMSUPS_EL1-VSD02 | 24
B2.1 | N |  |  |  | MCB 3P QEC01-VT3-IDP01 | TUN:QEC01 | MMS | MCB | 3P-VT3-IDP01 | QEC01_RTU |  |  |  |  | 82 |  |  |  |  | &3P-VT3-IDP01 | TUN_QEC01_MMS_3P-VT3-IDP01 |  |  |  | YES | TUNQEC01MMS3P-VT3-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P QEC01-VT3-IDP01 | TUN:QEC01 | MMS | MCB | 2P-VT3-IDP01 | QEC01_RTU |  |  |  |  | 83 |  |  |  |  | &2P-VT3-IDP01 | TUN_QEC01_MMS_2P-VT3-IDP01 |  |  |  | YES | TUNQEC01MMS2P-VT3-IDP01 | 23
B2.1 | N |  |  |  | MCB 3P QEC01-VT4-IDP01 | TUN:QEC01 | MMS | MCB | 3P-VT4-IDP01 | QEC01_RTU |  |  |  |  | 84 |  |  |  |  | &3P-VT4-IDP01 | TUN_QEC01_MMS_3P-VT4-IDP01 |  |  |  | YES | TUNQEC01MMS3P-VT4-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P QEC01-VT4-IDP01 | TUN:QEC01 | MMS | MCB | 2P-VT4-IDP01 | QEC01_RTU |  |  |  |  | 85 |  |  |  |  | &2P-VT4-IDP01 | TUN_QEC01_MMS_2P-VT4-IDP01 |  |  |  | YES | TUNQEC01MMS2P-VT4-IDP01 | 23
B2.1 | N |  |  |  | MCB 3P QEC01-VT6-TDP01-01 | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-01 | QEC01_RTU |  |  |  |  | 86 |  |  |  |  | &3P-VT6-TDP01-01 | TUN_QEC01_MMS_3P-VT6-TDP01-01 |  |  |  | YES | TUNQEC01MMS3P-VT6-TDP01-01 | 26
B2.1 | N |  |  |  | MCB 2P QEC01-VT6-TDP01-01 | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-01 | QEC01_RTU |  |  |  |  | 87 |  |  |  |  | &2P-VT6-TDP01-01 | TUN_QEC01_MMS_2P-VT6-TDP01-01 |  |  |  | YES | TUNQEC01MMS2P-VT6-TDP01-01 | 26
B2.1 | N |  |  |  | MCB 3P QEC01-VT6-TDP01-02 | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-02 | QEC01_RTU |  |  |  |  | 88 |  |  |  |  | &3P-VT6-TDP01-02 | TUN_QEC01_MMS_3P-VT6-TDP01-02 |  |  |  | YES | TUNQEC01MMS3P-VT6-TDP01-02 | 26
B2.1 | N |  |  |  | MCB 2P QEC01-VT6-TDP01-02 | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-02 | QEC01_RTU |  |  |  |  | 89 |  |  |  |  | &2P-VT6-TDP01-02 | TUN_QEC01_MMS_2P-VT6-TDP01-02 |  |  |  | YES | TUNQEC01MMS2P-VT6-TDP01-02 | 26
B2.1 | N |  |  |  | MCB 3P QEC01-VT6-TDP01-03 | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-03 | QEC01_RTU |  |  |  |  | 90 |  |  |  |  | &3P-VT6-TDP01-03 | TUN_QEC01_MMS_3P-VT6-TDP01-03 |  |  |  | YES | TUNQEC01MMS3P-VT6-TDP01-03 | 26
B2.1 | N |  |  |  | MCB 2P QEC01-VT6-TDP01-03 | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-03 | QEC01_RTU |  |  |  |  | 91 |  |  |  |  | &2P-VT6-TDP01-03 | TUN_QEC01_MMS_2P-VT6-TDP01-03 |  |  |  | YES | TUNQEC01MMS2P-VT6-TDP01-03 | 26
B2.1 | N |  |  |  | MCB 3P QEC01-FR2-BDP01-01 | TUN:QEC01 | MMS | MCB | 3P--FR2-BDP01-01 | QEC01_RTU |  |  |  |  | 92 |  |  |  |  | &3P--FR2-BDP01-01 | TUN_QEC01_MMS_3P--FR2-BDP01-01 |  |  |  | YES | TUNQEC01MMS3P--FR2-BDP01-01 | 27
B2.1 | N |  |  |  | MCB 2P QEC01-FR2-BDP01-01 | TUN:QEC01 | MMS | MCB | 2P--FR2-BDP01-01 | QEC01_RTU |  |  |  |  | 93 |  |  |  |  | &2P--FR2-BDP01-01 | TUN_QEC01_MMS_2P--FR2-BDP01-01 |  |  |  | YES | TUNQEC01MMS2P--FR2-BDP01-01 | 27
B2.1 | N |  |  |  | MCB 3P QEC01-FR2-BDP01-02 | TUN:QEC01 | MMS | MCB | 3P--FR2-BDP01-02 | QEC01_RTU |  |  |  |  | 94 |  |  |  |  | &3P--FR2-BDP01-02 | TUN_QEC01_MMS_3P--FR2-BDP01-02 |  |  |  | YES | TUNQEC01MMS3P--FR2-BDP01-02 | 27
B2.1 | N |  |  |  | MCB 2P QEC01-FR2-BDP01-02 | TUN:QEC01 | MMS | MCB | 2P--FR2-BDP01-02 | QEC01_RTU |  |  |  |  | 95 |  |  |  |  | &2P--FR2-BDP01-02 | TUN_QEC01_MMS_2P--FR2-BDP01-02 |  |  |  | YES | TUNQEC01MMS2P--FR2-BDP01-02 | 27
B2.1 | N |  |  |  | MCB QEC01-MSFD-CON-94 | TUN:QEC01 | MMS | MCB | MSFD-CON-94 | QEC01_RTU |  |  |  |  | 96 |  |  |  |  | &MSFD-CON-94 | TUN_QEC01_MMS_MSFD-CON-94 |  |  |  | YES | TUNQEC01MMSMSFD-CON-94 | 22
B2.1 | N |  |  |  | MCB QEC01-MSFD-CON-58 | TUN:QEC01 | MMS | MCB | MSFD-CON-58 | QEC01_RTU |  |  |  |  | 97 |  |  |  |  | &MSFD-CON-58 | TUN_QEC01_MMS_MSFD-CON-58 |  |  |  | YES | TUNQEC01MMSMSFD-CON-58 | 22
B2.1 | N |  |  |  | MCB QEC01-MSFD-CON-88 | TUN:QEC01 | MMS | MCB | MSFD-CON-88 | QEC01_RTU |  |  |  |  | 98 |  |  |  |  | &MSFD-CON-88 | TUN_QEC01_MMS_MSFD-CON-88 |  |  |  | YES | TUNQEC01MMSMSFD-CON-88 | 22
B1.8 | Y |  |  |  |  | Electrical Panel EL2 I/O 01
B2.1 | N |  |  |  | QEC01-EL2-IO01 | TUN:QEC01 | MMS | EL | EL2-IO01 | QEC01_RTU |  |  |  |  | 99 |  |  |  |  | &EL2-IO01 | TUN_QEC01_MMS_EL2-IO01 |  |  |  | YES | TUNQEC01MMSEL2-IO01 | 19
B2.1 | N |  |  |  | MCCB QEC01-EL2-UPS | TUN:QEC01 | MMS | MCCB | EL2-UPS | QEC01_RTU |  |  |  |  | 100 |  |  |  |  | &EL2-UPS | TUN_QEC01_MMS_EL2-UPS |  |  |  | YES | TUNQEC01MMSEL2-UPS | 18
B2.1 | N |  |  |  | LBS QEC01-EL2-UPS | TUN:QEC01 | MMS | LBS | EL2-UPS | QEC01_RTU |  |  |  |  | 101 |  |  |  |  | &EL2-UPS | TUN_QEC01_MMS_EL2-UPS |  |  |  | YES | TUNQEC01MMSEL2-UPS | 18
B2.1 | N |  |  |  | MCB UPS QEC01-EL2-VSD01 | TUN:QEC01 | MMS | MCB | UPS_EL2-VSD01 | QEC01_RTU |  |  |  |  | 102 |  |  |  |  | &UPS-EL2-VSD01 | TUN_QEC01_MMS_UPS_EL2-VSD01 |  |  |  | YES | TUNQEC01MMSUPS_EL2-VSD01 | 24
B2.1 | N |  |  |  | MCB UPS QEC01-EL2-VSD02 | TUN:QEC01 | MMS | MCB | UPS_EL2-VSD02 | QEC01_RTU |  |  |  |  | 103 |  |  |  |  | &UPS-EL2-VSD02 | TUN_QEC01_MMS_UPS_EL2-VSD02 |  |  |  | YES | TUNQEC01MMSUPS_EL2-VSD02 | 24
B2.1 | N |  |  |  | MCB 3P QEC01-VT1-IDP01 | TUN:QEC01 | MMS | MCB | 3P-VT1-IDP01 | QEC01_RTU |  |  |  |  | 104 |  |  |  |  | &3P-VT1-IDP01 | TUN_QEC01_MMS_3P-VT1-IDP01 |  |  |  | YES | TUNQEC01MMS3P-VT1-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P QEC01-VT1-IDP01 | TUN:QEC01 | MMS | MCB | 2P-VT1-IDP01 | QEC01_RTU |  |  |  |  | 105 |  |  |  |  | &2P-VT1-IDP01 | TUN_QEC01_MMS_2P-VT1-IDP01 |  |  |  | YES | TUNQEC01MMS2P-VT1-IDP01 | 23
B2.1 | N |  |  |  | MCB 3P QEC01-VT2-IDP01 | TUN:QEC01 | MMS | MCB | 3P-VT2-IDP01 | QEC01_RTU |  |  |  |  | 106 |  |  |  |  | &3P-VT2-IDP01 | TUN_QEC01_MMS_3P-VT2-IDP01 |  |  |  | YES | TUNQEC01MMS3P-VT2-IDP01 | 23
B2.1 | N |  |  |  | MCB 2P QEC01-VT2-IDP01 | TUN:QEC01 | MMS | MCB | 2P-VT2-IDP01 | QEC01_RTU |  |  |  |  | 107 |  |  |  |  | &2P-VT2-IDP01 | TUN_QEC01_MMS_2P-VT2-IDP01 |  |  |  | YES | TUNQEC01MMS2P-VT2-IDP01 | 23
B2.1 | N |  |  |  | MCB 3P QEC01-VT5-TDP01-01 | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-01 | QEC01_RTU |  |  |  |  | 108 |  |  |  |  | &3P-VT5-TDP01-01 | TUN_QEC01_MMS_3P-VT5-TDP01-01 |  |  |  | YES | TUNQEC01MMS3P-VT5-TDP01-01 | 26
B2.1 | N |  |  |  | MCB 2P QEC01-VT5-TDP01-01 | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-01 | QEC01_RTU |  |  |  |  | 109 |  |  |  |  | &2P-VT5-TDP01-01 | TUN_QEC01_MMS_2P-VT5-TDP01-01 |  |  |  | YES | TUNQEC01MMS2P-VT5-TDP01-01 | 26
B2.1 | N |  |  |  | MCB 3P QEC01-VT5-TDP01-02 | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-02 | QEC01_RTU |  |  |  |  | 110 |  |  |  |  | &3P-VT5-TDP01-02 | TUN_QEC01_MMS_3P-VT5-TDP01-02 |  |  |  | YES | TUNQEC01MMS3P-VT5-TDP01-02 | 26
B2.1 | N |  |  |  | MCB 2P QEC01-VT5-TDP01-02 | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-02 | QEC01_RTU |  |  |  |  | 111 |  |  |  |  | &2P-VT5-TDP01-02 | TUN_QEC01_MMS_2P-VT5-TDP01-02 |  |  |  | YES | TUNQEC01MMS2P-VT5-TDP01-02 | 26
B2.1 | N |  |  |  | MCB 3P QEC01-VT5-TDP01-03 | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-03 | QEC01_RTU |  |  |  |  | 112 |  |  |  |  | &3P-VT5-TDP01-03 | TUN_QEC01_MMS_3P-VT5-TDP01-03 |  |  |  | YES | TUNQEC01MMS3P-VT5-TDP01-03 | 26
B2.1 | N |  |  |  | MCB 2P QEC01-VT5-TDP01-03 | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-03 | QEC01_RTU |  |  |  |  | 113 |  |  |  |  | &2P-VT5-TDP01-03 | TUN_QEC01_MMS_2P-VT5-TDP01-03 |  |  |  | YES | TUNQEC01MMS2P-VT5-TDP01-03 | 26
B2.1 | N |  |  |  | MCB 3P QEC01-FR1-BDP01-01 | TUN:QEC01 | MMS | MCB | 3P-FR1-BDP01-01 | QEC01_RTU |  |  |  |  | 114 |  |  |  |  | &3P-FR1-BDP01-01 | TUN_QEC01_MMS_3P-FR1-BDP01-01 |  |  |  | YES | TUNQEC01MMS3P-FR1-BDP01-01 | 26
B2.1 | N |  |  |  | MCB 2P QEC01-FR1-BDP01-01 | TUN:QEC01 | MMS | MCB | 2P-FR1-BDP01-01 | QEC01_RTU |  |  |  |  | 115 |  |  |  |  | &2P-FR1-BDP01-01 | TUN_QEC01_MMS_2P-FR1-BDP01-01 |  |  |  | YES | TUNQEC01MMS2P-FR1-BDP01-01 | 26
B2.1 | N |  |  |  | MCB 3P QEC01-FR1-BDP01-02 | TUN:QEC01 | MMS | MCB | 3P-FR1-BDP01-02 | QEC01_RTU |  |  |  |  | 116 |  |  |  |  | &3P-FR1-BDP01-02 | TUN_QEC01_MMS_3P-FR1-BDP01-02 |  |  |  | YES | TUNQEC01MMS3P-FR1-BDP01-02 | 26
B2.1 | N |  |  |  | MCB 2P QEC01-FR1-BDP01-02 | TUN:QEC01 | MMS | MCB | 2P-FR1-BDP01-02 | QEC01_RTU |  |  |  |  | 117 |  |  |  |  | &2P-FR1-BDP01-02 | TUN_QEC01_MMS_2P-FR1-BDP01-02 |  |  |  | YES | TUNQEC01MMS2P-FR1-BDP01-02 | 26
B2.1 | N |  |  |  | MCB QEC01-MSFD-CON-50 | TUN:QEC01 | MMS | MCB | MSFD-CON-50 | QEC01_RTU |  |  |  |  | 118 |  |  |  |  | &MSFD-CON-50 | TUN_QEC01_MMS_MSFD-CON-50 |  |  |  | YES | TUNQEC01MMSMSFD-CON-50 | 22
B2.1 | N |  |  |  | MCB QEC01-MSFD-CON-52 | TUN:QEC01 | MMS | MCB | MSFD-CON-52 | QEC01_RTU |  |  |  |  | 119 |  |  |  |  | &MSFD-CON-52 | TUN_QEC01_MMS_MSFD-CON-52 |  |  |  | YES | TUNQEC01MMSMSFD-CON-52 | 22
B2.1 | N |  |  |  | MCB QEC01-MSFD-CON-95 | TUN:QEC01 | MMS | MCB | MSFD-CON-95 | QEC01_RTU |  |  |  |  | 120 |  |  |  |  | &MSFD-CON-95 | TUN_QEC01_MMS_MSFD-CON-95 |  |  |  | YES | TUNQEC01MMSMSFD-CON-95 | 22

## 3-Class Mapping
Class name | Prototype | Aggregate name | Object type | isAComment
MPLC | LusailHK:LusTvsMplc |  |  | N | LusTvsMplcType
WTDG | LusailHK:LusTvsWtdg |  |  | N | LusTvsWtdgType
SWI | LusailHK:LusTvsSwi |  |  | N | LusTvsSwiType
SPLC | LusailHK:LusTvsSplc |  |  | N | LusTvsSplcType
FMOP | LusailHK:LusTvsFmop |  |  | N | LusTvsFmopType
LCP | LusailHK:LusTvsLcp |  |  | N | LusTvsLcpType
VENTILATION | LusailHK:LusTvsVentilation | VENT |  | N | LusTvsVentType
EMERGENCY | LusailHK:LusTvsEmergency | EMER |  | N | LusTvsEmerType
MUL | LusailHK:LusTvsMul |  |  | N | LusTvsMulType
FXL | LusailHK:LusTvsFxl |  |  | N | LusTvsFxlType
TVF | LusailHK:LusTvsTvf |  |  | N | LusTvsTvfType
JET | LusailHK:LusTvsJet |  |  | N | LusTvsJetType
TVD | LusailHK:LusTvsTvd |  |  | N | LusTvsTvdType
IDP | LusailHK:LusTvsIdp |  |  | N | LusTvsIdpType
MSFD | LusailHK:LusTvsMsfd |  |  | N | LusTvsMsfdType
OTS | LusailHK:LusTvsOts |  |  | N | LusTvsOtsType
TTS | LusailHK:LusTvsTts |  |  | N | LusTvsTtsType
VS | LusailHK:LusTvsVs |  |  | N | LusTvsVsType
AHU | LusailHK:LusTvsAhu |  |  | N | LusTvsAhuType
PFA | LusailHK:LusTvsPfa |  |  | N | LusTvsPfaType
EXF | LusailHK:LusTvsExf |  |  | N | LusTvsExfType
SMC | LusailHK:LusTvsSmc |  |  | N | LusTvsSmcType
SED | LusailHK:LusTvsSed |  |  | N | LusTvsSedType
SPLCMMS | LusailHK:LusTvsSplcmms |  |  | N | LusTvsSplcmmsType
MPLCMMS | LusailHK:LusTvsMplcmms |  |  | N | LusTvsMplcmmsType
MCB | LusailHK:LusTvsMcb |  |  | N | LusTvsMcbType
ADS | LusailHK:LusTvsAds |  |  | N | LusTvsAdsType
TRF | LusailHK:LusTvsTrf |  |  | N | LusTvsTrfType
ACB | LusailHK:LusTvsAcb |  |  | N | LusTvsAcbType
MDB | LusailHK:LusTvsMdb |  |  | N | LusTvsMdbType
EL | LusailHK:LusTvsEl |  |  | N | LusTvsElType
MCCB | LusailHK:LusTvsMccb |  |  | N | LusTvsMccbType
LBS | LusailHK:LusTvsLbs |  |  | N | LusTvsLbsType
SMDB | LusailHK:LusTvsSmdb |  |  | N | LusTvsSmdbType

## 4-External Variables
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
MPLC | dciMPLC-PlcState:dac | DEIV | PlcState | PLC STATE | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-OpStatus:dac | DEIV | OpStatus | OPERATIONAL STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-PlcA:dac | DEIV | PlcA | PLC-A STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-PlcB:dac | DEIV | PlcB | PLC-B STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-AppDiff:dac | DEIV | AppDiff | APPLICATIONS ARE DIFFERENT ON THE TWO PLCS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-PwStat:dac | DEIV | PwStat | POWER SUPPLY STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-CpuStat:dac | DEIV | CpuStat | CPU MODULE STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-CrpStat:dac | DEIV | CrpStat | CRP MODULE STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComScada:dac | DEIV | ComScada | NOE MODULE COMMUNICATION [SCADA] STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComStation:dac | DEIV | ComStation | NOE MODULE COMMUNICATION [STATION PLC] STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-SdStat:dac | DEIV | SdStat | COMMUNICATION WITH SCADA STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComPea:dac | DEIV | ComPea | COMMUNICATION WITH STATION PEA-01 PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComMar1:dac | DEIV | ComMar1 | COMMUNICATION WITH STATION MAR-01 PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComMar2:dac | DEIV | ComMar2 | COMMUNICATION WITH STATION MAR-02 PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComMar3:dac | DEIV | ComMar3 | COMMUNICATION WITH STATION MAR-03 PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComMar4:dac | DEIV | ComMar4 | COMMUNICATION WITH STATION MAR-04 PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComQec:dac | DEIV | ComQec | COMMUNICATION WITH STATION QEC-01 PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComEc:dac | DEIV | ComEc | COMMUNICATION WITH STATION EC1-01 PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComQap:dac | DEIV | ComQap | COMMUNICATION WITH STATION QAP-01 PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComFxh:dac | DEIV | ComFxh | COMMUNICATION WITH STATION FXH-02 PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComPeaa:dac | DEIV | ComPeaa | COMMUNICATION WITH SHAFT PEA-0A PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComPeab:dac | DEIV | ComPeab | COMMUNICATION WITH SHAFT PEA-1B PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComMara:dac | DEIV | ComMara | COMMUNICATION WITH SHAFT MAR-0A PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComEca:dac | DEIV | ComEca | COMMUNICATION WITH SHAFT EC1-0A PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComQapb:dac | DEIV | ComQapb | COMMUNICATION WITH SHAFT QAP-1B PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
WTDG | aciWTDG-Counter:aac | AEIV | Counter | Watchdog Counter | $VOID | VEE | 0 |  |  |  | 4
SWI | dciSWI-SwStat:dac | DEIV | SwStat | SWITCH STATUS | $VOID | VEE | 0 |  |  |  | 4
SPLC | dciSPLC-PlcState:dac | DEIV | PlcState | PLC STATE | $VOID | VEE | 0 |  |  |  | 4
SPLC | dciSPLC-OpStatus:dac | DEIV | OpStatus | OPERATIONAL STATUS | $VOID | VEE | 0 |  |  |  | 4
SPLC | dciSPLC-PwStat:dac | DEIV | PwStat | POWER SUPPLY STATUS | $VOID | VEE | 0 |  |  |  | 4
SPLC | dciSPLC-CpuStat:dac | DEIV | CpuStat | CPU MODULE STATUS | $VOID | VEE | 0 |  |  |  | 4
SPLC | dciSPLC-CrpStat:dac | DEIV | CrpStat | CRP MODULE STATUS | $VOID | VEE | 0 |  |  |  | 4
SPLC | dciSPLC-CraStat:dac | DEIV | CraStat | CRA MODULE STATUS | $VOID | VEE | 0 |  |  |  | 4
SPLC | dciSPLC-NrpStat:dac | DEIV | NrpStat | NRP MODULE STATUS | $VOID | VEE | 0 |  |  |  | 4
SPLC | dciSPLC-ComStat:dac | DEIV | ComStat | NOE MODULE COMMUNICATION STATUS | $VOID | VEE | 0 |  |  |  | 4
SPLC | dciSPLC-IoStat:dac | DEIV | IoStat | IO MODULE STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-EmergNod:dac | DEIV | EmergNod | LOCAL FIRE PANEL EMERGENCY MODE | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-RightStat:dac | DEIV | RightStat | LOCAL FIRE PANEL RIGHT SCENARIO PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-LeftStat:dac | DEIV | LeftStat | LOCAL FIRE PANEL LEFT SCENARIO PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-Spare1:dac | DEIV | Spare1 | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-Spare2:dac | DEIV | Spare2 | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-Spare3:dac | DEIV | Spare3 | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-Spare4:dac | DEIV | Spare4 | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-Spare5:dac | DEIV | Spare5 | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-Spare6:dac | DEIV | Spare6 | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-Spare7:dac | DEIV | Spare7 | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-Spare8:dac | DEIV | Spare8 | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
LCP | dciLCP-ComFaultPlc:dac | DEIV | ComFaultPlc | COMMUNICATION WITH PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
LCP | dciLCP-LcpMode:dac | DEIV | LcpMode | LCP MODE | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dciVENT-OpMode:dac | DEIV | OpMode | OPERATING MODE | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dciVENT-ActMode:dac | DEIV | ActMode | ACTIVE VENTILATION MODE | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dioVENT-CmdAuto:dov1 | DEOV | CmdAuto | PLC AUTO MODE COMMAND | $VOID | VES | 0 |  |  |  | 4
VENTILATION | dioVENT-CmdSelMan:dov1 | DEOV | CmdSelMan | SCADA MANUAL MODE SELECT | $VOID | VES | 0 |  |  |  | 4
VENTILATION | dciVENT-AckSelMan:dac | DEIV | AckSelMan | SCADA MANUAL MODE SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dioVENT-CmdExeMan:dov1 | DEOV | CmdExeMan | SCADA MANUAL MODE EXECUTE | $VOID | VES | 0 |  |  |  | 4
VENTILATION | dciVENT-AckExeMan:dac | DEIV | AckExeMan | SCADA MANUAL MODE EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dioVENT-CmdSelPis:dov1 | DEOV | CmdSelPis | PISTON MODE SELECT | $VOID | VES | 0 |  |  |  | 4
VENTILATION | dciVENT-AckSelPis:dac | DEIV | AckSelPis | PISTON MODE SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dioVENT-CmdExePis:dov1 | DEOV | CmdExePis | PISTON MODE EXECUTE | $VOID | VES | 0 |  |  |  | 4
VENTILATION | dciVENT-AckExePis:dac | DEIV | AckExePis | PISTON MODE EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dioVENT-CmdSelMech:dov1 | DEOV | CmdSelMech | MECHANICAL MODE SELECT | $VOID | VES | 0 |  |  |  | 4
VENTILATION | dciVENT-AckSelMech:dac | DEIV | AckSelMech | MECHANICAL MODE SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dioVENT-CmdExeMech:dov1 | DEOV | CmdExeMech | MECHANICAL MODE EXECUTE | $VOID | VES | 0 |  |  |  | 4
VENTILATION | dciVENT-AckExeMech:dac | DEIV | AckExeMech | MECHANICAL MODE EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dioVENT-CmdExelCool:dov1 | DEOV | CmdExelCool | COOLING MODE SELECT | $VOID | VES | 0 |  |  |  | 4
VENTILATION | dciVENT-AckSelCool:dac | DEIV | AckSelCool | COOLING MODE SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dioVENT-CmdExeCool:dov1 | DEOV | CmdExeCool | COOLING MODE EXECUTE | $VOID | VES | 0 |  |  |  | 4
VENTILATION | dciVENT-AckExeCool:dac | DEIV | AckExeCool | COOLING MODE EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
EMERGENCY | dciEMERGENCY-ScenAct:dac | DEIV | ScenAct | SCENARIO ACTIVATION PROPOSAL BY TVS | $VOID | VEE | 0 |  |  |  | 4
EMERGENCY | dciEMERGENCY-ActEmerg:dac | DEIV | ActEmerg | ACTIVATION STATUS OF EMERGENCY SCENARIO | $VOID | VEE | 0 |  |  |  | 4
EMERGENCY | dioEMERGENCY-CmdSelMan:dov1 | DEOV | CmdSelMan | SCENARIO CONFIRMATION BY SCADA OPERATOR SELECT | $VOID | VES | 0 |  |  |  | 4
EMERGENCY | dciEMERGENCY-AckSelMan:dac | DEIV | AckSelMan | SCENARIO CONFIRMATION BY SCADA OPERATOR SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
EMERGENCY | dioEMERGENCY-CmdExeMan:dov1 | DEOV | CmdExeMan | SCENARIO CONFIRMATION BY SCADA OPERATOR EXECUTE | $VOID | VES | 0 |  |  |  | 4
EMERGENCY | dciEMERGENCY-AckExeMan:dac | DEIV | AckExeMan | SCENARIO CONFIRMATION BY SCADA OPERATOR EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone1:aac | AEIV | Zone1 | AVERAGE TUNNEL TEMPERATURE ZONE 1 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone2:aac | AEIV | Zone2 | AVERAGE TUNNEL TEMPERATURE ZONE 2 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone3:aac | AEIV | Zone3 | AVERAGE TUNNEL TEMPERATURE ZONE 3 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone4:aac | AEIV | Zone4 | AVERAGE TUNNEL TEMPERATURE ZONE 4 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone5:aac | AEIV | Zone5 | AVERAGE TUNNEL TEMPERATURE ZONE 5 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone6:aac | AEIV | Zone6 | AVERAGE TUNNEL TEMPERATURE ZONE 6 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone7:aac | AEIV | Zone7 | AVERAGE TUNNEL TEMPERATURE ZONE 7 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone8:aac | AEIV | Zone8 | AVERAGE TUNNEL TEMPERATURE ZONE 8 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone9:aac | AEIV | Zone9 | AVERAGE TUNNEL TEMPERATURE ZONE 9 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone10:aac | AEIV | Zone10 | AVERAGE TUNNEL TEMPERATURE ZONE 10 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone11:aac | AEIV | Zone11 | AVERAGE TUNNEL TEMPERATURE ZONE 11 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone12:aac | AEIV | Zone12 | AVERAGE TUNNEL TEMPERATURE ZONE 12 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone13:aac | AEIV | Zone13 | AVERAGE TUNNEL TEMPERATURE ZONE 13 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone14:aac | AEIV | Zone14 | AVERAGE TUNNEL TEMPERATURE ZONE 14 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone15:aac | AEIV | Zone15 | AVERAGE TUNNEL TEMPERATURE ZONE 15 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-OutTem:aac | AEIV | OutTem | AVERAGE OUTDOOR TEMPERATURE | $VOID | VEE | 0 |  |  |  | 4
FXL | aciFXL-Zone16:aac | AEIV | Zone16 | AVERAGE TUNNEL TEMPERATURE ZONE 16 | $VOID | VEE | 0 |  |  |  | 4
FXL | aciFXL-Zone17:aac | AEIV | Zone17 | AVERAGE TUNNEL TEMPERATURE ZONE 17 | $VOID | VEE | 0 |  |  |  | 4
FXL | aciFXL-OutTem:aac | AEIV | OutTem | AVERAGE OUTDOOR TEMPERATURE | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-SwitchStat:dac | DEIV | SwitchStat | ELECTRICAL PANEL SELECTOR SWITCH STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-OperatingMode:dac | DEIV | OperatingMode | OPERATING MODE | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-RunStatus:dac | DEIV | RunStatus | RUN STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dioTVF-CmdAuto:dov1 | DEOV | CmdAuto | SCADA AUTO MODE COMMAND | $VOID | VES | 0 |  |  |  | 4
TVF | dioTVF-CmdSelMan:dov1 | DEOV | CmdSelMan | SCADA MANUAL MODE SELECT | $VOID | VES | 0 |  |  |  | 4
TVF | dciTVF-AckSelMan:dac | DEIV | AckSelMan | SCADA MANUAL MODE SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
TVF | dioTVF-CmdExeMan:dov1 | DEOV | CmdExeMan | SCADA MANUAL MODE EXECUTE | $VOID | VES | 0 |  |  |  | 4
TVF | dciTVF-AckExeMan:dac | DEIV | AckExeMan | SCADA MANUAL MODE EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-EleStat:dac | DEIV | EleStat | VSD ELECTRICAL STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-StartStat:dac | DEIV | StartStat | VSD FAIL TO START STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-StopStat:dac | DEIV | StopStat | VSD FAIL TO STOP STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | aciTVF-SpeedFreq:aac | AEIV | SpeedFreq | VSD SPEED FREQUENCY | $VOID | VEE | 0 |  |  |  | 4
TVF | dioTVF-CmdSpeedOrd:dov1 | DEOV | CmdSpeedOrd | VSD SPEED ORDER | $VOID | VES | 0 |  |  |  | 4
TVF | dioTVF-CmdSelStop:dov1 | DEOV | CmdSelStop | STOP ORDER (VSD) SELECT | $VOID | VES | 0 |  |  |  | 4
TVF | dciTVF-AckSelStop:dac | DEIV | AckSelStop | STOP ORDER (VSD) SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
TVF | dioTVF-CmdExeStop:dov1 | DEOV | CmdExeStop | STOP ORDER (VSD) EXECUTE | $VOID | VES | 0 |  |  |  | 4
TVF | dciTVF-AckExeStop:dac | DEIV | AckExeStop | STOP ORDER (VSD) EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
TVF | dioTVF-CmdSelFwOrd:dov1 | DEOV | CmdSelFwOrd | FORWARD ORDER (VSD) SELECT | $VOID | VES | 0 |  |  |  | 4
TVF | dciTVF-AckSelFwOrd:dac | DEIV | AckSelFwOrd | FORWARD ORDER (VSD) SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
TVF | dioTVF-CmdExeFwOrd:dov1 | DEOV | CmdExeFwOrd | FORWARD ORDER (VSD) EXECUTE | $VOID | VES | 0 |  |  |  | 4
TVF | dciTVF-AckExeFwOrd:dac | DEIV | AckExeFwOrd | FORWARD ORDER (VSD) EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
TVF | dioTVF-CmdSelRvOrd:dov1 | DEOV | CmdSelRvOrd | REVERSE ORDER (VSD) SELECT | $VOID | VES | 0 |  |  |  | 4
TVF | dciTVF-AckSelRvOrd:dac | DEIV | AckSelRvOrd | REVERSE ORDER (VSD) SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
TVF | dioTVF-CmdExeRvOrd:dov1 | DEOV | CmdExeRvOrd | REVERSE ORDER (VSD) EXECUTE | $VOID | VES | 0 |  |  |  | 4
TVF | dciTVF-AckExeRvOrd:dac | DEIV | AckExeRvOrd | REVERSE ORDER (VSD) EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-AvailStat:dac | DEIV | AvailStat | FAN AVAILABILITY STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-CirPos:dac | DEIV | CirPos | CIRCUIT BREAKER POSITION | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-CirTrip:dac | DEIV | CirTrip | CIRCUIT BREAKER TRIPPED STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-FanPos:dac | DEIV | FanPos | FAN HEATER CIRCUIT BREAKER POSITION | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-FanTrip:dac | DEIV | FanTrip | FAN HEATER CIRCUIT BREAKER TRIPPED STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-ForOut:dac | DEIV | ForOut | FORWARD START-UP MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-RevOut:dac | DEIV | RevOut | REVERSE START-UP MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-StopOut:dac | DEIV | StopOut | STOP MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-WindTem:dac | DEIV | WindTem | WINDING TEMPERATURE STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-FrontTem:dac | DEIV | FrontTem | FRONT BEARING TEMPERATURE STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-RearTem:dac | DEIV | RearTem | REAR BEARING TEMPERATURE STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-Vib1:dac | DEIV | Vib1 | VIBRATION 1ST LEVEL STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-Vib2:dac | DEIV | Vib2 | VIBRATION 2ND LEVEL STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-More10:dac | DEIV | More10 | MORE THAN 10 STARTUP PER HOUR STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | aciTVF-RunHrs:aac | AEIV | RunHrs | RUNNING HOURS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-SwitchStat:dac | DEIV | SwitchStat | ELECTRICAL PANEL SELECTOR SWITCH STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-OperatingMode:dac | DEIV | OperatingMode | OPERATING MODE | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-RunStatus:dac | DEIV | RunStatus | RUN STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dioJET-CmdAutoCom:dov1 | DEOV | CmdAutoCom | SCADA AUTO MODE COMMAND | $VOID | VES | 0 |  |  |  | 4
JET | dioJET-CmdSelMan:dov1 | DEOV | CmdSelMan | SCADA MANUAL MODE SELECT | $VOID | VES | 0 |  |  |  | 4
JET | dciJET-AckSelMan:dac | DEIV | AckSelMan | SCADA MANUAL MODE SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
JET | dioJET-CmdExeMan:dov1 | DEOV | CmdExeMan | SCADA MANUAL MODE EXECUTE | $VOID | VES | 0 |  |  |  | 4
JET | dciJET-AckExeMan:dac | DEIV | AckExeMan | SCADA MANUAL MODE EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-EleStat:dac | DEIV | EleStat | VSD ELECTRICAL STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-FailStart:dac | DEIV | FailStart | VSD FAIL TO START STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-FailStop:dac | DEIV | FailStop | VSD FAIL TO STOP STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | aciJET-SpeedFrep:aac | AEIV | SpeedFrep | VSD SPEED FREQUENCY | $VOID | VEE | 0 |  |  |  | 4
JET | dioJET-CmdSpeedOrd:dov1 | DEOV | CmdSpeedOrd | VSD SPEED ORDER | $VOID | VES | 0 |  |  |  | 4
JET | dioJET-CmdSelStop:dov1 | DEOV | CmdSelStop | STOP ORDER (VSD) SELECT | $VOID | VES | 0 |  |  |  | 4
JET | dciJET-AckSelStop:dac | DEIV | AckSelStop | STOP ORDER (VSD) SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
JET | dioJET-CmdExeStop:dov1 | DEOV | CmdExeStop | STOP ORDER (VSD) EXECUTE | $VOID | VES | 0 |  |  |  | 4
JET | dciJET-AckExeStop:dac | DEIV | AckExeStop | STOP ORDER (VSD) EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
JET | dioJET-CmdSelFwOrd:dov1 | DEOV | CmdSelFwOrd | FORWARD ORDER (VSD) SELECT | $VOID | VES | 0 |  |  |  | 4
JET | dciJET-AckSelFwOrd:dac | DEIV | AckSelFwOrd | FORWARD ORDER (VSD) SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
JET | dioJET-CmdExeFwOrd:dov1 | DEOV | CmdExeFwOrd | FORWARD ORDER (VSD) EXECUTE | $VOID | VES | 0 |  |  |  | 4
JET | dciJET-AckExeFwOrd:dac | DEIV | AckExeFwOrd | FORWARD ORDER (VSD) EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
JET | dioJET-CmdSelRvOrd:dov1 | DEOV | CmdSelRvOrd | REVERSE ORDER (VSD) SELECT | $VOID | VES | 0 |  |  |  | 4
JET | dciJET-AckSelRvOrd:dac | DEIV | AckSelRvOrd | REVERSE ORDER (VSD) SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
JET | dioJET-CmdExeRvOrd:dov1 | DEOV | CmdExeRvOrd | REVERSE ORDER (VSD) EXECUTE | $VOID | VES | 0 |  |  |  | 4
JET | dciJET-AckExeRvOrd:dac | DEIV | AckExeRvOrd | REVERSE ORDER (VSD) EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-AvailStat:dac | DEIV | AvailStat | FAN AVAILABILITY STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-CirOpen:dac | DEIV | CirOpen | CIRCUIT BREAKER POSITION | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-CirOut:dac | DEIV | CirOut | CIRCUIT BREAKER TRIPPED STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-FanOpen:dac | DEIV | FanOpen | FAN HEATER CIRCUIT BREAKER POSITION | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-FanOut:dac | DEIV | FanOut | FAN HEATER CIRCUIT BREAKER TRIPPED STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-ForOut:dac | DEIV | ForOut | FORWARD START-UP MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-RevOut:dac | DEIV | RevOut | REVERSE START-UP MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-StopOut:dac | DEIV | StopOut | STOP MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-WindTem:dac | DEIV | WindTem | WINDING TEMPERATURE STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-FrontTem1:dac | DEIV | FrontTem1 | FRONT BEARING TEMPERATURE STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-RearTem:dac | DEIV | RearTem | REAR BEARING TEMPERATURE STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-Vib1:dac | DEIV | Vib1 | VIBRATION 1ST LEVEL STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-Vib2:dac | DEIV | Vib2 | VIBRATION 2ND LEVEL STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-More6hr:dac | DEIV | More6hr | MORE THAN 10 STARTUP PER HOUR STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | aciJET-RunHrs:aac | AEIV | RunHrs | RUNNING HOURS | $VOID | VEE | 0 |  |  |  | 4
TVD | dciTVD-SwitchStat:dac | DEIV | SwitchStat | ELECTRICAL PANEL SELECTOR SWITCH STATUS | $VOID | VEE | 0 |  |  |  | 4
TVD | dciTVD-OpMod:dac | DEIV | OpMod | OPERATING MODE | $VOID | VEE | 0 |  |  |  | 4
TVD | dciTVD-Stat:dac | DEIV | Stat | ARRAY STATUS | $VOID | VEE | 0 |  |  |  | 4
TVD | dioTVD-CmdAuto:dov1 | DEOV | CmdAuto | SCADA AUTO MODE COMMAND | $VOID | VES | 0 |  |  |  | 4
TVD | dioTVD-CmdSelMan:dov1 | DEOV | CmdSelMan | SCADA MANUAL MODE SELECT | $VOID | VES | 0 |  |  |  | 4
TVD | dciTVD-AckSelMan:dac | DEIV | AckSelMan | SCADA MANUAL MODE SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
TVD | dioTVD-CmdExeMan:dov1 | DEOV | CmdExeMan | SCADA MANUAL MODE EXECUTE | $VOID | VES | 0 |  |  |  | 4
TVD | dciTVD-AckExeMan:dac | DEIV | AckExeMan | SCADA MANUAL MODE EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
TVD | dioTVD-CmdSelOpen:dov1 | DEOV | CmdSelOpen | OPEN ORDER SELECT | $VOID | VES | 0 |  |  |  | 4
TVD | dciTVD-AckSelOpen:dac | DEIV | AckSelOpen | OPEN ORDER SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
TVD | dioTVD-CmdExeOpen:dov1 | DEOV | CmdExeOpen | OPEN ORDER EXECUTE | $VOID | VES | 0 |  |  |  | 4
TVD | dciTVD-AckExeOpen:dac | DEIV | AckExeOpen | OPEN ORDER EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
TVD | dioTVD-CmdSelClose:dov1 | DEOV | CmdSelClose | CLOSE ORDER SELECT | $VOID | VES | 0 |  |  |  | 4
TVD | dciTVD-AckSelClose:dac | DEIV | AckSelClose | CLOSE ORDER SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
TVD | dioTVD-CmdExeClose:dov1 | DEOV | CmdExeClose | CLOSE ORDER EXECUTE | $VOID | VES | 0 |  |  |  | 4
TVD | dciTVD-AckExeClose:dac | DEIV | AckExeClose | CLOSE ORDER EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
TVD | dciTVD-DamOpen:dac | DEIV | DamOpen | DAMPER SUPPLY CIRCUIT BREAKER POSITION | $VOID | VEE | 0 |  |  |  | 4
TVD | dciTVD-DamOut:dac | DEIV | DamOut | DAMPER SUPPLY CIRCUIT BREAKER TRIPPED STATUS | $VOID | VEE | 0 |  |  |  | 4
TVD | dciTVD-FailOpen:dac | DEIV | FailOpen | OPEN MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
TVD | dciTVD-FailClose:dac | DEIV | FailClose | CLOSE MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
IDP | dciIDP-SwitchStat:dac | DEIV | SwitchStat | ELECTRICAL PANEL SELECTOR SWITCH STATUS | $VOID | VEE | 0 |  |  |  | 4
IDP | dciIDP-Stat:dac | DEIV | Stat | ARRAY STATUS | $VOID | VEE | 0 |  |  |  | 4
IDP | dciIDP-CloseStat:dac | DEIV | CloseStat | DAMPER SUPPLY CIRCUIT BREAKER POSITION | $VOID | VEE | 0 |  |  |  | 4
IDP | dciIDP-TripStat:dac | DEIV | TripStat | DAMPER SUPPLY CIRCUIT BREAKER TRIPPED STATUS | $VOID | VEE | 0 |  |  |  | 4
IDP | dciIDP-FailOpen:dac | DEIV | FailOpen | OPEN MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
IDP | dciIDP-FailClose:dac | DEIV | FailClose | CLOSE MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
MSFD | dciMSFD-Stat:dac | DEIV | Stat | ARRAY STATUS | $VOID | VEE | 0 |  |  |  | 4
MSFD | dciMSFD-CloseStat:dac | DEIV | CloseStat | DAMPER SUPPLY CIRCUIT BREAKER POSITION | $VOID | VEE | 0 |  |  |  | 4
MSFD | dciMSFD-TripStat:dac | DEIV | TripStat | DAMPER SUPPLY CIRCUIT BREAKER TRIPPED STATUS | $VOID | VEE | 0 |  |  |  | 4
MSFD | dciMSFD-LocalMod:dac | DEIV | LocalMod | LOCAL MODE STATUS | $VOID | VEE | 0 |  |  |  | 4
OTS | dciOTS-AvailStat:dac | DEIV | AvailStat | AVAILABILITY STATUS | $VOID | VEE | 0 |  |  |  | 4
OTS | dciOTS-SenOut:dac | DEIV | SenOut | TEMPERATURE OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
OTS | dciOTS-AveTem:dac | DEIV | AveTem | AVERAGE TEMPERATURE EXCLUSION STATUS | $VOID | VEE | 0 |  |  |  | 4
OTS | aciOTS-TemMeasure:aac | AEIV | TemMeasure | TEMPERATURE MEASUREMENT | $VOID | VEE | 0 |  |  |  | 4
TTS | dciTTS-Availability:dac | DEIV | Availability | AVAILABILITY STATUS | $VOID | VEE | 0 |  |  |  | 4
TTS | dciTTS-TemOut:dac | DEIV | TemOut | TEMPERATURE SENSOR OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
TTS | dciTTS-HumOut:dac | DEIV | HumOut | HUMIDITY SENSOR OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
TTS | dciTTS-AveTem:dac | DEIV | AveTem | AVERAGE TEMPERATURE EXCLUSION STATUS | $VOID | VEE | 0 |  |  |  | 4
TTS | aciTTS-Temperature:aac | AEIV | Temperature | TEMPERATURE MEASUREMENT | $VOID | VEE | 0 |  |  |  | 4
TTS | aciTTS-Humidity:aac | AEIV | Humidity | HUMIDITY MEASUREMENT | $VOID | VEE | 0 |  |  |  | 4
VS | dciVS-Availability:dac | DEIV | Availability | AVAILABILITY STATUS | $VOID | VEE | 0 |  |  |  | 4
VS | dciVS-SenStat:dac | DEIV | SenStat | SENSOR OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
VS | aciVS-Velocity:aac | AEIV | Velocity | VELOCITY MEASUREMENT | $VOID | VEE | 0 |  |  |  | 4
AHU | dciAHU-ControlMod:dac | DEIV | ControlMod | CONTROL MODE | $VOID | VEE | 0 |  |  |  | 4
AHU | dciAHU-RunStat:dac | DEIV | RunStat | RUN STATUS | $VOID | VEE | 0 |  |  |  | 4
PFA | dciPFA-ControlMod:dac | DEIV | ControlMod | CONTROL MODE | $VOID | VEE | 0 |  |  |  | 4
PFA | dciPFA-OpMode:dac | DEIV | OpMode | OPERATING MODE | $VOID | VEE | 0 |  |  |  | 4
PFA | dciPFA-RunStat:dac | DEIV | RunStat | RUN STATUS | $VOID | VEE | 0 |  |  |  | 4
PFA | dioPFA-CmdAuto:dov1 | DEOV | CmdAuto | SCADA AUTO MODE COMMAND | $VOID | VES | 0 |  |  |  | 4
PFA | dioPFA-CmdSelMan:dov1 | DEOV | CmdSelMan | SCADA MANUAL MODE SELECT | $VOID | VES | 0 |  |  |  | 4
PFA | dciPFA-AckSelMan:dac | DEIV | AckSelMan | SCADA MANUAL MODE SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
PFA | dioPFA-CmdExeMan:dov1 | DEOV | CmdExeMan | SCADA MANUAL MODE EXECUTE | $VOID | VES | 0 |  |  |  | 4
PFA | dciPFA-AckExeMan:dac | DEIV | AckExeMan | SCADA MANUAL MODE EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
PFA | dioPFA-CmdSelRun:dov1 | DEOV | CmdSelRun | RUN ORDER SELECT | $VOID | VES | 0 |  |  |  | 4
PFA | dciPFA-AckSelRun:dac | DEIV | AckSelRun | RUN ORDER SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
PFA | dioPFA-CmdExeRun:dov1 | DEOV | CmdExeRun | RUN ORDER EXECUTE | $VOID | VES | 0 |  |  |  | 4
PFA | dciPFA-AckExeRun:dac | DEIV | AckExeRun | RUN ORDER EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
PFA | dioPFA-CmdSelStop:dov1 | DEOV | CmdSelStop | STOP ORDER SELECT | $VOID | VES | 0 |  |  |  | 4
PFA | dciPFA-AckSelStop:dac | DEIV | AckSelStop | STOP ORDER SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
PFA | dioPFA-CmdExeStop:dov1 | DEOV | CmdExeStop | STOP ORDER EXECUTE | $VOID | VES | 0 |  |  |  | 4
PFA | dciPFA-AckExeStop:dac | DEIV | AckExeStop | STOP ORDER EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
PFA | dciPFA-StartMis:dac | DEIV | StartMis | START MISMATCH STATUS | $VOID | VEE | 0 |  |  |  | 4
PFA | dciPFA-StopMis:dac | DEIV | StopMis | STOP MISMATCH STATUS | $VOID | VEE | 0 |  |  |  | 4
EXF | dciEXF-ControlMod:dac | DEIV | ControlMod | CONTROL MODE | $VOID | VEE | 0 |  |  |  | 4
EXF | dciEXF-OpMode:dac | DEIV | OpMode | OPERATING MODE | $VOID | VEE | 0 |  |  |  | 4
EXF | dciEXF-AutoCom:dac | DEIV | AutoCom | RUN STATUS | $VOID | VEE | 0 |  |  |  | 4
EXF | dioEXF-CmdMan:dov1 | DEOV | CmdMan | SCADA AUTO MODE COMMAND | $VOID | VES | 0 |  |  |  | 4
EXF | dioEXF-CmdSelMan:dov1 | DEOV | CmdSelMan | SCADA MANUAL MODE SELECT | $VOID | VES | 0 |  |  |  | 4
EXF | dciEXF-AckSelMan:dac | DEIV | AckSelMan | SCADA MANUAL MODE SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
EXF | dioEXF-CmdExeMan:dov1 | DEOV | CmdExeMan | SCADA MANUAL MODE EXECUTE | $VOID | VES | 0 |  |  |  | 4
EXF | dciEXF-AckExeMan:dac | DEIV | AckExeMan | SCADA MANUAL MODE EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
EXF | dioEXF-CmdSelRun:dov1 | DEOV | CmdSelRun | RUN ORDER SELECT | $VOID | VES | 0 |  |  |  | 4
EXF | dciEXF-AckSelRun:dac | DEIV | AckSelRun | RUN ORDER SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
EXF | dioEXF-CmdExeRun:dov1 | DEOV | CmdExeRun | RUN ORDER EXECUTE | $VOID | VES | 0 |  |  |  | 4
EXF | dciEXF-AckExeRun:dac | DEIV | AckExeRun | RUN ORDER EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
EXF | dioEXF-CmdSelStop:dov1 | DEOV | CmdSelStop | STOP ORDER SELECT | $VOID | VES | 0 |  |  |  | 4
EXF | dciEXF-AckSelStop:dac | DEIV | AckSelStop | STOP ORDER SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
EXF | dioEXF-CmdExeStop:dov1 | DEOV | CmdExeStop | STOP ORDER EXECUTE | $VOID | VES | 0 |  |  |  | 4
EXF | dciEXF-AckExeStop:dac | DEIV | AckExeStop | STOP ORDER EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
EXF | dciEXF-StartMis:dac | DEIV | StartMis | START MISMATCH STATUS | $VOID | VEE | 0 |  |  |  | 4
EXF | dciEXF-StopMis:dac | DEIV | StopMis | STOP MISMATCH STATUS | $VOID | VEE | 0 |  |  |  | 4
SMC | dciSMC-State:dac | DEIV | State | STATE | $VOID | VEE | 0 |  |  |  | 4
SED | dciSED-State:dac | DEIV | State | STATE | $VOID | VEE | 0 |  |  |  | 4
SED | dciSED-Open:dac | DEIV | Open | OPEN ORDER SENT BY TVS | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Vac240SwOp:dac | DEIV | Vac240SwOp | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Vac240Volt:dac | DEIV | Vac240Volt | 240VAC SUPPLY VOLTAGE PRESENCE | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-VolOpen:dac | DEIV | VolOpen | VOLTAGE RELAY CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-VolFault:dac | DEIV | VolFault | VOLTAGE RELAY CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-VolSupOpen:dac | DEIV | VolSupOpen | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-VolSupFault:dac | DEIV | VolSupFault | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-CabOpen:dac | DEIV | CabOpen | CABINET SOCKETS CIRCUIT BREAKERS OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-CabFault:dac | DEIV | CabFault | CABINET SOCKETS CIRCUIT BREAKERS FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-SerOpen:dac | DEIV | SerOpen | SERVICES CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-SerFault:dac | DEIV | SerFault | SERVICES CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-UpsBreOpen:dac | DEIV | UpsBreOpen | UPS CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-UpsBreFault:dac | DEIV | UpsBreFault | UPS CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-UpsSwOpen:dac | DEIV | UpsSwOpen | UPS DISCONNECTING SWITCH OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-UpsFault:dac | DEIV | UpsFault | UPS FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Sup24Vdc1Open:dac | DEIV | Sup24Vdc1Open | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Sup24Vdc1Fault:dac | DEIV | Sup24Vdc1Fault | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Sup24Vdc1Volt:dac | DEIV | Sup24Vdc1Volt | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Sup24Vdc2Open:dac | DEIV | Sup24Vdc2Open | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Sup24Vdc2Fault:dac | DEIV | Sup24Vdc2Fault | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Sup24Vdc2Volt:dac | DEIV | Sup24Vdc2Volt | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-SwOpen:dac | DEIV | SwOpen | SWITCH CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-SwFault:dac | DEIV | SwFault | SWITCH CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-LcpOpen:dac | DEIV | LcpOpen | LCP CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-LcpFault:dac | DEIV | LcpFault | LCP CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Plc1Open:dac | DEIV | Plc1Open | PLC SUPPLY 1 CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Plc1Fault:dac | DEIV | Plc1Fault | PLC SUPPLY 1 CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Plc2Open:dac | DEIV | Plc2Open | PLC SUPPLY 2 CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Plc2Fault:dac | DEIV | Plc2Fault | PLC SUPPLY 2 CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-SuArTrig:dac | DEIV | SuArTrig | SURGE ARRESTER TRIGGERED | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Vac240SwOp:dac | DEIV | Vac240SwOp | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Vac240Volt:dac | DEIV | Vac240Volt | 240VAC SUPPLY VOLTAGE PRESENCE | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-VolOpen:dac | DEIV | VolOpen | VOLTAGE RELAY CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-VolFault:dac | DEIV | VolFault | VOLTAGE RELAY CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-VolSupOpen:dac | DEIV | VolSupOpen | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-VolSupFault:dac | DEIV | VolSupFault | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-CabOpen:dac | DEIV | CabOpen | CABINET SOCKETS CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-CabFault:dac | DEIV | CabFault | CABINET SOCKETS CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-SerOpen:dac | DEIV | SerOpen | SERVICES CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-SerFault:dac | DEIV | SerFault | SERVICES CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sup24Vdc1Open:dac | DEIV | Sup24Vdc1Open | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sup24Vdc1Fault:dac | DEIV | Sup24Vdc1Fault | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sup24Vdc1Volt:dac | DEIV | Sup24Vdc1Volt | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sup24Vdc2Open:dac | DEIV | Sup24Vdc2Open | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sup24Vdc2Fault:dac | DEIV | Sup24Vdc2Fault | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sup24Vdc2Volt:dac | DEIV | Sup24Vdc2Volt | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sw1Open:dac | DEIV | Sw1Open | SWITCH 1 CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sw1Fault:dac | DEIV | Sw1Fault | SWITCH 1 CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sw2Open:dac | DEIV | Sw2Open | SWITCH 2 CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sw2Fault:dac | DEIV | Sw2Fault | SWITCH 2 CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-PlcAOpen:dac | DEIV | PlcAOpen | PLC A CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-PlcAFault:dac | DEIV | PlcAFault | PLC A CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-PlcBOpen:dac | DEIV | PlcBOpen | PLC B CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-PlcBFault:dac | DEIV | PlcBFault | PLC B CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-SuArTrig:dac | DEIV | SuArTrig | SURGE ARRESTER TRIGGERED | $VOID | VEE | 0 |  |  |  | 4
MCB | dciMCB-McbTrip:dac | DEIV | McbTrip | Auxiliary MCB trip status | $VOID | VEE | 0 |  |  |  | 4
MCB | dciMCB-McbClose:dac | DEIV | McbClose | Auxiliary MCB closed status | $VOID | VEE | 0 |  |  |  | 4
ADS | dciADS-LoadClose:dac | DEIV | LoadClose | Load breaker switched closed | $VOID | VEE | 0 |  |  |  | 4
ADS | dciADS-LbsPos:dac | DEIV | LbsPos | LBS Auxiliary Switch racked position | $VOID | VEE | 0 |  |  |  | 4
TRF | dciTRF-EmOff:dac | DEIV | EmOff | Emergency power off | $VOID | VEE | 0 |  |  |  | 4
TRF | dciTRF-TranFault:dac | DEIV | TranFault | Transformer fault | $VOID | VEE | 0 |  |  |  | 4
TRF | dciTRF-EmCut:dac | DEIV | EmCut | Emergency power cut | $VOID | VEE | 0 |  |  |  | 4
TRF | dciTRF-PreAlarm:dac | DEIV | PreAlarm | Transformer high Temperature pre alarm | $VOID | VEE | 0 |  |  |  | 4
TRF | dciTRF-Alarm:dac | DEIV | Alarm | Transformer high Temperature Alarm | $VOID | VEE | 0 |  |  |  | 4
ACB | dciACB-Fault:dac | DEIV | Fault | Main circuit breaker fault | $VOID | VEE | 0 |  |  |  | 4
ACB | dciACB-Status:dac | DEIV | Status | Main circuit breaker open/closed status | $VOID | VEE | 0 |  |  |  | 4
ACB | dciACB-Position:dac | DEIV | Position | Main CBC ACB racked position | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mcsd1Stat:dac | DEIV | Mcsd1Stat | Power normal MCSD 1 status | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mcsd2Stat:dac | DEIV | Mcsd2Stat | Power replacement MCSD 2 status | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mcsd1pos:dac | DEIV | Mcsd1pos | MDB-01 MCSD 1 racked position | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mcsd2pos:dac | DEIV | Mcsd2pos | MDB-01 MCSD 2 racked position | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Change:dac | DEIV | Change | Change over | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-relay1:dac | DEIV | relay1 | Phase failure relay 1 | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-relay2:dac | DEIV | relay2 | Phase failure relay 2 | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Closed:dac | DEIV | Closed | MCB closed status | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Trip:dac | DEIV | Trip | MCB tripped status | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-PowerCut:dac | DEIV | PowerCut | Emergency power cut (push button) | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mccb1Stat:dac | DEIV | Mccb1Stat | MCCB 1 Incomer EL2 status | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mccb1Trip:dac | DEIV | Mccb1Trip | MCCB 1 Incomer EL2 trip | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mccb2Stat:dac | DEIV | Mccb2Stat | MCCB 2 Incomer EL2 status | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mccb2Trip:dac | DEIV | Mccb2Trip | MCCB 2 Incomer EL2 trip | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mccb3Stat:dac | DEIV | Mccb3Stat | MCCB 3 Incomer EL2 status | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mccb3Trip:dac | DEIV | Mccb3Trip | MCCB 3 Incomer EL2 trip | $VOID | VEE | 0 |  |  |  | 4
EL | dciEL-Relay:dac | DEIV | Relay | Phase failure relay | $VOID | VEE | 0 |  |  |  | 4
EL | dciEL-Isolator:dac | DEIV | Isolator | LBS Main incomer isolator status | $VOID | VEE | 0 |  |  |  | 4
EL | dciEL-Supply:dac | DEIV | Supply | UPS supply status | $VOID | VEE | 0 |  |  |  | 4
EL | dciEL-Faulty:dac | DEIV | Faulty | UPS faulty | $VOID | VEE | 0 |  |  |  | 4
EL | dciEL-Power:dac | DEIV | Power | 24VDC UPS power status | $VOID | VEE | 0 |  |  |  | 4
MCCB | dciMCCB-Trip:dac | DEIV | Trip | MCCB trip status | $VOID | VEE | 0 |  |  |  | 4
MCCB | dciMCCB-Closed:dac | DEIV | Closed | MCCB closed status | $VOID | VEE | 0 |  |  |  | 4
LBS | dciLBS-Closed:dac | DEIV | Closed | LBS closed status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Acb1Closed:dac | DEIV | Acb1Closed | Power normal ACB 1 closed | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Acb1Trip:dac | DEIV | Acb1Trip | Power normal ACB 1 tripped | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Acb2Closed:dac | DEIV | Acb2Closed | Power replacement ACB 2 closed status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Acb2Trip:dac | DEIV | Acb2Trip | Power replacement ACB 2 Triped status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Acb1Pos:dac | DEIV | Acb1Pos | MDB-01 ACB 1 racked position | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Acb2Pos:dac | DEIV | Acb2Pos | MDB-01 ACB 2 racked position | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Change:dac | DEIV | Change | Change over | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Relay1:dac | DEIV | Relay1 | Phase failure relay 1 | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Relay2:dac | DEIV | Relay2 | Phase failure relay 2 | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-McbClose:dac | DEIV | McbClose | MCB closed status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-McbTrip:dac | DEIV | McbTrip | MCB tripped status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-PowerCut:dac | DEIV | PowerCut | Emergency power cut (push button) | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Plc01Close:dac | DEIV | Plc01Close | Control cabinet MCCB PLC01 closed status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Plc01Trip:dac | DEIV | Plc01Trip | Control cabinet MCCB PLC01 on tripped status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Vsd1Close:dac | DEIV | Vsd1Close | Control cabinet MCCB VSD1 closed status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Vsd1Trip:dac | DEIV | Vsd1Trip | Control cabinet MCCB VSD1 on tripped status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Vsd2Close:dac | DEIV | Vsd2Close | Control cabinet MCCB VSD2 closed status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Vsd2Trip:dac | DEIV | Vsd2Trip | Control cabinet MCCB VSD2 on tripped status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-E1Close:dac | DEIV | E1Close | Spare E1 cabinet closed status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-E1Trip:dac | DEIV | E1Trip | Spare E1 tripped status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-E2Close:dac | DEIV | E2Close | Spare E2 cabinet closed status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-E2Trip:dac | DEIV | E2Trip | Spare E2 tripped status | $VOID | VEE | 0 |  |  |  | 4
Note on F1: HILDEBERT Rene: To be calculated from the instance List

## 4-External Variables - SIL0
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
MPLC | dciMPLC-PlcState:dac | DEIV | PlcState | PLC STATE | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-OpStatus:dac | DEIV | OpStatus | OPERATIONAL STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-PlcA:dac | DEIV | PlcA | PLC-A STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-PlcB:dac | DEIV | PlcB | PLC-B STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-AppDiff:dac | DEIV | AppDiff | APPLICATIONS ARE DIFFERENT ON THE TWO PLCS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-PwStat:dac | DEIV | PwStat | POWER SUPPLY STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-CpuStat:dac | DEIV | CpuStat | CPU MODULE STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-CrpStat:dac | DEIV | CrpStat | CRP MODULE STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComScada:dac | DEIV | ComScada | NOE MODULE COMMUNICATION [SCADA] STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComStation:dac | DEIV | ComStation | NOE MODULE COMMUNICATION [STATION PLC] STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-SdStat:dac | DEIV | SdStat | COMMUNICATION WITH SCADA STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComPea:dac | DEIV | ComPea | COMMUNICATION WITH STATION PEA-01 PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComMar1:dac | DEIV | ComMar1 | COMMUNICATION WITH STATION MAR-01 PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComMar2:dac | DEIV | ComMar2 | COMMUNICATION WITH STATION MAR-02 PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComMar3:dac | DEIV | ComMar3 | COMMUNICATION WITH STATION MAR-03 PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComMar4:dac | DEIV | ComMar4 | COMMUNICATION WITH STATION MAR-04 PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComQec:dac | DEIV | ComQec | COMMUNICATION WITH STATION QEC-01 PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComEc:dac | DEIV | ComEc | COMMUNICATION WITH STATION EC1-01 PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComQap:dac | DEIV | ComQap | COMMUNICATION WITH STATION QAP-01 PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComFxh:dac | DEIV | ComFxh | COMMUNICATION WITH STATION FXH-02 PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComPeaa:dac | DEIV | ComPeaa | COMMUNICATION WITH SHAFT PEA-0A PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComPeab:dac | DEIV | ComPeab | COMMUNICATION WITH SHAFT PEA-1B PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComMara:dac | DEIV | ComMara | COMMUNICATION WITH SHAFT MAR-0A PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComEca:dac | DEIV | ComEca | COMMUNICATION WITH SHAFT EC1-0A PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
MPLC | dciMPLC-ComQapb:dac | DEIV | ComQapb | COMMUNICATION WITH SHAFT QAP-1B PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
WTDG | aciWTDG-Counter:aac | AEIV | Counter | Watchdog Counter | $VOID | VEE | 0 |  |  |  | 4
SWI | dciSWI-SwStat:dac | DEIV | SwStat | SWITCH STATUS | $VOID | VEE | 0 |  |  |  | 4
SPLC | dciSPLC-PlcState:dac | DEIV | PlcState | PLC STATE | $VOID | VEE | 0 |  |  |  | 4
SPLC | dciSPLC-OpStatus:dac | DEIV | OpStatus | OPERATIONAL STATUS | $VOID | VEE | 0 |  |  |  | 4
SPLC | dciSPLC-PwStat:dac | DEIV | PwStat | POWER SUPPLY STATUS | $VOID | VEE | 0 |  |  |  | 4
SPLC | dciSPLC-CpuStat:dac | DEIV | CpuStat | CPU MODULE STATUS | $VOID | VEE | 0 |  |  |  | 4
SPLC | dciSPLC-CrpStat:dac | DEIV | CrpStat | CRP MODULE STATUS | $VOID | VEE | 0 |  |  |  | 4
SPLC | dciSPLC-CraStat:dac | DEIV | CraStat | CRA MODULE STATUS | $VOID | VEE | 0 |  |  |  | 4
SPLC | dciSPLC-NrpStat:dac | DEIV | NrpStat | NRP MODULE STATUS | $VOID | VEE | 0 |  |  |  | 4
SPLC | dciSPLC-ComStat:dac | DEIV | ComStat | NOE MODULE COMMUNICATION STATUS | $VOID | VEE | 0 |  |  |  | 4
SPLC | dciSPLC-IoStat:dac | DEIV | IoStat | IO MODULE STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-EmergNod:dac | DEIV | EmergNod | LOCAL FIRE PANEL EMERGENCY MODE | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-RightStat:dac | DEIV | RightStat | LOCAL FIRE PANEL RIGHT SCENARIO PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-LeftStat:dac | DEIV | LeftStat | LOCAL FIRE PANEL LEFT SCENARIO PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-Spare1:dac | DEIV | Spare1 | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-Spare2:dac | DEIV | Spare2 | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-Spare3:dac | DEIV | Spare3 | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-Spare4:dac | DEIV | Spare4 | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-Spare5:dac | DEIV | Spare5 | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-Spare6:dac | DEIV | Spare6 | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-Spare7:dac | DEIV | Spare7 | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
FMOP | dciFMOP-Spare8:dac | DEIV | Spare8 | LOCAL FIRE PANEL SPARE PUSH BUTTON STATUS | $VOID | VEE | 0 |  |  |  | 4
LCP | dciLCP-ComFaultPlc:dac | DEIV | ComFaultPlc | COMMUNICATION WITH PLC STATUS | $VOID | VEE | 0 |  |  |  | 4
LCP | dciLCP-LcpMode:dac | DEIV | LcpMode | LCP MODE | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dciVENT-OpMode:dac | DEIV | OpMode | OPERATING MODE | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dciVENT-ActMode:dac | DEIV | ActMode | ACTIVE VENTILATION MODE | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dioVENT-CmdAuto:dov1 | DEOV | CmdAuto | PLC AUTO MODE COMMAND | $VOID | VES | 0 |  |  |  | 4
VENTILATION | dioVENT-CmdSelMan:dov1 | DEOV | CmdSelMan | SCADA MANUAL MODE SELECT | $VOID | VES | 0 |  |  |  | 4
VENTILATION | dciVENT-AckSelMan:dac | DEIV | AckSelMan | SCADA MANUAL MODE SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dioVENT-CmdExeMan:dov1 | DEOV | CmdExeMan | SCADA MANUAL MODE EXECUTE | $VOID | VES | 0 |  |  |  | 4
VENTILATION | dciVENT-AckExeMan:dac | DEIV | AckExeMan | SCADA MANUAL MODE EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dioVENT-CmdSelPis:dov1 | DEOV | CmdSelPis | PISTON MODE SELECT | $VOID | VES | 0 |  |  |  | 4
VENTILATION | dciVENT-AckSelPis:dac | DEIV | AckSelPis | PISTON MODE SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dioVENT-CmdExePis:dov1 | DEOV | CmdExePis | PISTON MODE EXECUTE | $VOID | VES | 0 |  |  |  | 4
VENTILATION | dciVENT-AckExePis:dac | DEIV | AckExePis | PISTON MODE EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dioVENT-CmdSelMech:dov1 | DEOV | CmdSelMech | MECHANICAL MODE SELECT | $VOID | VES | 0 |  |  |  | 4
VENTILATION | dciVENT-AckSelMech:dac | DEIV | AckSelMech | MECHANICAL MODE SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dioVENT-CmdExeMech:dov1 | DEOV | CmdExeMech | MECHANICAL MODE EXECUTE | $VOID | VES | 0 |  |  |  | 4
VENTILATION | dciVENT-AckExeMech:dac | DEIV | AckExeMech | MECHANICAL MODE EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dioVENT-CmdExelCool:dov1 | DEOV | CmdExelCool | COOLING MODE SELECT | $VOID | VES | 0 |  |  |  | 4
VENTILATION | dciVENT-AckSelCool:dac | DEIV | AckSelCool | COOLING MODE SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
VENTILATION | dioVENT-CmdExeCool:dov1 | DEOV | CmdExeCool | COOLING MODE EXECUTE | $VOID | VES | 0 |  |  |  | 4
VENTILATION | dciVENT-AckExeCool:dac | DEIV | AckExeCool | COOLING MODE EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
EMERGENCY | dciEMERGENCY-ScenAct:dac | DEIV | ScenAct | SCENARIO ACTIVATION PROPOSAL BY TVS | $VOID | VEE | 0 |  |  |  | 4
EMERGENCY | dciEMERGENCY-ActEmerg:dac | DEIV | ActEmerg | ACTIVATION STATUS OF EMERGENCY SCENARIO | $VOID | VEE | 0 |  |  |  | 4
EMERGENCY | dioEMERGENCY-CmdSelMan:dov1 | DEOV | CmdSelMan | SCENARIO CONFIRMATION BY SCADA OPERATOR SELECT | $VOID | VES | 0 |  |  |  | 4
EMERGENCY | dciEMERGENCY-AckSelMan:dac | DEIV | AckSelMan | SCENARIO CONFIRMATION BY SCADA OPERATOR SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
EMERGENCY | dioEMERGENCY-CmdExeMan:dov1 | DEOV | CmdExeMan | SCENARIO CONFIRMATION BY SCADA OPERATOR EXECUTE | $VOID | VES | 0 |  |  |  | 4
EMERGENCY | dciEMERGENCY-AckExeMan:dac | DEIV | AckExeMan | SCENARIO CONFIRMATION BY SCADA OPERATOR EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone1:aac | AEIV | Zone1 | AVERAGE TUNNEL TEMPERATURE ZONE 1 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone2:aac | AEIV | Zone2 | AVERAGE TUNNEL TEMPERATURE ZONE 2 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone3:aac | AEIV | Zone3 | AVERAGE TUNNEL TEMPERATURE ZONE 3 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone4:aac | AEIV | Zone4 | AVERAGE TUNNEL TEMPERATURE ZONE 4 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone5:aac | AEIV | Zone5 | AVERAGE TUNNEL TEMPERATURE ZONE 5 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone6:aac | AEIV | Zone6 | AVERAGE TUNNEL TEMPERATURE ZONE 6 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone7:aac | AEIV | Zone7 | AVERAGE TUNNEL TEMPERATURE ZONE 7 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone8:aac | AEIV | Zone8 | AVERAGE TUNNEL TEMPERATURE ZONE 8 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone9:aac | AEIV | Zone9 | AVERAGE TUNNEL TEMPERATURE ZONE 9 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone10:aac | AEIV | Zone10 | AVERAGE TUNNEL TEMPERATURE ZONE 10 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone11:aac | AEIV | Zone11 | AVERAGE TUNNEL TEMPERATURE ZONE 11 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone12:aac | AEIV | Zone12 | AVERAGE TUNNEL TEMPERATURE ZONE 12 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone13:aac | AEIV | Zone13 | AVERAGE TUNNEL TEMPERATURE ZONE 13 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone14:aac | AEIV | Zone14 | AVERAGE TUNNEL TEMPERATURE ZONE 14 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-Zone15:aac | AEIV | Zone15 | AVERAGE TUNNEL TEMPERATURE ZONE 15 | $VOID | VEE | 0 |  |  |  | 4
MUL | aciMUL-OutTem:aac | AEIV | OutTem | AVERAGE OUTDOOR TEMPERATURE | $VOID | VEE | 0 |  |  |  | 4
FXL | aciFXL-Zone16:aac | AEIV | Zone16 | AVERAGE TUNNEL TEMPERATURE ZONE 16 | $VOID | VEE | 0 |  |  |  | 4
FXL | aciFXL-Zone17:aac | AEIV | Zone17 | AVERAGE TUNNEL TEMPERATURE ZONE 17 | $VOID | VEE | 0 |  |  |  | 4
FXL | aciFXL-OutTem:aac | AEIV | OutTem | AVERAGE OUTDOOR TEMPERATURE | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-SwitchStat:dac | DEIV | SwitchStat | ELECTRICAL PANEL SELECTOR SWITCH STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-OperatingMode:dac | DEIV | OperatingMode | OPERATING MODE | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-RunStatus:dac | DEIV | RunStatus | RUN STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dioTVF-CmdAuto:dov1 | DEOV | CmdAuto | SCADA AUTO MODE COMMAND | $VOID | VES | 0 |  |  |  | 4
TVF | dioTVF-CmdSelMan:dov1 | DEOV | CmdSelMan | SCADA MANUAL MODE SELECT | $VOID | VES | 0 |  |  |  | 4
TVF | dciTVF-AckSelMan:dac | DEIV | AckSelMan | SCADA MANUAL MODE SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
TVF | dioTVF-CmdExeMan:dov1 | DEOV | CmdExeMan | SCADA MANUAL MODE EXECUTE | $VOID | VES | 0 |  |  |  | 4
TVF | dciTVF-AckExeMan:dac | DEIV | AckExeMan | SCADA MANUAL MODE EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-EleStat:dac | DEIV | EleStat | VSD ELECTRICAL STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-StartStat:dac | DEIV | StartStat | VSD FAIL TO START STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-StopStat:dac | DEIV | StopStat | VSD FAIL TO STOP STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | aciTVF-SpeedFreq:aac | AEIV | SpeedFreq | VSD SPEED FREQUENCY | $VOID | VEE | 0 |  |  |  | 4
TVF | dioTVF-CmdSpeedOrd:dov1 | DEOV | CmdSpeedOrd | VSD SPEED ORDER | $VOID | VES | 0 |  |  |  | 4
TVF | dioTVF-CmdSelStop:dov1 | DEOV | CmdSelStop | STOP ORDER (VSD) SELECT | $VOID | VES | 0 |  |  |  | 4
TVF | dciTVF-AckSelStop:dac | DEIV | AckSelStop | STOP ORDER (VSD) SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
TVF | dioTVF-CmdExeStop:dov1 | DEOV | CmdExeStop | STOP ORDER (VSD) EXECUTE | $VOID | VES | 0 |  |  |  | 4
TVF | dciTVF-AckExeStop:dac | DEIV | AckExeStop | STOP ORDER (VSD) EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
TVF | dioTVF-CmdSelFwOrd:dov1 | DEOV | CmdSelFwOrd | FORWARD ORDER (VSD) SELECT | $VOID | VES | 0 |  |  |  | 4
TVF | dciTVF-AckSelFwOrd:dac | DEIV | AckSelFwOrd | FORWARD ORDER (VSD) SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
TVF | dioTVF-CmdExeFwOrd:dov1 | DEOV | CmdExeFwOrd | FORWARD ORDER (VSD) EXECUTE | $VOID | VES | 0 |  |  |  | 4
TVF | dciTVF-AckExeFwOrd:dac | DEIV | AckExeFwOrd | FORWARD ORDER (VSD) EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
TVF | dioTVF-CmdSelRvOrd:dov1 | DEOV | CmdSelRvOrd | REVERSE ORDER (VSD) SELECT | $VOID | VES | 0 |  |  |  | 4
TVF | dciTVF-AckSelRvOrd:dac | DEIV | AckSelRvOrd | REVERSE ORDER (VSD) SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
TVF | dioTVF-CmdExeRvOrd:dov1 | DEOV | CmdExeRvOrd | REVERSE ORDER (VSD) EXECUTE | $VOID | VES | 0 |  |  |  | 4
TVF | dciTVF-AckExeRvOrd:dac | DEIV | AckExeRvOrd | REVERSE ORDER (VSD) EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-AvailStat:dac | DEIV | AvailStat | FAN AVAILABILITY STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-CirPos:dac | DEIV | CirPos | CIRCUIT BREAKER POSITION | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-CirTrip:dac | DEIV | CirTrip | CIRCUIT BREAKER TRIPPED STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-FanPos:dac | DEIV | FanPos | FAN HEATER CIRCUIT BREAKER POSITION | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-FanTrip:dac | DEIV | FanTrip | FAN HEATER CIRCUIT BREAKER TRIPPED STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-ForOut:dac | DEIV | ForOut | FORWARD START-UP MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-RevOut:dac | DEIV | RevOut | REVERSE START-UP MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-StopOut:dac | DEIV | StopOut | STOP MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-WindTem:dac | DEIV | WindTem | WINDING TEMPERATURE STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-FrontTem:dac | DEIV | FrontTem | FRONT BEARING TEMPERATURE STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-RearTem:dac | DEIV | RearTem | REAR BEARING TEMPERATURE STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-Vib1:dac | DEIV | Vib1 | VIBRATION 1ST LEVEL STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-Vib2:dac | DEIV | Vib2 | VIBRATION 2ND LEVEL STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | dciTVF-More10:dac | DEIV | More10 | MORE THAN 10 STARTUP PER HOUR STATUS | $VOID | VEE | 0 |  |  |  | 4
TVF | aciTVF-RunHrs:aac | AEIV | RunHrs | RUNNING HOURS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-SwitchStat:dac | DEIV | SwitchStat | ELECTRICAL PANEL SELECTOR SWITCH STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-OperatingMode:dac | DEIV | OperatingMode | OPERATING MODE | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-RunStatus:dac | DEIV | RunStatus | RUN STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dioJET-CmdAutoCom:dov1 | DEOV | CmdAutoCom | SCADA AUTO MODE COMMAND | $VOID | VES | 0 |  |  |  | 4
JET | dioJET-CmdSelMan:dov1 | DEOV | CmdSelMan | SCADA MANUAL MODE SELECT | $VOID | VES | 0 |  |  |  | 4
JET | dciJET-AckSelMan:dac | DEIV | AckSelMan | SCADA MANUAL MODE SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
JET | dioJET-CmdExeMan:dov1 | DEOV | CmdExeMan | SCADA MANUAL MODE EXECUTE | $VOID | VES | 0 |  |  |  | 4
JET | dciJET-AckExeMan:dac | DEIV | AckExeMan | SCADA MANUAL MODE EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-EleStat:dac | DEIV | EleStat | VSD ELECTRICAL STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-FailStart:dac | DEIV | FailStart | VSD FAIL TO START STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-FailStop:dac | DEIV | FailStop | VSD FAIL TO STOP STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | aciJET-SpeedFrep:aac | AEIV | SpeedFrep | VSD SPEED FREQUENCY | $VOID | VEE | 0 |  |  |  | 4
JET | dioJET-CmdSpeedOrd:dov1 | DEOV | CmdSpeedOrd | VSD SPEED ORDER | $VOID | VES | 0 |  |  |  | 4
JET | dioJET-CmdSelStop:dov1 | DEOV | CmdSelStop | STOP ORDER (VSD) SELECT | $VOID | VES | 0 |  |  |  | 4
JET | dciJET-AckSelStop:dac | DEIV | AckSelStop | STOP ORDER (VSD) SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
JET | dioJET-CmdExeStop:dov1 | DEOV | CmdExeStop | STOP ORDER (VSD) EXECUTE | $VOID | VES | 0 |  |  |  | 4
JET | dciJET-AckExeStop:dac | DEIV | AckExeStop | STOP ORDER (VSD) EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
JET | dioJET-CmdSelFwOrd:dov1 | DEOV | CmdSelFwOrd | FORWARD ORDER (VSD) SELECT | $VOID | VES | 0 |  |  |  | 4
JET | dciJET-AckSelFwOrd:dac | DEIV | AckSelFwOrd | FORWARD ORDER (VSD) SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
JET | dioJET-CmdExeFwOrd:dov1 | DEOV | CmdExeFwOrd | FORWARD ORDER (VSD) EXECUTE | $VOID | VES | 0 |  |  |  | 4
JET | dciJET-AckExeFwOrd:dac | DEIV | AckExeFwOrd | FORWARD ORDER (VSD) EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
JET | dioJET-CmdSelRvOrd:dov1 | DEOV | CmdSelRvOrd | REVERSE ORDER (VSD) SELECT | $VOID | VES | 0 |  |  |  | 4
JET | dciJET-AckSelRvOrd:dac | DEIV | AckSelRvOrd | REVERSE ORDER (VSD) SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
JET | dioJET-CmdExeRvOrd:dov1 | DEOV | CmdExeRvOrd | REVERSE ORDER (VSD) EXECUTE | $VOID | VES | 0 |  |  |  | 4
JET | dciJET-AckExeRvOrd:dac | DEIV | AckExeRvOrd | REVERSE ORDER (VSD) EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-AvailStat:dac | DEIV | AvailStat | FAN AVAILABILITY STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-CirOpen:dac | DEIV | CirOpen | CIRCUIT BREAKER POSITION | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-CirOut:dac | DEIV | CirOut | CIRCUIT BREAKER TRIPPED STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-FanOpen:dac | DEIV | FanOpen | FAN HEATER CIRCUIT BREAKER POSITION | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-FanOut:dac | DEIV | FanOut | FAN HEATER CIRCUIT BREAKER TRIPPED STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-ForOut:dac | DEIV | ForOut | FORWARD START-UP MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-RevOut:dac | DEIV | RevOut | REVERSE START-UP MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-StopOut:dac | DEIV | StopOut | STOP MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-WindTem:dac | DEIV | WindTem | WINDING TEMPERATURE STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-FrontTem1:dac | DEIV | FrontTem1 | FRONT BEARING TEMPERATURE STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-RearTem:dac | DEIV | RearTem | REAR BEARING TEMPERATURE STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-Vib1:dac | DEIV | Vib1 | VIBRATION 1ST LEVEL STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-Vib2:dac | DEIV | Vib2 | VIBRATION 2ND LEVEL STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | dciJET-More6hr:dac | DEIV | More6hr | MORE THAN 10 STARTUP PER HOUR STATUS | $VOID | VEE | 0 |  |  |  | 4
JET | aciJET-RunHrs:aac | AEIV | RunHrs | RUNNING HOURS | $VOID | VEE | 0 |  |  |  | 4
TVD | dciTVD-SwitchStat:dac | DEIV | SwitchStat | ELECTRICAL PANEL SELECTOR SWITCH STATUS | $VOID | VEE | 0 |  |  |  | 4
TVD | dciTVD-OpMod:dac | DEIV | OpMod | OPERATING MODE | $VOID | VEE | 0 |  |  |  | 4
TVD | dciTVD-Stat:dac | DEIV | Stat | ARRAY STATUS | $VOID | VEE | 0 |  |  |  | 4
TVD | dioTVD-CmdAuto:dov1 | DEOV | CmdAuto | SCADA AUTO MODE COMMAND | $VOID | VES | 0 |  |  |  | 4
TVD | dioTVD-CmdSelMan:dov1 | DEOV | CmdSelMan | SCADA MANUAL MODE SELECT | $VOID | VES | 0 |  |  |  | 4
TVD | dciTVD-AckSelMan:dac | DEIV | AckSelMan | SCADA MANUAL MODE SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
TVD | dioTVD-CmdExeMan:dov1 | DEOV | CmdExeMan | SCADA MANUAL MODE EXECUTE | $VOID | VES | 0 |  |  |  | 4
TVD | dciTVD-AckExeMan:dac | DEIV | AckExeMan | SCADA MANUAL MODE EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
TVD | dioTVD-CmdSelOpen:dov1 | DEOV | CmdSelOpen | OPEN ORDER SELECT | $VOID | VES | 0 |  |  |  | 4
TVD | dciTVD-AckSelOpen:dac | DEIV | AckSelOpen | OPEN ORDER SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
TVD | dioTVD-CmdExeOpen:dov1 | DEOV | CmdExeOpen | OPEN ORDER EXECUTE | $VOID | VES | 0 |  |  |  | 4
TVD | dciTVD-AckExeOpen:dac | DEIV | AckExeOpen | OPEN ORDER EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
TVD | dioTVD-CmdSelClose:dov1 | DEOV | CmdSelClose | CLOSE ORDER SELECT | $VOID | VES | 0 |  |  |  | 4
TVD | dciTVD-AckSelClose:dac | DEIV | AckSelClose | CLOSE ORDER SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
TVD | dioTVD-CmdExeClose:dov1 | DEOV | CmdExeClose | CLOSE ORDER EXECUTE | $VOID | VES | 0 |  |  |  | 4
TVD | dciTVD-AckExeClose:dac | DEIV | AckExeClose | CLOSE ORDER EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
TVD | dciTVD-DamOpen:dac | DEIV | DamOpen | DAMPER SUPPLY CIRCUIT BREAKER POSITION | $VOID | VEE | 0 |  |  |  | 4
TVD | dciTVD-DamOut:dac | DEIV | DamOut | DAMPER SUPPLY CIRCUIT BREAKER TRIPPED STATUS | $VOID | VEE | 0 |  |  |  | 4
TVD | dciTVD-FailOpen:dac | DEIV | FailOpen | OPEN MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
TVD | dciTVD-FailClose:dac | DEIV | FailClose | CLOSE MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
IDP | dciIDP-SwitchStat:dac | DEIV | SwitchStat | ELECTRICAL PANEL SELECTOR SWITCH STATUS | $VOID | VEE | 0 |  |  |  | 4
IDP | dciIDP-Stat:dac | DEIV | Stat | ARRAY STATUS | $VOID | VEE | 0 |  |  |  | 4
IDP | dciIDP-CloseStat:dac | DEIV | CloseStat | DAMPER SUPPLY CIRCUIT BREAKER POSITION | $VOID | VEE | 0 |  |  |  | 4
IDP | dciIDP-TripStat:dac | DEIV | TripStat | DAMPER SUPPLY CIRCUIT BREAKER TRIPPED STATUS | $VOID | VEE | 0 |  |  |  | 4
IDP | dciIDP-FailOpen:dac | DEIV | FailOpen | OPEN MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
IDP | dciIDP-FailClose:dac | DEIV | FailClose | CLOSE MISMATCH OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
MSFD | dciMSFD-Stat:dac | DEIV | Stat | ARRAY STATUS | $VOID | VEE | 0 |  |  |  | 4
MSFD | dciMSFD-CloseStat:dac | DEIV | CloseStat | DAMPER SUPPLY CIRCUIT BREAKER POSITION | $VOID | VEE | 0 |  |  |  | 4
MSFD | dciMSFD-TripStat:dac | DEIV | TripStat | DAMPER SUPPLY CIRCUIT BREAKER TRIPPED STATUS | $VOID | VEE | 0 |  |  |  | 4
MSFD | dciMSFD-LocalMod:dac | DEIV | LocalMod | LOCAL MODE STATUS | $VOID | VEE | 0 |  |  |  | 4
OTS | dciOTS-AvailStat:dac | DEIV | AvailStat | AVAILABILITY STATUS | $VOID | VEE | 0 |  |  |  | 4
OTS | dciOTS-SenOut:dac | DEIV | SenOut | TEMPERATURE OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
OTS | dciOTS-AveTem:dac | DEIV | AveTem | AVERAGE TEMPERATURE EXCLUSION STATUS | $VOID | VEE | 0 |  |  |  | 4
OTS | aciOTS-TemMeasure:aac | AEIV | TemMeasure | TEMPERATURE MEASUREMENT | $VOID | VEE | 0 |  |  |  | 4
TTS | dciTTS-Availability:dac | DEIV | Availability | AVAILABILITY STATUS | $VOID | VEE | 0 |  |  |  | 4
TTS | dciTTS-TemOut:dac | DEIV | TemOut | TEMPERATURE SENSOR OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
TTS | dciTTS-HumOut:dac | DEIV | HumOut | HUMIDITY SENSOR OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
TTS | dciTTS-AveTem:dac | DEIV | AveTem | AVERAGE TEMPERATURE EXCLUSION STATUS | $VOID | VEE | 0 |  |  |  | 4
TTS | aciTTS-Temperature:aac | AEIV | Temperature | TEMPERATURE MEASUREMENT | $VOID | VEE | 0 |  |  |  | 4
TTS | aciTTS-Humidity:aac | AEIV | Humidity | HUMIDITY MEASUREMENT | $VOID | VEE | 0 |  |  |  | 4
VS | dciVS-Availability:dac | DEIV | Availability | AVAILABILITY STATUS | $VOID | VEE | 0 |  |  |  | 4
VS | dciVS-SenStat:dac | DEIV | SenStat | SENSOR OUTAGE STATUS | $VOID | VEE | 0 |  |  |  | 4
VS | aciVS-Velocity:aac | AEIV | Velocity | VELOCITY MEASUREMENT | $VOID | VEE | 0 |  |  |  | 4
AHU | dciAHU-ControlMod:dac | DEIV | ControlMod | CONTROL MODE | $VOID | VEE | 0 |  |  |  | 4
AHU | dciAHU-RunStat:dac | DEIV | RunStat | RUN STATUS | $VOID | VEE | 0 |  |  |  | 4
PFA | dciPFA-ControlMod:dac | DEIV | ControlMod | CONTROL MODE | $VOID | VEE | 0 |  |  |  | 4
PFA | dciPFA-OpMode:dac | DEIV | OpMode | OPERATING MODE | $VOID | VEE | 0 |  |  |  | 4
PFA | dciPFA-RunStat:dac | DEIV | RunStat | RUN STATUS | $VOID | VEE | 0 |  |  |  | 4
PFA | dioPFA-CmdAuto:dov1 | DEOV | CmdAuto | SCADA AUTO MODE COMMAND | $VOID | VES | 0 |  |  |  | 4
PFA | dioPFA-CmdSelMan:dov1 | DEOV | CmdSelMan | SCADA MANUAL MODE SELECT | $VOID | VES | 0 |  |  |  | 4
PFA | dciPFA-AckSelMan:dac | DEIV | AckSelMan | SCADA MANUAL MODE SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
PFA | dioPFA-CmdExeMan:dov1 | DEOV | CmdExeMan | SCADA MANUAL MODE EXECUTE | $VOID | VES | 0 |  |  |  | 4
PFA | dciPFA-AckExeMan:dac | DEIV | AckExeMan | SCADA MANUAL MODE EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
PFA | dioPFA-CmdSelRun:dov1 | DEOV | CmdSelRun | RUN ORDER SELECT | $VOID | VES | 0 |  |  |  | 4
PFA | dciPFA-AckSelRun:dac | DEIV | AckSelRun | RUN ORDER SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
PFA | dioPFA-CmdExeRun:dov1 | DEOV | CmdExeRun | RUN ORDER EXECUTE | $VOID | VES | 0 |  |  |  | 4
PFA | dciPFA-AckExeRun:dac | DEIV | AckExeRun | RUN ORDER EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
PFA | dioPFA-CmdSelStop:dov1 | DEOV | CmdSelStop | STOP ORDER SELECT | $VOID | VES | 0 |  |  |  | 4
PFA | dciPFA-AckSelStop:dac | DEIV | AckSelStop | STOP ORDER SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
PFA | dioPFA-CmdExeStop:dov1 | DEOV | CmdExeStop | STOP ORDER EXECUTE | $VOID | VES | 0 |  |  |  | 4
PFA | dciPFA-AckExeStop:dac | DEIV | AckExeStop | STOP ORDER EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
PFA | dciPFA-StartMis:dac | DEIV | StartMis | START MISMATCH STATUS | $VOID | VEE | 0 |  |  |  | 4
PFA | dciPFA-StopMis:dac | DEIV | StopMis | STOP MISMATCH STATUS | $VOID | VEE | 0 |  |  |  | 4
EXF | dciEXF-ControlMod:dac | DEIV | ControlMod | CONTROL MODE | $VOID | VEE | 0 |  |  |  | 4
EXF | dciEXF-OpMode:dac | DEIV | OpMode | OPERATING MODE | $VOID | VEE | 0 |  |  |  | 4
EXF | dciEXF-AutoCom:dac | DEIV | AutoCom | RUN STATUS | $VOID | VEE | 0 |  |  |  | 4
EXF | dioEXF-CmdMan:dov1 | DEOV | CmdMan | SCADA AUTO MODE COMMAND | $VOID | VES | 0 |  |  |  | 4
EXF | dioEXF-CmdSelMan:dov1 | DEOV | CmdSelMan | SCADA MANUAL MODE SELECT | $VOID | VES | 0 |  |  |  | 4
EXF | dciEXF-AckSelMan:dac | DEIV | AckSelMan | SCADA MANUAL MODE SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
EXF | dioEXF-CmdExeMan:dov1 | DEOV | CmdExeMan | SCADA MANUAL MODE EXECUTE | $VOID | VES | 0 |  |  |  | 4
EXF | dciEXF-AckExeMan:dac | DEIV | AckExeMan | SCADA MANUAL MODE EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
EXF | dioEXF-CmdSelRun:dov1 | DEOV | CmdSelRun | RUN ORDER SELECT | $VOID | VES | 0 |  |  |  | 4
EXF | dciEXF-AckSelRun:dac | DEIV | AckSelRun | RUN ORDER SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
EXF | dioEXF-CmdExeRun:dov1 | DEOV | CmdExeRun | RUN ORDER EXECUTE | $VOID | VES | 0 |  |  |  | 4
EXF | dciEXF-AckExeRun:dac | DEIV | AckExeRun | RUN ORDER EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
EXF | dioEXF-CmdSelStop:dov1 | DEOV | CmdSelStop | STOP ORDER SELECT | $VOID | VES | 0 |  |  |  | 4
EXF | dciEXF-AckSelStop:dac | DEIV | AckSelStop | STOP ORDER SELECT ACK | $VOID | VEE | 0 |  |  |  | 4
EXF | dioEXF-CmdExeStop:dov1 | DEOV | CmdExeStop | STOP ORDER EXECUTE | $VOID | VES | 0 |  |  |  | 4
EXF | dciEXF-AckExeStop:dac | DEIV | AckExeStop | STOP ORDER EXECUTE ACK | $VOID | VEE | 0 |  |  |  | 4
EXF | dciEXF-StartMis:dac | DEIV | StartMis | START MISMATCH STATUS | $VOID | VEE | 0 |  |  |  | 4
EXF | dciEXF-StopMis:dac | DEIV | StopMis | STOP MISMATCH STATUS | $VOID | VEE | 0 |  |  |  | 4
SMC | dciSMC-State:dac | DEIV | State | STATE | $VOID | VEE | 0 |  |  |  | 4
SED | dciSED-State:dac | DEIV | State | STATE | $VOID | VEE | 0 |  |  |  | 4
SED | dciSED-Open:dac | DEIV | Open | OPEN ORDER SENT BY TVS | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Vac240SwOp:dac | DEIV | Vac240SwOp | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Vac240Volt:dac | DEIV | Vac240Volt | 240VAC SUPPLY VOLTAGE PRESENCE | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-VolOpen:dac | DEIV | VolOpen | VOLTAGE RELAY CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-VolFault:dac | DEIV | VolFault | VOLTAGE RELAY CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-VolSupOpen:dac | DEIV | VolSupOpen | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-VolSupFault:dac | DEIV | VolSupFault | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-CabOpen:dac | DEIV | CabOpen | CABINET SOCKETS CIRCUIT BREAKERS OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-CabFault:dac | DEIV | CabFault | CABINET SOCKETS CIRCUIT BREAKERS FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-SerOpen:dac | DEIV | SerOpen | SERVICES CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-SerFault:dac | DEIV | SerFault | SERVICES CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-UpsBreOpen:dac | DEIV | UpsBreOpen | UPS CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-UpsBreFault:dac | DEIV | UpsBreFault | UPS CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-UpsSwOpen:dac | DEIV | UpsSwOpen | UPS DISCONNECTING SWITCH OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-UpsFault:dac | DEIV | UpsFault | UPS FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Sup24Vdc1Open:dac | DEIV | Sup24Vdc1Open | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Sup24Vdc1Fault:dac | DEIV | Sup24Vdc1Fault | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Sup24Vdc1Volt:dac | DEIV | Sup24Vdc1Volt | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Sup24Vdc2Open:dac | DEIV | Sup24Vdc2Open | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Sup24Vdc2Fault:dac | DEIV | Sup24Vdc2Fault | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Sup24Vdc2Volt:dac | DEIV | Sup24Vdc2Volt | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-SwOpen:dac | DEIV | SwOpen | SWITCH CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-SwFault:dac | DEIV | SwFault | SWITCH CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-LcpOpen:dac | DEIV | LcpOpen | LCP CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-LcpFault:dac | DEIV | LcpFault | LCP CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Plc1Open:dac | DEIV | Plc1Open | PLC SUPPLY 1 CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Plc1Fault:dac | DEIV | Plc1Fault | PLC SUPPLY 1 CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Plc2Open:dac | DEIV | Plc2Open | PLC SUPPLY 2 CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-Plc2Fault:dac | DEIV | Plc2Fault | PLC SUPPLY 2 CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
SPLCMMS | dciSPLM-SuArTrig:dac | DEIV | SuArTrig | SURGE ARRESTER TRIGGERED | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Vac240SwOp:dac | DEIV | Vac240SwOp | 240VAC SUPPLY DISCONNECTING SWITCH - OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Vac240Volt:dac | DEIV | Vac240Volt | 240VAC SUPPLY VOLTAGE PRESENCE | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-VolOpen:dac | DEIV | VolOpen | VOLTAGE RELAY CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-VolFault:dac | DEIV | VolFault | VOLTAGE RELAY CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-VolSupOpen:dac | DEIV | VolSupOpen | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-VolSupFault:dac | DEIV | VolSupFault | VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-CabOpen:dac | DEIV | CabOpen | CABINET SOCKETS CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-CabFault:dac | DEIV | CabFault | CABINET SOCKETS CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-SerOpen:dac | DEIV | SerOpen | SERVICES CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-SerFault:dac | DEIV | SerFault | SERVICES CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sup24Vdc1Open:dac | DEIV | Sup24Vdc1Open | SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sup24Vdc1Fault:dac | DEIV | Sup24Vdc1Fault | SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sup24Vdc1Volt:dac | DEIV | Sup24Vdc1Volt | SUPPLY 24VDC 1 ABSENCE OF VOLTAGE | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sup24Vdc2Open:dac | DEIV | Sup24Vdc2Open | SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sup24Vdc2Fault:dac | DEIV | Sup24Vdc2Fault | SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sup24Vdc2Volt:dac | DEIV | Sup24Vdc2Volt | SUPPLY 24VDC 2 ABSENCE OF VOLTAGE | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sw1Open:dac | DEIV | Sw1Open | SWITCH 1 CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sw1Fault:dac | DEIV | Sw1Fault | SWITCH 1 CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sw2Open:dac | DEIV | Sw2Open | SWITCH 2 CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-Sw2Fault:dac | DEIV | Sw2Fault | SWITCH 2 CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-PlcAOpen:dac | DEIV | PlcAOpen | PLC A CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-PlcAFault:dac | DEIV | PlcAFault | PLC A CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-PlcBOpen:dac | DEIV | PlcBOpen | PLC B CIRCUIT BREAKER OPEN | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-PlcBFault:dac | DEIV | PlcBFault | PLC B CIRCUIT BREAKER FAULT | $VOID | VEE | 0 |  |  |  | 4
MPLCMMS | dciMPLM-SuArTrig:dac | DEIV | SuArTrig | SURGE ARRESTER TRIGGERED | $VOID | VEE | 0 |  |  |  | 4
MCB | dciMCB-McbTrip:dac | DEIV | McbTrip | Auxiliary MCB trip status | $VOID | VEE | 0 |  |  |  | 4
MCB | dciMCB-McbClose:dac | DEIV | McbClose | Auxiliary MCB closed status | $VOID | VEE | 0 |  |  |  | 4
ADS | dciADS-LoadClose:dac | DEIV | LoadClose | Load breaker switched closed | $VOID | VEE | 0 |  |  |  | 4
ADS | dciADS-LbsPos:dac | DEIV | LbsPos | LBS Auxiliary Switch racked position | $VOID | VEE | 0 |  |  |  | 4
TRF | dciTRF-EmOff:dac | DEIV | EmOff | Emergency power off | $VOID | VEE | 0 |  |  |  | 4
TRF | dciTRF-TranFault:dac | DEIV | TranFault | Transformer fault | $VOID | VEE | 0 |  |  |  | 4
TRF | dciTRF-EmCut:dac | DEIV | EmCut | Emergency power cut | $VOID | VEE | 0 |  |  |  | 4
TRF | dciTRF-PreAlarm:dac | DEIV | PreAlarm | Transformer high Temperature pre alarm | $VOID | VEE | 0 |  |  |  | 4
TRF | dciTRF-Alarm:dac | DEIV | Alarm | Transformer high Temperature Alarm | $VOID | VEE | 0 |  |  |  | 4
ACB | dciACB-Fault:dac | DEIV | Fault | Main circuit breaker fault | $VOID | VEE | 0 |  |  |  | 4
ACB | dciACB-Status:dac | DEIV | Status | Main circuit breaker open/closed status | $VOID | VEE | 0 |  |  |  | 4
ACB | dciACB-Position:dac | DEIV | Position | Main CBC ACB racked position | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mcsd1Stat:dac | DEIV | Mcsd1Stat | Power normal MCSD 1 status | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mcsd2Stat:dac | DEIV | Mcsd2Stat | Power replacement MCSD 2 status | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mcsd1pos:dac | DEIV | Mcsd1pos | MDB-01 MCSD 1 racked position | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mcsd2pos:dac | DEIV | Mcsd2pos | MDB-01 MCSD 2 racked position | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Change:dac | DEIV | Change | Change over | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-relay1:dac | DEIV | relay1 | Phase failure relay 1 | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-relay2:dac | DEIV | relay2 | Phase failure relay 2 | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Closed:dac | DEIV | Closed | MCB closed status | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Trip:dac | DEIV | Trip | MCB tripped status | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-PowerCut:dac | DEIV | PowerCut | Emergency power cut (push button) | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mccb1Stat:dac | DEIV | Mccb1Stat | MCCB 1 Incomer EL2 status | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mccb1Trip:dac | DEIV | Mccb1Trip | MCCB 1 Incomer EL2 trip | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mccb2Stat:dac | DEIV | Mccb2Stat | MCCB 2 Incomer EL2 status | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mccb2Trip:dac | DEIV | Mccb2Trip | MCCB 2 Incomer EL2 trip | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mccb3Stat:dac | DEIV | Mccb3Stat | MCCB 3 Incomer EL2 status | $VOID | VEE | 0 |  |  |  | 4
MDB | dciMDB-Mccb3Trip:dac | DEIV | Mccb3Trip | MCCB 3 Incomer EL2 trip | $VOID | VEE | 0 |  |  |  | 4
EL | dciEL-Relay:dac | DEIV | Relay | Phase failure relay | $VOID | VEE | 0 |  |  |  | 4
EL | dciEL-Isolator:dac | DEIV | Isolator | LBS Main incomer isolator status | $VOID | VEE | 0 |  |  |  | 4
EL | dciEL-Supply:dac | DEIV | Supply | UPS supply status | $VOID | VEE | 0 |  |  |  | 4
EL | dciEL-Faulty:dac | DEIV | Faulty | UPS faulty | $VOID | VEE | 0 |  |  |  | 4
EL | dciEL-Power:dac | DEIV | Power | 24VDC UPS power status | $VOID | VEE | 0 |  |  |  | 4
MCCB | dciMCCB-Trip:dac | DEIV | Trip | MCCB trip status | $VOID | VEE | 0 |  |  |  | 4
MCCB | dciMCCB-Closed:dac | DEIV | Closed | MCCB closed status | $VOID | VEE | 0 |  |  |  | 4
LBS | dciLBS-Closed:dac | DEIV | Closed | LBS closed status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Acb1Closed:dac | DEIV | Acb1Closed | Power normal ACB 1 closed | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Acb1Trip:dac | DEIV | Acb1Trip | Power normal ACB 1 tripped | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Acb2Closed:dac | DEIV | Acb2Closed | Power replacement ACB 2 closed status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Acb2Trip:dac | DEIV | Acb2Trip | Power replacement ACB 2 Triped status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Acb1Pos:dac | DEIV | Acb1Pos | MDB-01 ACB 1 racked position | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Acb2Pos:dac | DEIV | Acb2Pos | MDB-01 ACB 2 racked position | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Change:dac | DEIV | Change | Change over | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Relay1:dac | DEIV | Relay1 | Phase failure relay 1 | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Relay2:dac | DEIV | Relay2 | Phase failure relay 2 | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-McbClose:dac | DEIV | McbClose | MCB closed status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-McbTrip:dac | DEIV | McbTrip | MCB tripped status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-PowerCut:dac | DEIV | PowerCut | Emergency power cut (push button) | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Plc01Close:dac | DEIV | Plc01Close | Control cabinet MCCB PLC01 closed status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Plc01Trip:dac | DEIV | Plc01Trip | Control cabinet MCCB PLC01 on tripped status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Vsd1Close:dac | DEIV | Vsd1Close | Control cabinet MCCB VSD1 closed status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Vsd1Trip:dac | DEIV | Vsd1Trip | Control cabinet MCCB VSD1 on tripped status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Vsd2Close:dac | DEIV | Vsd2Close | Control cabinet MCCB VSD2 closed status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-Vsd2Trip:dac | DEIV | Vsd2Trip | Control cabinet MCCB VSD2 on tripped status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-E1Close:dac | DEIV | E1Close | Spare E1 cabinet closed status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-E1Trip:dac | DEIV | E1Trip | Spare E1 tripped status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-E2Close:dac | DEIV | E2Close | Spare E2 cabinet closed status | $VOID | VEE | 0 |  |  |  | 4
SMDB | dciSMDB-E2Trip:dac | DEIV | E2Trip | Spare E2 tripped status | $VOID | VEE | 0 |  |  |  | 4
Note on F1: HILDEBERT Rene: To be calculated from the instance List

## 4-External Variables - SIL2MON
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
Note on F1: HILDEBERT Rene: To be calculated from the instance List

## 4-External Variables - SIL2CON
Class name | iopath | vetype | ve_basename | description | address | EVGroup | deadband | Range Min value | Range Max value | functTrans | length | PTP Classes Test | PTP Instances Test | isAComment
Note on F1: HILDEBERT Rene: To be calculated from the instance List

## 10-PLC Points
row_id | concentrator | location | sub_location | class_name | eqp_name | instance_id | attribute_code | sil_channel | operation_type | point_address | start_bit | nb_bits | Warning | Error | PRTU Name | SWC Name | Daccom Source File | Daccom Variable Type | FC Code / ASDU Type | Daccom Type Num | Protocol Address | Start Bit | Nb Bits | Daccom External Variable Name | field1 | field2 | field3 | field4 | field5 | External Var Comment
1 | EC101_RTU | TUN:EC101 | SCR | LCP | LCP01 | 1 | ComFaultPlc | SIL0 | MODBUS:4:Read:Input Registers | 20011 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20011 | 0 | 1 | deiTUNEC101SCRLCP01ComFaultPlc | 4 |  |  | 0 | $ComStatus , , | #COMMUNICATION FAULT WITH PLC
2 | EC101_RTU | TUN:EC101 | SCR | LCP | LCP01 | 1 | LcpMode | SIL0 | MODBUS:4:Read:Input Registers | 20011 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20011 | 1 | 1 | deiTUNEC101SCRLCP01LcpMode | 4 |  |  | 0 | $ComStatus , , | #LOCAL / REMOTE STATUS
3 | EC101_RTU | TUN:EC101 | SCR | FMOP | FMOP01 | 2 | EmergNod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20021 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20021 | 0 | 1 | deiTUNEC101SCRFMOP01EmergNod | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
4 | EC101_RTU | TUN:EC101 | SCR | FMOP | FMOP01 | 2 | RightStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20021 | 1 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20021 | 1 | 1 | deiTUNEC101SCRFMOP01RightStat | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
5 | EC101_RTU | TUN:EC101 | SCR | FMOP | FMOP01 | 2 | LeftStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20021 | 2 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20021 | 2 | 1 | deiTUNEC101SCRFMOP01LeftStat | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
6 | EC101_RTU | TUN:EC101 | TEL | SPLC | PLC01 | 3 | PlcState | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 0 | 1 | deiTUNEC101TELPLC01PlcState | 4 |  |  | 0 | $ComStatus , , | #PLC A/B OFFLINE
7 | EC101_RTU | TUN:EC101 | TEL | SPLC | PLC01 | 3 | OpStatus | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 1 | 1 | deiTUNEC101TELPLC01OpStatus | 4 |  |  | 0 | $ComStatus , , | #PLC RUNNING.
8 | EC101_RTU | TUN:EC101 | TEL | SPLC | PLC01 | 3 | PwStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 2 | 1 | deiTUNEC101TELPLC01PwStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: POWER SUPPLY FAULT
9 | EC101_RTU | TUN:EC101 | TEL | SPLC | PLC01 | 3 | CpuStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 3 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 3 | 1 | deiTUNEC101TELPLC01CpuStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CPU MODULE FAULT
10 | EC101_RTU | TUN:EC101 | TEL | SPLC | PLC01 | 3 | CrpStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 4 | 1 | deiTUNEC101TELPLC01CrpStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CRP MODULE FAULT
11 | EC101_RTU | TUN:EC101 | TEL | SPLC | PLC01 | 3 | CraStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 5 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 5 | 1 | deiTUNEC101TELPLC01CraStat | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
12 | EC101_RTU | TUN:EC101 | TEL | SPLC | PLC01 | 3 | NrpStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 6 | 1 | deiTUNEC101TELPLC01NrpStat | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
13 | EC101_RTU | TUN:EC101 | TEL | SPLC | PLC01 | 3 | ComStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 7 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 7 | 1 | deiTUNEC101TELPLC01ComStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
14 | EC101_RTU | TUN:EC101 | TEL | SPLC | PLC01 | 3 | IoStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 8 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 8 | 1 | deiTUNEC101TELPLC01IoStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
15 | EC101_RTU | TUN:EC101 | TEL | SWI | SWI01 | 4 | SwStat | SIL0 | MODBUS:4:Read:Input Registers | 20041 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20041 | 0 | 1 | deiTUNEC101TELSWI01SwStat | 4 |  |  | 0 | $ComStatus , , | #SWITCH FAULT
16 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 5 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20051 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20051 | 0 | 1 | deiTUNEC101WS01PFACON-06ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
17 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 5 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20051 | 2 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20051 | 2 | 1 | deiTUNEC101WS01PFACON-06OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
18 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 5 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20051 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20051 | 4 | 1 | deiTUNEC101WS01PFACON-06AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
19 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 5 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10101 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10101 | 0 | 1 | deoTUNEC101WS01PFACON-06CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
20 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 5 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10102 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10102 | 0 | 1 | deoTUNEC101WS01PFACON-06CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
21 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 5 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 6 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 6 | 2 | deiTUNEC101WS01PFACON-06AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
22 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 5 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10103 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10103 | 0 | 1 | deoTUNEC101WS01PFACON-06CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
23 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 5 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 8 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 8 | 2 | deiTUNEC101WS01PFACON-06AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
24 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 5 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10104 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10104 | 0 | 1 | deoTUNEC101WS01PFACON-06CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
25 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 5 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 10 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 10 | 2 | deiTUNEC101WS01PFACON-06AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
26 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 5 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10105 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10105 | 0 | 1 | deoTUNEC101WS01PFACON-06CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
27 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 5 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 12 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 12 | 2 | deiTUNEC101WS01PFACON-06AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
28 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 5 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10106 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10106 | 0 | 1 | deoTUNEC101WS01PFACON-06CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
29 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 5 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 14 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 14 | 2 | deiTUNEC101WS01PFACON-06AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
30 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 5 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10107 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10107 | 0 | 1 | deoTUNEC101WS01PFACON-06CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
31 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 5 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20052 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20052 | 0 | 2 | deiTUNEC101WS01PFACON-06AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
32 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 5 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20052 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20052 | 2 | 1 | deiTUNEC101WS01PFACON-06StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
33 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-06 | 5 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20052 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20052 | 4 | 1 | deiTUNEC101WS01PFACON-06StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
34 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 6 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20061 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20061 | 0 | 1 | deiTUNEC101WS01PFAGRD-01ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
35 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 6 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20061 | 2 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20061 | 2 | 1 | deiTUNEC101WS01PFAGRD-01OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
36 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 6 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20061 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20061 | 4 | 1 | deiTUNEC101WS01PFAGRD-01AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
37 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 6 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10121 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10121 | 0 | 1 | deoTUNEC101WS01PFAGRD-01CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
38 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 6 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10122 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10122 | 0 | 1 | deoTUNEC101WS01PFAGRD-01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
39 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 6 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 6 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 6 | 2 | deiTUNEC101WS01PFAGRD-01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
40 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 6 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10123 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10123 | 0 | 1 | deoTUNEC101WS01PFAGRD-01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
41 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 6 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 8 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 8 | 2 | deiTUNEC101WS01PFAGRD-01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
42 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 6 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10124 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10124 | 0 | 1 | deoTUNEC101WS01PFAGRD-01CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
43 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 6 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 10 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 10 | 2 | deiTUNEC101WS01PFAGRD-01AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
44 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 6 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10125 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10125 | 0 | 1 | deoTUNEC101WS01PFAGRD-01CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
45 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 6 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 12 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 12 | 2 | deiTUNEC101WS01PFAGRD-01AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
46 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 6 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10126 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10126 | 0 | 1 | deoTUNEC101WS01PFAGRD-01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
47 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 6 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 14 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 14 | 2 | deiTUNEC101WS01PFAGRD-01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
48 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 6 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10127 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10127 | 0 | 1 | deoTUNEC101WS01PFAGRD-01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
49 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 6 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20062 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20062 | 0 | 2 | deiTUNEC101WS01PFAGRD-01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
50 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 6 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20062 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20062 | 2 | 1 | deiTUNEC101WS01PFAGRD-01StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
51 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | GRD-01 | 6 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20062 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20062 | 4 | 1 | deiTUNEC101WS01PFAGRD-01StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
52 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 7 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20071 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20071 | 0 | 1 | deiTUNEC101ES01PFACON-03ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
53 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 7 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20071 | 2 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20071 | 2 | 1 | deiTUNEC101ES01PFACON-03OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
54 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 7 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20071 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20071 | 4 | 1 | deiTUNEC101ES01PFACON-03AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
55 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 7 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10141 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10141 | 0 | 1 | deoTUNEC101ES01PFACON-03CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
56 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 7 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10142 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10142 | 0 | 1 | deoTUNEC101ES01PFACON-03CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
57 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 7 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 6 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 6 | 2 | deiTUNEC101ES01PFACON-03AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
58 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 7 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10143 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10143 | 0 | 1 | deoTUNEC101ES01PFACON-03CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
59 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 7 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 8 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 8 | 2 | deiTUNEC101ES01PFACON-03AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
60 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 7 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10144 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10144 | 0 | 1 | deoTUNEC101ES01PFACON-03CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
61 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 7 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 10 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 10 | 2 | deiTUNEC101ES01PFACON-03AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
62 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 7 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10145 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10145 | 0 | 1 | deoTUNEC101ES01PFACON-03CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
63 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 7 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 12 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 12 | 2 | deiTUNEC101ES01PFACON-03AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
64 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 7 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10146 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10146 | 0 | 1 | deoTUNEC101ES01PFACON-03CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
65 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 7 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 14 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 14 | 2 | deiTUNEC101ES01PFACON-03AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
66 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 7 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10147 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10147 | 0 | 1 | deoTUNEC101ES01PFACON-03CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
67 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 7 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20072 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20072 | 0 | 2 | deiTUNEC101ES01PFACON-03AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
68 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 7 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20072 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20072 | 2 | 1 | deiTUNEC101ES01PFACON-03StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
69 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-03 | 7 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20072 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20072 | 4 | 1 | deiTUNEC101ES01PFACON-03StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
70 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 8 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20081 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20081 | 0 | 1 | deiTUNEC101ES01PFACON-04ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
71 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 8 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20081 | 2 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20081 | 2 | 1 | deiTUNEC101ES01PFACON-04OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
72 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 8 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20081 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20081 | 4 | 1 | deiTUNEC101ES01PFACON-04AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
73 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 8 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10161 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10161 | 0 | 1 | deoTUNEC101ES01PFACON-04CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
74 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 8 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10162 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10162 | 0 | 1 | deoTUNEC101ES01PFACON-04CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
75 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 8 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 6 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 6 | 2 | deiTUNEC101ES01PFACON-04AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
76 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 8 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10163 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10163 | 0 | 1 | deoTUNEC101ES01PFACON-04CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
77 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 8 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 8 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 8 | 2 | deiTUNEC101ES01PFACON-04AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
78 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 8 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10164 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10164 | 0 | 1 | deoTUNEC101ES01PFACON-04CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
79 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 8 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 10 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 10 | 2 | deiTUNEC101ES01PFACON-04AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
80 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 8 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10165 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10165 | 0 | 1 | deoTUNEC101ES01PFACON-04CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
81 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 8 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 12 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 12 | 2 | deiTUNEC101ES01PFACON-04AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
82 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 8 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10166 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10166 | 0 | 1 | deoTUNEC101ES01PFACON-04CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
83 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 8 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 14 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 14 | 2 | deiTUNEC101ES01PFACON-04AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
84 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 8 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10167 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10167 | 0 | 1 | deoTUNEC101ES01PFACON-04CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
85 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 8 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20082 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20082 | 0 | 2 | deiTUNEC101ES01PFACON-04AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
86 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 8 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20082 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20082 | 2 | 1 | deiTUNEC101ES01PFACON-04StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
87 | EC101_RTU | TUN:EC101 | ES01:PFA | PFA | CON-04 | 8 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20082 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20082 | 4 | 1 | deiTUNEC101ES01PFACON-04StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
88 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 9 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20091 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20091 | 0 | 1 | deiTUNEC101WS01PFACON-07ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
89 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 9 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20091 | 2 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20091 | 2 | 1 | deiTUNEC101WS01PFACON-07OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
90 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 9 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20091 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20091 | 4 | 1 | deiTUNEC101WS01PFACON-07AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
91 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 9 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10181 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10181 | 0 | 1 | deoTUNEC101WS01PFACON-07CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
92 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 9 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10182 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10182 | 0 | 1 | deoTUNEC101WS01PFACON-07CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
93 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 9 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 6 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 6 | 2 | deiTUNEC101WS01PFACON-07AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
94 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 9 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10183 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10183 | 0 | 1 | deoTUNEC101WS01PFACON-07CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
95 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 9 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 8 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 8 | 2 | deiTUNEC101WS01PFACON-07AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
96 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 9 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10184 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10184 | 0 | 1 | deoTUNEC101WS01PFACON-07CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
97 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 9 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 10 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 10 | 2 | deiTUNEC101WS01PFACON-07AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
98 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 9 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10185 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10185 | 0 | 1 | deoTUNEC101WS01PFACON-07CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
99 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 9 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 12 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 12 | 2 | deiTUNEC101WS01PFACON-07AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
100 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 9 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10186 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10186 | 0 | 1 | deoTUNEC101WS01PFACON-07CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
101 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 9 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 14 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 14 | 2 | deiTUNEC101WS01PFACON-07AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
102 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 9 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10187 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10187 | 0 | 1 | deoTUNEC101WS01PFACON-07CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
103 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 9 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20092 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20092 | 0 | 2 | deiTUNEC101WS01PFACON-07AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
104 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 9 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20092 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20092 | 2 | 1 | deiTUNEC101WS01PFACON-07StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
105 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | CON-07 | 9 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20092 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20092 | 4 | 1 | deiTUNEC101WS01PFACON-07StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
106 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 10 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20101 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20101 | 0 | 1 | deiTUNEC101WS01PFAPLA-01ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
107 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 10 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20101 | 2 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20101 | 2 | 1 | deiTUNEC101WS01PFAPLA-01OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
108 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 10 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20101 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20101 | 4 | 1 | deiTUNEC101WS01PFAPLA-01AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
109 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 10 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10201 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10201 | 0 | 1 | deoTUNEC101WS01PFAPLA-01CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
110 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 10 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10202 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10202 | 0 | 1 | deoTUNEC101WS01PFAPLA-01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
111 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 10 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 6 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 6 | 2 | deiTUNEC101WS01PFAPLA-01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
112 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 10 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10203 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10203 | 0 | 1 | deoTUNEC101WS01PFAPLA-01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
113 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 10 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 8 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 8 | 2 | deiTUNEC101WS01PFAPLA-01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
114 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 10 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10204 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10204 | 0 | 1 | deoTUNEC101WS01PFAPLA-01CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
115 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 10 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 10 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 10 | 2 | deiTUNEC101WS01PFAPLA-01AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
116 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 10 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10205 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10205 | 0 | 1 | deoTUNEC101WS01PFAPLA-01CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
117 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 10 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 12 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 12 | 2 | deiTUNEC101WS01PFAPLA-01AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
118 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 10 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10206 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10206 | 0 | 1 | deoTUNEC101WS01PFAPLA-01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
119 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 10 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 14 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 14 | 2 | deiTUNEC101WS01PFAPLA-01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
120 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 10 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10207 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10207 | 0 | 1 | deoTUNEC101WS01PFAPLA-01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
121 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 10 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20102 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20102 | 0 | 2 | deiTUNEC101WS01PFAPLA-01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
122 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 10 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20102 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20102 | 2 | 1 | deiTUNEC101WS01PFAPLA-01StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
123 | EC101_RTU | TUN:EC101 | WS01:PFA | PFA | PLA-01 | 10 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20102 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20102 | 4 | 1 | deiTUNEC101WS01PFAPLA-01StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
124 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC01 | 11 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20111 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20111 | 0 | 1 | deiTUNEC101SMCSMC01State | 4 |  |  | 0 | $ComStatus , , | #STATE
125 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC02 | 12 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20121 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20121 | 0 | 1 | deiTUNEC101SMCSMC02State | 4 |  |  | 0 | $ComStatus , , | #STATE
126 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC03 | 13 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20131 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20131 | 0 | 1 | deiTUNEC101SMCSMC03State | 4 |  |  | 0 | $ComStatus , , | #STATE
127 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC04 | 14 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20141 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20141 | 0 | 1 | deiTUNEC101SMCSMC04State | 4 |  |  | 0 | $ComStatus , , | #STATE
128 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC05 | 15 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20151 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20151 | 0 | 1 | deiTUNEC101SMCSMC05State | 4 |  |  | 0 | $ComStatus , , | #STATE
129 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC06 | 16 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20161 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20161 | 0 | 1 | deiTUNEC101SMCSMC06State | 4 |  |  | 0 | $ComStatus , , | #STATE
130 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC07 | 17 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20171 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20171 | 0 | 1 | deiTUNEC101SMCSMC07State | 4 |  |  | 0 | $ComStatus , , | #STATE
131 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC08 | 18 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20181 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20181 | 0 | 1 | deiTUNEC101SMCSMC08State | 4 |  |  | 0 | $ComStatus , , | #STATE
132 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC09 | 19 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20191 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20191 | 0 | 1 | deiTUNEC101SMCSMC09State | 4 |  |  | 0 | $ComStatus , , | #STATE
133 | EC101_RTU | TUN:EC101 | SMC | SMC | SMC10 | 20 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20201 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20201 | 0 | 1 | deiTUNEC101SMCSMC10State | 4 |  |  | 0 | $ComStatus , , | #STATE
134 | EC101_RTU | TUN:EC101 | SED | SED | SED01 | 21 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20211 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20211 | 0 | 1 | deiTUNEC101SEDSED01State | 4 |  |  | 0 | $ComStatus , , | #STATE
135 | EC101_RTU | TUN:EC101 | SED | SED | SED01 | 21 | Open | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20211 | 1 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20211 | 1 | 1 | deiTUNEC101SEDSED01Open | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
136 | EC101_RTU | TUN:EC101 | SED | SED | SED02 | 22 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20221 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20221 | 0 | 1 | deiTUNEC101SEDSED02State | 4 |  |  | 0 | $ComStatus , , | #STATE
137 | EC101_RTU | TUN:EC101 | SED | SED | SED02 | 22 | Open | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20221 | 1 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20221 | 1 | 1 | deiTUNEC101SEDSED02Open | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
138 | EC101_RTU | TUN:EC101 | SED | SED | SED03 | 23 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20231 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20231 | 0 | 1 | deiTUNEC101SEDSED03State | 4 |  |  | 0 | $ComStatus , , | #STATE
139 | EC101_RTU | TUN:EC101 | SED | SED | SED03 | 23 | Open | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20231 | 1 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20231 | 1 | 1 | deiTUNEC101SEDSED03Open | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
140 | EC101_RTU | TUN:EC101 | SED | SED | SED04 | 24 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20241 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20241 | 0 | 1 | deiTUNEC101SEDSED04State | 4 |  |  | 0 | $ComStatus , , | #STATE
141 | EC101_RTU | TUN:EC101 | SED | SED | SED04 | 24 | Open | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20241 | 1 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20241 | 1 | 1 | deiTUNEC101SEDSED04Open | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
142 | EC101_RTU | TUN:EC101 | OTS | OTS | OTS001 | 25 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20251 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20251 | 0 | 1 | deiTUNEC101OTSOTS001AvailStat | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
143 | EC101_RTU | TUN:EC101 | OTS | OTS | OTS001 | 25 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20251 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20251 | 2 | 1 | deiTUNEC101OTSOTS001AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
144 | EC101_RTU | TUN:EC101 | OTS | OTS | OTS001 | 25 | TemMeasure | SIL0 | MODBUS:4:Read:Input Registers | 20252 | 0 | 32 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20252 | 0 | 32 | aeiTUNEC101OTSOTS001TemMeasure | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
145 | EC101_RTU | TUN:EC101 | OTS | OTS | OTS002 | 26 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20261 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20261 | 0 | 1 | deiTUNEC101OTSOTS002AvailStat | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
146 | EC101_RTU | TUN:EC101 | OTS | OTS | OTS002 | 26 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20261 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20261 | 2 | 1 | deiTUNEC101OTSOTS002AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
147 | EC101_RTU | TUN:EC101 | OTS | OTS | OTS002 | 26 | TemMeasure | SIL0 | MODBUS:4:Read:Input Registers | 20262 | 0 | 32 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20262 | 0 | 32 | aeiTUNEC101OTSOTS002TemMeasure | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
148 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20271 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20271 | 0 | 2 | deiTUNEC101WS01TVFVT1-TVF01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
149 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20271 | 2 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20271 | 2 | 1 | deiTUNEC101WS01TVFVT1-TVF01OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
150 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20271 | 4 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20271 | 4 | 2 | deiTUNEC101WS01TVFVT1-TVF01RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
151 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10541 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10541 | 0 | 1 | deoTUNEC101WS01TVFVT1-TVF01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
152 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10542 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10542 | 0 | 1 | deoTUNEC101WS01TVFVT1-TVF01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
153 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20271 | 6 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20271 | 6 | 2 | deiTUNEC101WS01TVFVT1-TVF01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
154 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10543 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10543 | 0 | 1 | deoTUNEC101WS01TVFVT1-TVF01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
155 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20271 | 8 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20271 | 8 | 2 | deiTUNEC101WS01TVFVT1-TVF01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
156 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20271 | 10 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20271 | 10 | 1 | deiTUNEC101WS01TVFVT1-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
157 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20271 | 12 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20271 | 12 | 1 | deiTUNEC101WS01TVFVT1-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
158 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20271 | 14 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20271 | 14 | 1 | deiTUNEC101WS01TVFVT1-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
159 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20272 | 0 | 32 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20272 | 0 | 32 | aeiTUNEC101WS01TVFVT1-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
160 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10544 | 0 | 2 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10544 | 0 | 2 | deoTUNEC101WS01TVFVT1-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
161 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10545 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10545 | 0 | 1 | deoTUNEC101WS01TVFVT1-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
162 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 0 | 2 | deiTUNEC101WS01TVFVT1-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
163 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10546 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10546 | 0 | 1 | deoTUNEC101WS01TVFVT1-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
164 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 2 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 2 | 2 | deiTUNEC101WS01TVFVT1-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
165 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10547 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10547 | 0 | 1 | deoTUNEC101WS01TVFVT1-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
166 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 4 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 4 | 2 | deiTUNEC101WS01TVFVT1-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
167 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10548 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10548 | 0 | 1 | deoTUNEC101WS01TVFVT1-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
168 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 6 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 6 | 2 | deiTUNEC101WS01TVFVT1-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
169 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10549 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10549 | 0 | 1 | deoTUNEC101WS01TVFVT1-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
170 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 8 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 8 | 2 | deiTUNEC101WS01TVFVT1-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
171 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10550 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10550 | 0 | 1 | deoTUNEC101WS01TVFVT1-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
172 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 10 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 10 | 2 | deiTUNEC101WS01TVFVT1-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
173 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20274 | 12 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20274 | 12 | 1 | deiTUNEC101WS01TVFVT1-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
174 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20274 | 14 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20274 | 14 | 1 | deiTUNEC101WS01TVFVT1-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
175 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 0 | 1 | deiTUNEC101WS01TVFVT1-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
176 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 1 | 1 | deiTUNEC101WS01TVFVT1-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
177 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 2 | 1 | deiTUNEC101WS01TVFVT1-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
178 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 3 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 3 | 1 | deiTUNEC101WS01TVFVT1-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
179 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 4 | 1 | deiTUNEC101WS01TVFVT1-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
180 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 5 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 5 | 1 | deiTUNEC101WS01TVFVT1-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
181 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 6 | 1 | deiTUNEC101WS01TVFVT1-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
182 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 7 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 7 | 1 | deiTUNEC101WS01TVFVT1-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
183 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 8 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 8 | 1 | deiTUNEC101WS01TVFVT1-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
184 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 9 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 9 | 1 | deiTUNEC101WS01TVFVT1-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
185 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 10 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 10 | 1 | deiTUNEC101WS01TVFVT1-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
186 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 11 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 11 | 1 | deiTUNEC101WS01TVFVT1-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
187 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT1-TVF01 | 27 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20276 | 0 | 16 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20276 | 0 | 16 | aeiTUNEC101WS01TVFVT1-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
188 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20281 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20281 | 0 | 2 | deiTUNEC101WS01TVFVT2-TVF01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
189 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20281 | 2 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20281 | 2 | 1 | deiTUNEC101WS01TVFVT2-TVF01OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
190 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20281 | 4 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20281 | 4 | 2 | deiTUNEC101WS01TVFVT2-TVF01RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
191 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10561 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10561 | 0 | 1 | deoTUNEC101WS01TVFVT2-TVF01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
192 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10562 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10562 | 0 | 1 | deoTUNEC101WS01TVFVT2-TVF01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
193 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20281 | 6 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20281 | 6 | 2 | deiTUNEC101WS01TVFVT2-TVF01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
194 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10563 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10563 | 0 | 1 | deoTUNEC101WS01TVFVT2-TVF01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
195 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20281 | 8 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20281 | 8 | 2 | deiTUNEC101WS01TVFVT2-TVF01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
196 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20281 | 10 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20281 | 10 | 1 | deiTUNEC101WS01TVFVT2-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
197 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20281 | 12 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20281 | 12 | 1 | deiTUNEC101WS01TVFVT2-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
198 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20281 | 14 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20281 | 14 | 1 | deiTUNEC101WS01TVFVT2-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
199 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20282 | 0 | 32 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20282 | 0 | 32 | aeiTUNEC101WS01TVFVT2-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
200 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10564 | 0 | 2 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10564 | 0 | 2 | deoTUNEC101WS01TVFVT2-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
201 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10565 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10565 | 0 | 1 | deoTUNEC101WS01TVFVT2-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
202 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 0 | 2 | deiTUNEC101WS01TVFVT2-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
203 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10566 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10566 | 0 | 1 | deoTUNEC101WS01TVFVT2-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
204 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 2 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 2 | 2 | deiTUNEC101WS01TVFVT2-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
205 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10567 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10567 | 0 | 1 | deoTUNEC101WS01TVFVT2-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
206 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 4 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 4 | 2 | deiTUNEC101WS01TVFVT2-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
207 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10568 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10568 | 0 | 1 | deoTUNEC101WS01TVFVT2-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
208 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 6 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 6 | 2 | deiTUNEC101WS01TVFVT2-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
209 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10569 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10569 | 0 | 1 | deoTUNEC101WS01TVFVT2-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
210 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 8 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 8 | 2 | deiTUNEC101WS01TVFVT2-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
211 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10570 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10570 | 0 | 1 | deoTUNEC101WS01TVFVT2-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
212 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 10 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 10 | 2 | deiTUNEC101WS01TVFVT2-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
213 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20284 | 12 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20284 | 12 | 1 | deiTUNEC101WS01TVFVT2-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
214 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20284 | 14 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20284 | 14 | 1 | deiTUNEC101WS01TVFVT2-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
215 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 0 | 1 | deiTUNEC101WS01TVFVT2-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
216 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 1 | 1 | deiTUNEC101WS01TVFVT2-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
217 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 2 | 1 | deiTUNEC101WS01TVFVT2-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
218 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 3 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 3 | 1 | deiTUNEC101WS01TVFVT2-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
219 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 4 | 1 | deiTUNEC101WS01TVFVT2-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
220 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 5 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 5 | 1 | deiTUNEC101WS01TVFVT2-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
221 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 6 | 1 | deiTUNEC101WS01TVFVT2-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
222 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 7 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 7 | 1 | deiTUNEC101WS01TVFVT2-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
223 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 8 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 8 | 1 | deiTUNEC101WS01TVFVT2-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
224 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 9 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 9 | 1 | deiTUNEC101WS01TVFVT2-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
225 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 10 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 10 | 1 | deiTUNEC101WS01TVFVT2-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
226 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 11 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 11 | 1 | deiTUNEC101WS01TVFVT2-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
227 | EC101_RTU | TUN:EC101 | WS01:TVF | TVF | VT2-TVF01 | 28 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20286 | 0 | 16 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20286 | 0 | 16 | aeiTUNEC101WS01TVFVT2-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
228 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20291 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20291 | 0 | 2 | deiTUNEC101ES01TVFVT3-TVF01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
229 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20291 | 2 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20291 | 2 | 1 | deiTUNEC101ES01TVFVT3-TVF01OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
230 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20291 | 4 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20291 | 4 | 2 | deiTUNEC101ES01TVFVT3-TVF01RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
231 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10581 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10581 | 0 | 1 | deoTUNEC101ES01TVFVT3-TVF01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
232 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10582 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10582 | 0 | 1 | deoTUNEC101ES01TVFVT3-TVF01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
233 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20291 | 6 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20291 | 6 | 2 | deiTUNEC101ES01TVFVT3-TVF01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
234 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10583 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10583 | 0 | 1 | deoTUNEC101ES01TVFVT3-TVF01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
235 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20291 | 8 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20291 | 8 | 2 | deiTUNEC101ES01TVFVT3-TVF01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
236 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20291 | 10 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20291 | 10 | 1 | deiTUNEC101ES01TVFVT3-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
237 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20291 | 12 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20291 | 12 | 1 | deiTUNEC101ES01TVFVT3-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
238 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20291 | 14 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20291 | 14 | 1 | deiTUNEC101ES01TVFVT3-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
239 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20292 | 0 | 32 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20292 | 0 | 32 | aeiTUNEC101ES01TVFVT3-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
240 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10584 | 0 | 2 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10584 | 0 | 2 | deoTUNEC101ES01TVFVT3-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
241 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10585 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10585 | 0 | 1 | deoTUNEC101ES01TVFVT3-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
242 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 0 | 2 | deiTUNEC101ES01TVFVT3-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
243 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10586 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10586 | 0 | 1 | deoTUNEC101ES01TVFVT3-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
244 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 2 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 2 | 2 | deiTUNEC101ES01TVFVT3-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
245 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10587 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10587 | 0 | 1 | deoTUNEC101ES01TVFVT3-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
246 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 4 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 4 | 2 | deiTUNEC101ES01TVFVT3-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
247 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10588 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10588 | 0 | 1 | deoTUNEC101ES01TVFVT3-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
248 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 6 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 6 | 2 | deiTUNEC101ES01TVFVT3-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
249 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10589 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10589 | 0 | 1 | deoTUNEC101ES01TVFVT3-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
250 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 8 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 8 | 2 | deiTUNEC101ES01TVFVT3-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
251 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10590 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10590 | 0 | 1 | deoTUNEC101ES01TVFVT3-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
252 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 10 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 10 | 2 | deiTUNEC101ES01TVFVT3-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
253 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20294 | 12 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20294 | 12 | 1 | deiTUNEC101ES01TVFVT3-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
254 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20294 | 14 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20294 | 14 | 1 | deiTUNEC101ES01TVFVT3-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
255 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 0 | 1 | deiTUNEC101ES01TVFVT3-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
256 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 1 | 1 | deiTUNEC101ES01TVFVT3-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
257 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 2 | 1 | deiTUNEC101ES01TVFVT3-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
258 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 3 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 3 | 1 | deiTUNEC101ES01TVFVT3-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
259 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 4 | 1 | deiTUNEC101ES01TVFVT3-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
260 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 5 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 5 | 1 | deiTUNEC101ES01TVFVT3-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
261 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 6 | 1 | deiTUNEC101ES01TVFVT3-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
262 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 7 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 7 | 1 | deiTUNEC101ES01TVFVT3-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
263 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 8 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 8 | 1 | deiTUNEC101ES01TVFVT3-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
264 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 9 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 9 | 1 | deiTUNEC101ES01TVFVT3-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
265 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 10 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 10 | 1 | deiTUNEC101ES01TVFVT3-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
266 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 11 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 11 | 1 | deiTUNEC101ES01TVFVT3-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
267 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT3-TVF01 | 29 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20296 | 0 | 16 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20296 | 0 | 16 | aeiTUNEC101ES01TVFVT3-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
268 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20301 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20301 | 0 | 2 | deiTUNEC101ES01TVFVT4-TVF01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
269 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20301 | 2 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20301 | 2 | 1 | deiTUNEC101ES01TVFVT4-TVF01OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
270 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20301 | 4 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20301 | 4 | 2 | deiTUNEC101ES01TVFVT4-TVF01RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
271 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10601 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10601 | 0 | 1 | deoTUNEC101ES01TVFVT4-TVF01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
272 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10602 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10602 | 0 | 1 | deoTUNEC101ES01TVFVT4-TVF01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
273 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20301 | 6 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20301 | 6 | 2 | deiTUNEC101ES01TVFVT4-TVF01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
274 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10603 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10603 | 0 | 1 | deoTUNEC101ES01TVFVT4-TVF01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
275 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20301 | 8 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20301 | 8 | 2 | deiTUNEC101ES01TVFVT4-TVF01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
276 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20301 | 10 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20301 | 10 | 1 | deiTUNEC101ES01TVFVT4-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
277 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20301 | 12 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20301 | 12 | 1 | deiTUNEC101ES01TVFVT4-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
278 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20301 | 14 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20301 | 14 | 1 | deiTUNEC101ES01TVFVT4-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
279 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20302 | 0 | 32 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20302 | 0 | 32 | aeiTUNEC101ES01TVFVT4-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
280 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10604 | 0 | 2 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10604 | 0 | 2 | deoTUNEC101ES01TVFVT4-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
281 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10605 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10605 | 0 | 1 | deoTUNEC101ES01TVFVT4-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
282 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 0 | 2 | deiTUNEC101ES01TVFVT4-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
283 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10606 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10606 | 0 | 1 | deoTUNEC101ES01TVFVT4-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
284 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 2 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 2 | 2 | deiTUNEC101ES01TVFVT4-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
285 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10607 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10607 | 0 | 1 | deoTUNEC101ES01TVFVT4-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
286 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 4 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 4 | 2 | deiTUNEC101ES01TVFVT4-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
287 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10608 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10608 | 0 | 1 | deoTUNEC101ES01TVFVT4-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
288 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 6 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 6 | 2 | deiTUNEC101ES01TVFVT4-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
289 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10609 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10609 | 0 | 1 | deoTUNEC101ES01TVFVT4-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
290 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 8 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 8 | 2 | deiTUNEC101ES01TVFVT4-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
291 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10610 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10610 | 0 | 1 | deoTUNEC101ES01TVFVT4-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
292 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 10 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 10 | 2 | deiTUNEC101ES01TVFVT4-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
293 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20304 | 12 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20304 | 12 | 1 | deiTUNEC101ES01TVFVT4-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
294 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20304 | 14 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20304 | 14 | 1 | deiTUNEC101ES01TVFVT4-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
295 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 0 | 1 | deiTUNEC101ES01TVFVT4-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
296 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 1 | 1 | deiTUNEC101ES01TVFVT4-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
297 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 2 | 1 | deiTUNEC101ES01TVFVT4-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
298 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 3 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 3 | 1 | deiTUNEC101ES01TVFVT4-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
299 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 4 | 1 | deiTUNEC101ES01TVFVT4-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
300 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 5 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 5 | 1 | deiTUNEC101ES01TVFVT4-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
301 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 6 | 1 | deiTUNEC101ES01TVFVT4-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
302 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 7 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 7 | 1 | deiTUNEC101ES01TVFVT4-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
303 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 8 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 8 | 1 | deiTUNEC101ES01TVFVT4-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
304 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 9 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 9 | 1 | deiTUNEC101ES01TVFVT4-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
305 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 10 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 10 | 1 | deiTUNEC101ES01TVFVT4-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
306 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 11 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 11 | 1 | deiTUNEC101ES01TVFVT4-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
307 | EC101_RTU | TUN:EC101 | ES01:TVF | TVF | VT4-TVF01 | 30 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20306 | 0 | 16 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20306 | 0 | 16 | aeiTUNEC101ES01TVFVT4-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
308 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101561 | 31 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 0 | 1 | deiTUNEC101WS01SENSORTS101561Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
309 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101561 | 31 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 1 | 1 | deiTUNEC101WS01SENSORTS101561TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
310 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101561 | 31 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 2 | 1 | deiTUNEC101WS01SENSORTS101561HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
311 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101561 | 31 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 3 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 3 | 1 | deiTUNEC101WS01SENSORTS101561AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
312 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101561 | 31 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20312 | 0 | 32 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20312 | 0 | 32 | aeiTUNEC101WS01SENSORTS101561Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
313 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101561 | 31 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20314 | 0 | 32 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20314 | 0 | 32 | aeiTUNEC101WS01SENSORTS101561Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
314 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101647 | 32 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 0 | 1 | deiTUNEC101WS01SENSORTS101647Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
315 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101647 | 32 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 1 | 1 | deiTUNEC101WS01SENSORTS101647TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
316 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101647 | 32 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 2 | 1 | deiTUNEC101WS01SENSORTS101647HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
317 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101647 | 32 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 3 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 3 | 1 | deiTUNEC101WS01SENSORTS101647AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
318 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101647 | 32 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20322 | 0 | 32 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20322 | 0 | 32 | aeiTUNEC101WS01SENSORTS101647Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
319 | EC101_RTU | TUN:EC101 | WS01:SENSOR | TTS | TS101647 | 32 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20324 | 0 | 32 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20324 | 0 | 32 | aeiTUNEC101WS01SENSORTS101647Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
320 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101045 | 33 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 0 | 1 | deiTUNEC101ES01SENSORTS101045Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
321 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101045 | 33 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 1 | 1 | deiTUNEC101ES01SENSORTS101045TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
322 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101045 | 33 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 2 | 1 | deiTUNEC101ES01SENSORTS101045HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
323 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101045 | 33 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 3 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 3 | 1 | deiTUNEC101ES01SENSORTS101045AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
324 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101045 | 33 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20332 | 0 | 32 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20332 | 0 | 32 | aeiTUNEC101ES01SENSORTS101045Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
325 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101045 | 33 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20334 | 0 | 32 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20334 | 0 | 32 | aeiTUNEC101ES01SENSORTS101045Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
326 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101184 | 34 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 0 | 1 | deiTUNEC101ES01SENSORTS101184Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
327 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101184 | 34 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 1 | 1 | deiTUNEC101ES01SENSORTS101184TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
328 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101184 | 34 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 2 | 1 | deiTUNEC101ES01SENSORTS101184HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
329 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101184 | 34 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 3 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 3 | 1 | deiTUNEC101ES01SENSORTS101184AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
330 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101184 | 34 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20342 | 0 | 32 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20342 | 0 | 32 | aeiTUNEC101ES01SENSORTS101184Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
331 | EC101_RTU | TUN:EC101 | ES01:SENSOR | TTS | TS101184 | 34 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20344 | 0 | 32 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20344 | 0 | 32 | aeiTUNEC101ES01SENSORTS101184Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
332 | EC101_RTU | TUN:EC101 | WS01:SENSOR | VS | VS101618 | 35 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20351 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20351 | 0 | 1 | deiTUNEC101WS01SENSORVS101618Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
333 | EC101_RTU | TUN:EC101 | WS01:SENSOR | VS | VS101618 | 35 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20352 | 0 | 32 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20352 | 0 | 32 | aeiTUNEC101WS01SENSORVS101618Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
334 | EC101_RTU | TUN:EC101 | ES01:SENSOR | VS | VS101094 | 36 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20361 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20361 | 0 | 1 | deiTUNEC101ES01SENSORVS101094Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
335 | EC101_RTU | TUN:EC101 | ES01:SENSOR | VS | VS101094 | 36 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20362 | 0 | 32 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20362 | 0 | 32 | aeiTUNEC101ES01SENSORVS101094Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
336 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20371 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20371 | 0 | 2 | deiTUNEC101WS01DAMPERVT5-TDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
337 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20371 | 2 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20371 | 2 | 1 | deiTUNEC101WS01DAMPERVT5-TDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
338 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20371 | 4 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20371 | 4 | 2 | deiTUNEC101WS01DAMPERVT5-TDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
339 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10741 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10741 | 0 | 1 | deoTUNEC101WS01DAMPERVT5-TDP01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
340 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10742 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10742 | 0 | 1 | deoTUNEC101WS01DAMPERVT5-TDP01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
341 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20371 | 6 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20371 | 6 | 2 | deiTUNEC101WS01DAMPERVT5-TDP01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
342 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10743 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10743 | 0 | 1 | deoTUNEC101WS01DAMPERVT5-TDP01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
343 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20371 | 8 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20371 | 8 | 2 | deiTUNEC101WS01DAMPERVT5-TDP01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
344 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10744 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10744 | 0 | 1 | deoTUNEC101WS01DAMPERVT5-TDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
345 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20371 | 10 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20371 | 10 | 2 | deiTUNEC101WS01DAMPERVT5-TDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
346 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10745 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10745 | 0 | 1 | deoTUNEC101WS01DAMPERVT5-TDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
347 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20371 | 12 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20371 | 12 | 2 | deiTUNEC101WS01DAMPERVT5-TDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
348 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10746 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10746 | 0 | 1 | deoTUNEC101WS01DAMPERVT5-TDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
349 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20371 | 14 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20371 | 14 | 2 | deiTUNEC101WS01DAMPERVT5-TDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
350 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10747 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10747 | 0 | 1 | deoTUNEC101WS01DAMPERVT5-TDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
351 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20372 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20372 | 0 | 2 | deiTUNEC101WS01DAMPERVT5-TDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
352 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20372 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20372 | 2 | 1 | deiTUNEC101WS01DAMPERVT5-TDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
353 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20372 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20372 | 4 | 1 | deiTUNEC101WS01DAMPERVT5-TDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
354 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20372 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20372 | 6 | 1 | deiTUNEC101WS01DAMPERVT5-TDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
355 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | VT5-TDP01 | 37 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20372 | 8 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20372 | 8 | 1 | deiTUNEC101WS01DAMPERVT5-TDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
356 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20381 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20381 | 0 | 2 | deiTUNEC101ES01DAMPERVT6-TDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
357 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20381 | 2 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20381 | 2 | 1 | deiTUNEC101ES01DAMPERVT6-TDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
358 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20381 | 4 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20381 | 4 | 2 | deiTUNEC101ES01DAMPERVT6-TDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
359 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10761 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10761 | 0 | 1 | deoTUNEC101ES01DAMPERVT6-TDP01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
360 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10762 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10762 | 0 | 1 | deoTUNEC101ES01DAMPERVT6-TDP01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
361 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20381 | 6 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20381 | 6 | 2 | deiTUNEC101ES01DAMPERVT6-TDP01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
362 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10763 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10763 | 0 | 1 | deoTUNEC101ES01DAMPERVT6-TDP01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
363 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20381 | 8 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20381 | 8 | 2 | deiTUNEC101ES01DAMPERVT6-TDP01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
364 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10764 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10764 | 0 | 1 | deoTUNEC101ES01DAMPERVT6-TDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
365 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20381 | 10 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20381 | 10 | 2 | deiTUNEC101ES01DAMPERVT6-TDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
366 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10765 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10765 | 0 | 1 | deoTUNEC101ES01DAMPERVT6-TDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
367 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20381 | 12 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20381 | 12 | 2 | deiTUNEC101ES01DAMPERVT6-TDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
368 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10766 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10766 | 0 | 1 | deoTUNEC101ES01DAMPERVT6-TDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
369 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20381 | 14 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20381 | 14 | 2 | deiTUNEC101ES01DAMPERVT6-TDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
370 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10767 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10767 | 0 | 1 | deoTUNEC101ES01DAMPERVT6-TDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
371 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20382 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20382 | 0 | 2 | deiTUNEC101ES01DAMPERVT6-TDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
372 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20382 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20382 | 2 | 1 | deiTUNEC101ES01DAMPERVT6-TDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
373 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20382 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20382 | 4 | 1 | deiTUNEC101ES01DAMPERVT6-TDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
374 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20382 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20382 | 6 | 1 | deiTUNEC101ES01DAMPERVT6-TDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
375 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | VT6-TDP01 | 38 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20382 | 8 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20382 | 8 | 1 | deiTUNEC101ES01DAMPERVT6-TDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
376 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT1-IDP01 | 39 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20391 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20391 | 0 | 2 | deiTUNEC101WS01DAMPERVT1-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
377 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT1-IDP01 | 39 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20391 | 2 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20391 | 2 | 2 | deiTUNEC101WS01DAMPERVT1-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
378 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT1-IDP01 | 39 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 4 | 1 | deiTUNEC101WS01DAMPERVT1-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
379 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT1-IDP01 | 39 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 6 | 1 | deiTUNEC101WS01DAMPERVT1-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
380 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT1-IDP01 | 39 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 8 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 8 | 1 | deiTUNEC101WS01DAMPERVT1-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
381 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT1-IDP01 | 39 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 10 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 10 | 1 | deiTUNEC101WS01DAMPERVT1-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
382 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT2-IDP01 | 40 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20401 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20401 | 0 | 2 | deiTUNEC101WS01DAMPERVT2-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
383 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT2-IDP01 | 40 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20401 | 2 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20401 | 2 | 2 | deiTUNEC101WS01DAMPERVT2-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
384 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT2-IDP01 | 40 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 4 | 1 | deiTUNEC101WS01DAMPERVT2-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
385 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT2-IDP01 | 40 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 6 | 1 | deiTUNEC101WS01DAMPERVT2-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
386 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT2-IDP01 | 40 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 8 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 8 | 1 | deiTUNEC101WS01DAMPERVT2-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
387 | EC101_RTU | TUN:EC101 | WS01:DAMPER | IDP | VT2-IDP01 | 40 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 10 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 10 | 1 | deiTUNEC101WS01DAMPERVT2-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
388 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT3-IDP01 | 41 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20411 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20411 | 0 | 2 | deiTUNEC101ES01DAMPERVT3-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
389 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT3-IDP01 | 41 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20411 | 2 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20411 | 2 | 2 | deiTUNEC101ES01DAMPERVT3-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
390 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT3-IDP01 | 41 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20411 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20411 | 4 | 1 | deiTUNEC101ES01DAMPERVT3-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
391 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT3-IDP01 | 41 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20411 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20411 | 6 | 1 | deiTUNEC101ES01DAMPERVT3-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
392 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT3-IDP01 | 41 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20411 | 8 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20411 | 8 | 1 | deiTUNEC101ES01DAMPERVT3-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
393 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT3-IDP01 | 41 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20411 | 10 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20411 | 10 | 1 | deiTUNEC101ES01DAMPERVT3-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
394 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT4-IDP01 | 42 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20421 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20421 | 0 | 2 | deiTUNEC101ES01DAMPERVT4-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
395 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT4-IDP01 | 42 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20421 | 2 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20421 | 2 | 2 | deiTUNEC101ES01DAMPERVT4-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
396 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT4-IDP01 | 42 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20421 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20421 | 4 | 1 | deiTUNEC101ES01DAMPERVT4-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
397 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT4-IDP01 | 42 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20421 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20421 | 6 | 1 | deiTUNEC101ES01DAMPERVT4-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
398 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT4-IDP01 | 42 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20421 | 8 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20421 | 8 | 1 | deiTUNEC101ES01DAMPERVT4-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
399 | EC101_RTU | TUN:EC101 | ES01:DAMPER | IDP | VT4-IDP01 | 42 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20421 | 10 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20421 | 10 | 1 | deiTUNEC101ES01DAMPERVT4-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
400 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20431 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20431 | 0 | 2 | deiTUNEC101WS01DAMPERFR1-BDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
401 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20431 | 2 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20431 | 2 | 1 | deiTUNEC101WS01DAMPERFR1-BDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
402 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20431 | 4 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20431 | 4 | 2 | deiTUNEC101WS01DAMPERFR1-BDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
403 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10861 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10861 | 0 | 1 | deoTUNEC101WS01DAMPERFR1-BDP01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
404 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10862 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10862 | 0 | 1 | deoTUNEC101WS01DAMPERFR1-BDP01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
405 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20431 | 6 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20431 | 6 | 2 | deiTUNEC101WS01DAMPERFR1-BDP01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
406 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10863 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10863 | 0 | 1 | deoTUNEC101WS01DAMPERFR1-BDP01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
407 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20431 | 8 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20431 | 8 | 2 | deiTUNEC101WS01DAMPERFR1-BDP01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
408 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10864 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10864 | 0 | 1 | deoTUNEC101WS01DAMPERFR1-BDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
409 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20431 | 10 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20431 | 10 | 2 | deiTUNEC101WS01DAMPERFR1-BDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
410 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10865 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10865 | 0 | 1 | deoTUNEC101WS01DAMPERFR1-BDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
411 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20431 | 12 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20431 | 12 | 2 | deiTUNEC101WS01DAMPERFR1-BDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
412 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10866 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10866 | 0 | 1 | deoTUNEC101WS01DAMPERFR1-BDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
413 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20431 | 14 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20431 | 14 | 2 | deiTUNEC101WS01DAMPERFR1-BDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
414 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10867 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10867 | 0 | 1 | deoTUNEC101WS01DAMPERFR1-BDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
415 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20432 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20432 | 0 | 2 | deiTUNEC101WS01DAMPERFR1-BDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
416 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20432 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20432 | 2 | 1 | deiTUNEC101WS01DAMPERFR1-BDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
417 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20432 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20432 | 4 | 1 | deiTUNEC101WS01DAMPERFR1-BDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
418 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20432 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20432 | 6 | 1 | deiTUNEC101WS01DAMPERFR1-BDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
419 | EC101_RTU | TUN:EC101 | WS01:DAMPER | TVD | FR1-BDP01 | 43 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20432 | 8 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20432 | 8 | 1 | deiTUNEC101WS01DAMPERFR1-BDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
420 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20441 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20441 | 0 | 2 | deiTUNEC101ES01DAMPERFR2-BDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
421 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20441 | 2 | 1 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20441 | 2 | 1 | deiTUNEC101ES01DAMPERFR2-BDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
422 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20441 | 4 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20441 | 4 | 2 | deiTUNEC101ES01DAMPERFR2-BDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
423 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10881 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10881 | 0 | 1 | deoTUNEC101ES01DAMPERFR2-BDP01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
424 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10882 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10882 | 0 | 1 | deoTUNEC101ES01DAMPERFR2-BDP01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
425 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20441 | 6 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20441 | 6 | 2 | deiTUNEC101ES01DAMPERFR2-BDP01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
426 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10883 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10883 | 0 | 1 | deoTUNEC101ES01DAMPERFR2-BDP01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
427 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20441 | 8 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20441 | 8 | 2 | deiTUNEC101ES01DAMPERFR2-BDP01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
428 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10884 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10884 | 0 | 1 | deoTUNEC101ES01DAMPERFR2-BDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
429 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20441 | 10 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20441 | 10 | 2 | deiTUNEC101ES01DAMPERFR2-BDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
430 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10885 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10885 | 0 | 1 | deoTUNEC101ES01DAMPERFR2-BDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
431 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20441 | 12 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20441 | 12 | 2 | deiTUNEC101ES01DAMPERFR2-BDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
432 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10886 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10886 | 0 | 1 | deoTUNEC101ES01DAMPERFR2-BDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
433 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20441 | 14 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20441 | 14 | 2 | deiTUNEC101ES01DAMPERFR2-BDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
434 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10887 | 0 | 1 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10887 | 0 | 1 | deoTUNEC101ES01DAMPERFR2-BDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
435 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20442 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Control |  | EC101_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20442 | 0 | 2 | deiTUNEC101ES01DAMPERFR2-BDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
436 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20442 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20442 | 2 | 1 | deiTUNEC101ES01DAMPERFR2-BDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
437 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20442 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20442 | 4 | 1 | deiTUNEC101ES01DAMPERFR2-BDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
438 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20442 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20442 | 6 | 1 | deiTUNEC101ES01DAMPERFR2-BDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
439 | EC101_RTU | TUN:EC101 | ES01:DAMPER | TVD | FR2-BDP01 | 44 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20442 | 8 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20442 | 8 | 1 | deiTUNEC101ES01DAMPERFR2-BDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
440 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | PLA-68 | 45 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20451 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20451 | 0 | 2 | deiTUNEC101WS01DAMPERPLA-68Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
441 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | PLA-68 | 45 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20451 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20451 | 2 | 1 | deiTUNEC101WS01DAMPERPLA-68CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
442 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | PLA-68 | 45 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20451 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20451 | 4 | 1 | deiTUNEC101WS01DAMPERPLA-68TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
443 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | PLA-68 | 45 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20451 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20451 | 6 | 1 | deiTUNEC101WS01DAMPERPLA-68LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
444 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | PLA-33 | 46 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20461 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20461 | 0 | 2 | deiTUNEC101ES01DAMPERPLA-33Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
445 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | PLA-33 | 46 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20461 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20461 | 2 | 1 | deiTUNEC101ES01DAMPERPLA-33CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
446 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | PLA-33 | 46 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20461 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20461 | 4 | 1 | deiTUNEC101ES01DAMPERPLA-33TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
447 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | PLA-33 | 46 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20461 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20461 | 6 | 1 | deiTUNEC101ES01DAMPERPLA-33LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
448 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-80 | 47 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20471 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20471 | 0 | 2 | deiTUNEC101WS01DAMPERCON-80Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
449 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-80 | 47 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20471 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20471 | 2 | 1 | deiTUNEC101WS01DAMPERCON-80CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
450 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-80 | 47 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20471 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20471 | 4 | 1 | deiTUNEC101WS01DAMPERCON-80TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
451 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-80 | 47 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20471 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20471 | 6 | 1 | deiTUNEC101WS01DAMPERCON-80LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
452 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-72 | 48 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20481 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20481 | 0 | 2 | deiTUNEC101WS01DAMPERCON-72Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
453 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-72 | 48 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20481 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20481 | 2 | 1 | deiTUNEC101WS01DAMPERCON-72CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
454 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-72 | 48 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20481 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20481 | 4 | 1 | deiTUNEC101WS01DAMPERCON-72TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
455 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-72 | 48 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20481 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20481 | 6 | 1 | deiTUNEC101WS01DAMPERCON-72LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
456 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-25 | 49 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20491 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20491 | 0 | 2 | deiTUNEC101ES01DAMPERCON-25Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
457 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-25 | 49 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20491 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20491 | 2 | 1 | deiTUNEC101ES01DAMPERCON-25CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
458 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-25 | 49 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20491 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20491 | 4 | 1 | deiTUNEC101ES01DAMPERCON-25TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
459 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-25 | 49 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20491 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20491 | 6 | 1 | deiTUNEC101ES01DAMPERCON-25LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
460 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-26 | 50 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20501 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20501 | 0 | 2 | deiTUNEC101ES01DAMPERCON-26Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
461 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-26 | 50 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20501 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20501 | 2 | 1 | deiTUNEC101ES01DAMPERCON-26CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
462 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-26 | 50 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20501 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20501 | 4 | 1 | deiTUNEC101ES01DAMPERCON-26TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
463 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-26 | 50 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20501 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20501 | 6 | 1 | deiTUNEC101ES01DAMPERCON-26LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
464 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-79 | 51 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20511 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20511 | 0 | 2 | deiTUNEC101WS01DAMPERCON-79Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
465 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-79 | 51 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20511 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20511 | 2 | 1 | deiTUNEC101WS01DAMPERCON-79CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
466 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-79 | 51 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20511 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20511 | 4 | 1 | deiTUNEC101WS01DAMPERCON-79TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
467 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-79 | 51 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20511 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20511 | 6 | 1 | deiTUNEC101WS01DAMPERCON-79LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
468 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-34 | 52 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20521 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20521 | 0 | 2 | deiTUNEC101WS01DAMPERCON-34Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
469 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-34 | 52 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20521 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20521 | 2 | 1 | deiTUNEC101WS01DAMPERCON-34CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
470 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-34 | 52 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20521 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20521 | 4 | 1 | deiTUNEC101WS01DAMPERCON-34TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
471 | EC101_RTU | TUN:EC101 | WS01:DAMPER | MSFD | CON-34 | 52 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20521 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20521 | 6 | 1 | deiTUNEC101WS01DAMPERCON-34LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
472 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-24 | 53 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20531 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20531 | 0 | 2 | deiTUNEC101ES01DAMPERCON-24Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
473 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-24 | 53 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20531 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20531 | 2 | 1 | deiTUNEC101ES01DAMPERCON-24CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
474 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-24 | 53 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20531 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20531 | 4 | 1 | deiTUNEC101ES01DAMPERCON-24TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
475 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-24 | 53 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20531 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20531 | 6 | 1 | deiTUNEC101ES01DAMPERCON-24LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
476 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-42 | 54 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20541 | 0 | 2 | Check SWC Name |  | EC101-SIL2_Monitoring |  | EC101_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20541 | 0 | 2 | deiTUNEC101ES01DAMPERCON-42Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
477 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-42 | 54 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20541 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20541 | 2 | 1 | deiTUNEC101ES01DAMPERCON-42CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
478 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-42 | 54 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20541 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20541 | 4 | 1 | deiTUNEC101ES01DAMPERCON-42TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
479 | EC101_RTU | TUN:EC101 | ES01:DAMPER | MSFD | CON-42 | 54 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20541 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20541 | 6 | 1 | deiTUNEC101ES01DAMPERCON-42LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
480 | EC101_RTU | TUN:EC101 | WS01:AHU | AHU | PLA-01 | 55 | ControlMod | SIL0 | MODBUS:4:Read:Input Registers | 20551 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20551 | 0 | 1 | deiTUNEC101WS01AHUPLA-01ControlMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
481 | EC101_RTU | TUN:EC101 | WS01:AHU | AHU | PLA-01 | 55 | RunStat | SIL0 | MODBUS:4:Read:Input Registers | 20551 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20551 | 1 | 1 | deiTUNEC101WS01AHUPLA-01RunStat | 4 |  |  | 0 | $ComStatus , , | #RUN
482 | EC101_RTU | TUN:EC101 | ES01:AHU | AHU | PLA-02 | 56 | ControlMod | SIL0 | MODBUS:4:Read:Input Registers | 20561 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20561 | 0 | 1 | deiTUNEC101ES01AHUPLA-02ControlMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
483 | EC101_RTU | TUN:EC101 | ES01:AHU | AHU | PLA-02 | 56 | RunStat | SIL0 | MODBUS:4:Read:Input Registers | 20561 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20561 | 1 | 1 | deiTUNEC101ES01AHUPLA-02RunStat | 4 |  |  | 0 | $ComStatus , , | #RUN
484 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | Vac240SwOp | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 0 | 1 | deiTUNEC101MMSSPLC01Vac240SwOp | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY DISCONNECTING SWITCH - OPEN
485 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | Vac240Volt | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 1 | 1 | deiTUNEC101MMSSPLC01Vac240Volt | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY VOLTAGE PRESENCE
486 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | VolOpen | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 2 | 1 | deiTUNEC101MMSSPLC01VolOpen | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER OPEN
487 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | VolFault | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 3 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 3 | 1 | deiTUNEC101MMSSPLC01VolFault | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER FAULT
488 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | VolSupOpen | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 4 | 1 | deiTUNEC101MMSSPLC01VolSupOpen | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN
489 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | VolSupFault | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 5 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 5 | 1 | deiTUNEC101MMSSPLC01VolSupFault | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT
490 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | CabOpen | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 6 | 1 | deiTUNEC101MMSSPLC01CabOpen | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS OPEN
491 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | CabFault | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 7 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 7 | 1 | deiTUNEC101MMSSPLC01CabFault | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS FAULT
492 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | SerOpen | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 8 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 8 | 1 | deiTUNEC101MMSSPLC01SerOpen | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER OPEN
493 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | SerFault | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 9 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 9 | 1 | deiTUNEC101MMSSPLC01SerFault | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER FAULT
494 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | UpsBreOpen | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 10 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 10 | 1 | deiTUNEC101MMSSPLC01UpsBreOpen | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER OPEN
495 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | UpsBreFault | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 11 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 11 | 1 | deiTUNEC101MMSSPLC01UpsBreFault | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER FAULT
496 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | UpsSwOpen | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 12 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 12 | 1 | deiTUNEC101MMSSPLC01UpsSwOpen | 4 |  |  | 0 | $ComStatus , , | #UPS DISCONNECTING SWITCH OPEN
497 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | UpsFault | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 13 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 13 | 1 | deiTUNEC101MMSSPLC01UpsFault | 4 |  |  | 0 | $ComStatus , , | #UPS FAULT
498 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | Sup24Vdc1Open | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 14 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 14 | 1 | deiTUNEC101MMSSPLC01Sup24Vdc1Open | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN
499 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | Sup24Vdc1Fault | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 15 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 15 | 1 | deiTUNEC101MMSSPLC01Sup24Vdc1Fault | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT
500 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | Sup24Vdc1Volt | SIL0 | MODBUS:4:Read:Input Registers | 20572 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20572 | 0 | 1 | deiTUNEC101MMSSPLC01Sup24Vdc1Volt | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 ABSENCE OF VOLTAGE
501 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | Sup24Vdc2Open | SIL0 | MODBUS:4:Read:Input Registers | 20572 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20572 | 1 | 1 | deiTUNEC101MMSSPLC01Sup24Vdc2Open | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN
502 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | Sup24Vdc2Fault | SIL0 | MODBUS:4:Read:Input Registers | 20572 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20572 | 2 | 1 | deiTUNEC101MMSSPLC01Sup24Vdc2Fault | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT
503 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | Sup24Vdc2Volt | SIL0 | MODBUS:4:Read:Input Registers | 20572 | 3 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20572 | 3 | 1 | deiTUNEC101MMSSPLC01Sup24Vdc2Volt | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 ABSENCE OF VOLTAGE
504 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | SwOpen | SIL0 | MODBUS:4:Read:Input Registers | 20572 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20572 | 4 | 1 | deiTUNEC101MMSSPLC01SwOpen | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER OPEN
505 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | SwFault | SIL0 | MODBUS:4:Read:Input Registers | 20572 | 5 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20572 | 5 | 1 | deiTUNEC101MMSSPLC01SwFault | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER FAULT
506 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | LcpOpen | SIL0 | MODBUS:4:Read:Input Registers | 20572 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20572 | 6 | 1 | deiTUNEC101MMSSPLC01LcpOpen | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER OPEN
507 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | LcpFault | SIL0 | MODBUS:4:Read:Input Registers | 20572 | 7 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20572 | 7 | 1 | deiTUNEC101MMSSPLC01LcpFault | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER FAULT
508 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | Plc1Open | SIL0 | MODBUS:4:Read:Input Registers | 20572 | 8 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20572 | 8 | 1 | deiTUNEC101MMSSPLC01Plc1Open | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER OPEN
509 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | Plc1Fault | SIL0 | MODBUS:4:Read:Input Registers | 20572 | 9 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20572 | 9 | 1 | deiTUNEC101MMSSPLC01Plc1Fault | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER FAULT
510 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | Plc2Open | SIL0 | MODBUS:4:Read:Input Registers | 20572 | 10 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20572 | 10 | 1 | deiTUNEC101MMSSPLC01Plc2Open | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER OPEN
511 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | Plc2Fault | SIL0 | MODBUS:4:Read:Input Registers | 20572 | 11 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20572 | 11 | 1 | deiTUNEC101MMSSPLC01Plc2Fault | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER FAULT
512 | EC101_RTU | TUN:EC101 | MMS | SPLCMMS | SPLC01 | 57 | SuArTrig | SIL0 | MODBUS:4:Read:Input Registers | 20572 | 12 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20572 | 12 | 1 | deiTUNEC101MMSSPLC01SuArTrig | 4 |  |  | 0 | $ComStatus , , | #SURGE ARRESTER TRIGGERED
513 | EC101_RTU | TUN:EC101 | MMS | ADS | EL0-LBS01 | 58 | LoadClose | SIL0 | MODBUS:4:Read:Input Registers | 20581 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20581 | 0 | 1 | deiTUNEC101MMSEL0-LBS01LoadClose | 4 |  |  | 0 | $ComStatus , , | #Load breaker switched closed
514 | EC101_RTU | TUN:EC101 | MMS | ADS | EL0-LBS01 | 58 | LbsPos | SIL0 | MODBUS:4:Read:Input Registers | 20581 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20581 | 1 | 1 | deiTUNEC101MMSEL0-LBS01LbsPos | 4 |  |  | 0 | $ComStatus , , | #LBS Auxiliary Switch racked position
515 | EC101_RTU | TUN:EC101 | MMS | ADS | EL0-LBS02 | 59 | LoadClose | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 0 | 1 | deiTUNEC101MMSEL0-LBS02LoadClose | 4 |  |  | 0 | $ComStatus , , | #Load breaker switched closed
516 | EC101_RTU | TUN:EC101 | MMS | ADS | EL0-LBS02 | 59 | LbsPos | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 1 | 1 | deiTUNEC101MMSEL0-LBS02LbsPos | 4 |  |  | 0 | $ComStatus , , | #LBS Auxiliary Switch racked position
517 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF01 | 60 | EmOff | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 0 | 1 | deiTUNEC101MMSMV-TRF01EmOff | 4 |  |  | 0 | $ComStatus , , | #Emergency power off
518 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF01 | 60 | TranFault | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 1 | 1 | deiTUNEC101MMSMV-TRF01TranFault | 4 |  |  | 0 | $ComStatus , , | #Transformer fault
519 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF01 | 60 | EmCut | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 2 | 1 | deiTUNEC101MMSMV-TRF01EmCut | 4 |  |  | 0 | $ComStatus , , | #Emergency power cut
520 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF01 | 60 | PAlarm | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 3 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 3 | 1 | deiTUNEC101MMSMV-TRF01PAlarm | 4 |  |  | 0 | $ComStatus , , | #Transformer high Temperature pre alarm
521 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF01 | 60 | Alarm | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 4 | 1 | deiTUNEC101MMSMV-TRF01Alarm | 4 |  |  | 0 | $ComStatus , , | #Transformer high Temperature Alarm
522 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF02 | 61 | EmOff | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 0 | 1 | deiTUNEC101MMSMV-TRF02EmOff | 4 |  |  | 0 | $ComStatus , , | #Emergency power off
523 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF02 | 61 | TranFault | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 1 | 1 | deiTUNEC101MMSMV-TRF02TranFault | 4 |  |  | 0 | $ComStatus , , | #Transformer fault
524 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF02 | 61 | EmCut | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 2 | 1 | deiTUNEC101MMSMV-TRF02EmCut | 4 |  |  | 0 | $ComStatus , , | #Emergency power cut
525 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF02 | 61 | PAlarm | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 3 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 3 | 1 | deiTUNEC101MMSMV-TRF02PAlarm | 4 |  |  | 0 | $ComStatus , , | #Transformer high Temperature pre alarm
526 | EC101_RTU | TUN:EC101 | MMS | TRF | MV-TRF02 | 61 | Alarm | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 4 | 1 | deiTUNEC101MMSMV-TRF02Alarm | 4 |  |  | 0 | $ComStatus , , | #Transformer high Temperature Alarm
527 | EC101_RTU | TUN:EC101 | MMS | ACB | EL0-CBC01 | 62 | Fault | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 0 | 1 | deiTUNEC101MMSEL0-CBC01Fault | 4 |  |  | 0 | $ComStatus , , | #Main circuit breaker fault
528 | EC101_RTU | TUN:EC101 | MMS | ACB | EL0-CBC01 | 62 | Status | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 1 | 1 | deiTUNEC101MMSEL0-CBC01Status | 4 |  |  | 0 | $ComStatus , , | #Main circuit breaker open/closed status
529 | EC101_RTU | TUN:EC101 | MMS | ACB | EL0-CBC01 | 62 | Position | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 2 | 1 | deiTUNEC101MMSEL0-CBC01Position | 4 |  |  | 0 | $ComStatus , , | #Main CBC ACB racked position
530 | EC101_RTU | TUN:EC101 | MMS | ACB | EL0-CBC02 | 63 | Fault | SIL0 | MODBUS:4:Read:Input Registers | 20631 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20631 | 0 | 1 | deiTUNEC101MMSEL0-CBC02Fault | 4 |  |  | 0 | $ComStatus , , | #Main circuit breaker fault
531 | EC101_RTU | TUN:EC101 | MMS | ACB | EL0-CBC02 | 63 | Status | SIL0 | MODBUS:4:Read:Input Registers | 20631 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20631 | 1 | 1 | deiTUNEC101MMSEL0-CBC02Status | 4 |  |  | 0 | $ComStatus , , | #Main circuit breaker open/closed status
532 | EC101_RTU | TUN:EC101 | MMS | ACB | EL0-CBC02 | 63 | Position | SIL0 | MODBUS:4:Read:Input Registers | 20631 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20631 | 2 | 1 | deiTUNEC101MMSEL0-CBC02Position | 4 |  |  | 0 | $ComStatus , , | #Main CBC ACB racked position
533 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 64 | Mcsd1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 0 | 1 | deiTUNEC101MMSLPS-MDB01Mcsd1Stat | 4 |  |  | 0 | $ComStatus , , | #Power normal MCSD 1 status
534 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 64 | Mcsd2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 1 | 1 | deiTUNEC101MMSLPS-MDB01Mcsd2Stat | 4 |  |  | 0 | $ComStatus , , | #Power replacement MCSD 2 status
535 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 64 | Mcsd1pos | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 2 | 1 | deiTUNEC101MMSLPS-MDB01Mcsd1pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 1 racked position
536 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 64 | Mcsd2pos | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 3 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 3 | 1 | deiTUNEC101MMSLPS-MDB01Mcsd2pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 2 racked position
537 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 64 | Change | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 4 | 1 | deiTUNEC101MMSLPS-MDB01Change | 4 |  |  | 0 | $ComStatus , , | #Change over
538 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 64 | relay1 | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 5 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 5 | 1 | deiTUNEC101MMSLPS-MDB01relay1 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 1
539 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 64 | relay2 | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 6 | 1 | deiTUNEC101MMSLPS-MDB01relay2 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 2
540 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 64 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 7 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 7 | 1 | deiTUNEC101MMSLPS-MDB01Closed | 4 |  |  | 0 | $ComStatus , , | #MCB closed status
541 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 64 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 8 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 8 | 1 | deiTUNEC101MMSLPS-MDB01Trip | 4 |  |  | 0 | $ComStatus , , | #MCB tripped status
542 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 64 | PowerCut | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 9 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 9 | 1 | deiTUNEC101MMSLPS-MDB01PowerCut | 4 |  |  | 0 | $ComStatus , , | #Emergency power cut (push button)
543 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 64 | Mccb1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 10 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 10 | 1 | deiTUNEC101MMSLPS-MDB01Mccb1Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 status
544 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 64 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 11 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 11 | 1 | deiTUNEC101MMSLPS-MDB01Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 trip
545 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 64 | Mccb2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 12 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 12 | 1 | deiTUNEC101MMSLPS-MDB01Mccb2Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 status
546 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 64 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 13 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 13 | 1 | deiTUNEC101MMSLPS-MDB01Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 trip
547 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 64 | Mccb3Stat | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 14 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 14 | 1 | deiTUNEC101MMSLPS-MDB01Mccb3Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 status
548 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB01 | 64 | Mccb3Trip | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 15 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 15 | 1 | deiTUNEC101MMSLPS-MDB01Mccb3Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 trip
549 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 65 | Mcsd1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 0 | 1 | deiTUNEC101MMSLPS-MDB02Mcsd1Stat | 4 |  |  | 0 | $ComStatus , , | #Power normal MCSD 1 status
550 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 65 | Mcsd2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 1 | 1 | deiTUNEC101MMSLPS-MDB02Mcsd2Stat | 4 |  |  | 0 | $ComStatus , , | #Power replacement MCSD 2 status
551 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 65 | Mcsd1pos | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 2 | 1 | deiTUNEC101MMSLPS-MDB02Mcsd1pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 1 racked position
552 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 65 | Mcsd2pos | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 3 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 3 | 1 | deiTUNEC101MMSLPS-MDB02Mcsd2pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 2 racked position
553 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 65 | Change | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 4 | 1 | deiTUNEC101MMSLPS-MDB02Change | 4 |  |  | 0 | $ComStatus , , | #Change over
554 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 65 | relay1 | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 5 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 5 | 1 | deiTUNEC101MMSLPS-MDB02relay1 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 1
555 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 65 | relay2 | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 6 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 6 | 1 | deiTUNEC101MMSLPS-MDB02relay2 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 2
556 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 65 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 7 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 7 | 1 | deiTUNEC101MMSLPS-MDB02Closed | 4 |  |  | 0 | $ComStatus , , | #MCB closed status
557 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 65 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 8 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 8 | 1 | deiTUNEC101MMSLPS-MDB02Trip | 4 |  |  | 0 | $ComStatus , , | #MCB tripped status
558 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 65 | PowerCut | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 9 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 9 | 1 | deiTUNEC101MMSLPS-MDB02PowerCut | 4 |  |  | 0 | $ComStatus , , | #Emergency power cut (push button)
559 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 65 | Mccb1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 10 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 10 | 1 | deiTUNEC101MMSLPS-MDB02Mccb1Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 status
560 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 65 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 11 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 11 | 1 | deiTUNEC101MMSLPS-MDB02Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 trip
561 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 65 | Mccb2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 12 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 12 | 1 | deiTUNEC101MMSLPS-MDB02Mccb2Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 status
562 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 65 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 13 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 13 | 1 | deiTUNEC101MMSLPS-MDB02Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 trip
563 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 65 | Mccb3Stat | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 14 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 14 | 1 | deiTUNEC101MMSLPS-MDB02Mccb3Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 status
564 | EC101_RTU | TUN:EC101 | MMS | MDB | LPS-MDB02 | 65 | Mccb3Trip | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 15 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 15 | 1 | deiTUNEC101MMSLPS-MDB02Mccb3Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 trip
565 | EC101_RTU | TUN:EC101 | MMS | EL | EL1-IO01 | 66 | Relay | SIL0 | MODBUS:4:Read:Input Registers | 20661 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20661 | 0 | 1 | deiTUNEC101MMSEL1-IO01Relay | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay
566 | EC101_RTU | TUN:EC101 | MMS | EL | EL1-IO01 | 66 | Isolator | SIL0 | MODBUS:4:Read:Input Registers | 20661 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20661 | 1 | 1 | deiTUNEC101MMSEL1-IO01Isolator | 4 |  |  | 0 | $ComStatus , , | #LBS Main incomer isolator status
567 | EC101_RTU | TUN:EC101 | MMS | EL | EL1-IO01 | 66 | Supply | SIL0 | MODBUS:4:Read:Input Registers | 20661 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20661 | 2 | 1 | deiTUNEC101MMSEL1-IO01Supply | 4 |  |  | 0 | $ComStatus , , | #UPS supply status
568 | EC101_RTU | TUN:EC101 | MMS | EL | EL1-IO01 | 66 | Faulty | SIL0 | MODBUS:4:Read:Input Registers | 20661 | 3 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20661 | 3 | 1 | deiTUNEC101MMSEL1-IO01Faulty | 4 |  |  | 0 | $ComStatus , , | #UPS faulty
569 | EC101_RTU | TUN:EC101 | MMS | EL | EL1-IO01 | 66 | Power | SIL0 | MODBUS:4:Read:Input Registers | 20661 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20661 | 4 | 1 | deiTUNEC101MMSEL1-IO01Power | 4 |  |  | 0 | $ComStatus , , | #24VDC UPS power status
570 | EC101_RTU | TUN:EC101 | MMS | MCB | EL0-LBS01 | 67 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 0 | 1 | deiTUNEC101MMSEL0-LBS01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
571 | EC101_RTU | TUN:EC101 | MMS | MCB | EL0-LBS01 | 67 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 1 | 1 | deiTUNEC101MMSEL0-LBS01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
572 | EC101_RTU | TUN:EC101 | MMS | MCB | EL0-LBS02 | 68 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20681 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20681 | 0 | 1 | deiTUNEC101MMSEL0-LBS02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
573 | EC101_RTU | TUN:EC101 | MMS | MCB | EL0-LBS02 | 68 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20681 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20681 | 1 | 1 | deiTUNEC101MMSEL0-LBS02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
574 | EC101_RTU | TUN:EC101 | MMS | MCB | EL0-CBC01 | 69 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20691 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20691 | 0 | 1 | deiTUNEC101MMSEL0-CBC01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
575 | EC101_RTU | TUN:EC101 | MMS | MCB | EL0-CBC01 | 69 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20691 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20691 | 1 | 1 | deiTUNEC101MMSEL0-CBC01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
576 | EC101_RTU | TUN:EC101 | MMS | MCB | EL0-CBC02 | 70 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20701 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20701 | 0 | 1 | deiTUNEC101MMSEL0-CBC02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
577 | EC101_RTU | TUN:EC101 | MMS | MCB | EL0-CBC02 | 70 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20701 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20701 | 1 | 1 | deiTUNEC101MMSEL0-CBC02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
578 | EC101_RTU | TUN:EC101 | MMS | MCCB | EL1-UPS | 71 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20711 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20711 | 0 | 1 | deiTUNEC101MMSEL1-UPSTrip | 4 |  |  | 0 | $ComStatus , , | #MCCB trip status
579 | EC101_RTU | TUN:EC101 | MMS | MCCB | EL1-UPS | 71 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20711 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20711 | 1 | 1 | deiTUNEC101MMSEL1-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #MCCB closed status
580 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL0-LBS01 | 72 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20721 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20721 | 0 | 1 | deiTUNEC101MMSUPS_EL0-LBS01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
581 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL0-LBS01 | 72 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20721 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20721 | 1 | 1 | deiTUNEC101MMSUPS_EL0-LBS01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
582 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL0-LBS02 | 73 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20731 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20731 | 0 | 1 | deiTUNEC101MMSUPS_EL0-LBS02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
583 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL0-LBS02 | 73 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20731 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20731 | 1 | 1 | deiTUNEC101MMSUPS_EL0-LBS02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
584 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL0-CBC01 | 74 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 0 | 1 | deiTUNEC101MMSUPS_EL0-CBC01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
585 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL0-CBC01 | 74 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 1 | 1 | deiTUNEC101MMSUPS_EL0-CBC01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
586 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL0-CBC02 | 75 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 0 | 1 | deiTUNEC101MMSUPS_EL0-CBC02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
587 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL0-CBC02 | 75 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 1 | 1 | deiTUNEC101MMSUPS_EL0-CBC02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
588 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL1-VSD01 | 76 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 0 | 1 | deiTUNEC101MMSUPS_EL1-VSD01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
589 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL1-VSD01 | 76 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 1 | 1 | deiTUNEC101MMSUPS_EL1-VSD01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
590 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL1-VSD02 | 77 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20771 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20771 | 0 | 1 | deiTUNEC101MMSUPS_EL1-VSD02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
591 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL1-VSD02 | 77 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20771 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20771 | 1 | 1 | deiTUNEC101MMSUPS_EL1-VSD02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
592 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT3-IDP01 | 78 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20781 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20781 | 0 | 1 | deiTUNEC101MMS3P-VT3-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
593 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT3-IDP01 | 78 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20781 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20781 | 1 | 1 | deiTUNEC101MMS3P-VT3-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
594 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT3-IDP01 | 79 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20791 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20791 | 0 | 1 | deiTUNEC101MMS2P-VT3-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
595 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT3-IDP01 | 79 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20791 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20791 | 1 | 1 | deiTUNEC101MMS2P-VT3-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
596 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT4-IDP01 | 80 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20801 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20801 | 0 | 1 | deiTUNEC101MMS3P-VT4-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
597 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT4-IDP01 | 80 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20801 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20801 | 1 | 1 | deiTUNEC101MMS3P-VT4-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
598 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT4-IDP01 | 81 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20811 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20811 | 0 | 1 | deiTUNEC101MMS2P-VT4-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
599 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT4-IDP01 | 81 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20811 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20811 | 1 | 1 | deiTUNEC101MMS2P-VT4-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
600 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT6-TDP01-01 | 82 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20821 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20821 | 0 | 1 | deiTUNEC101MMS3P-VT6-TDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
601 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT6-TDP01-01 | 82 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20821 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20821 | 1 | 1 | deiTUNEC101MMS3P-VT6-TDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
602 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT6-TDP01-01 | 83 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20831 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20831 | 0 | 1 | deiTUNEC101MMS2P-VT6-TDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
603 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT6-TDP01-01 | 83 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20831 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20831 | 1 | 1 | deiTUNEC101MMS2P-VT6-TDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
604 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT6-TDP01-02 | 84 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20841 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20841 | 0 | 1 | deiTUNEC101MMS3P-VT6-TDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
605 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT6-TDP01-02 | 84 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20841 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20841 | 1 | 1 | deiTUNEC101MMS3P-VT6-TDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
606 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT6-TDP01-02 | 85 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20851 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20851 | 0 | 1 | deiTUNEC101MMS2P-VT6-TDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
607 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT6-TDP01-02 | 85 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20851 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20851 | 1 | 1 | deiTUNEC101MMS2P-VT6-TDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
608 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT6-TDP01-03 | 86 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20861 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20861 | 0 | 1 | deiTUNEC101MMS3P-VT6-TDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
609 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT6-TDP01-03 | 86 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20861 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20861 | 1 | 1 | deiTUNEC101MMS3P-VT6-TDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
610 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT6-TDP01-03 | 87 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20871 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20871 | 0 | 1 | deiTUNEC101MMS2P-VT6-TDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
611 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT6-TDP01-03 | 87 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20871 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20871 | 1 | 1 | deiTUNEC101MMS2P-VT6-TDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
612 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P--FR2-BDP01-01 | 88 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20881 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20881 | 0 | 1 | deiTUNEC101MMS3P--FR2-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
613 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P--FR2-BDP01-01 | 88 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20881 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20881 | 1 | 1 | deiTUNEC101MMS3P--FR2-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
614 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P--FR2-BDP01-01 | 89 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20891 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20891 | 0 | 1 | deiTUNEC101MMS2P--FR2-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
615 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P--FR2-BDP01-01 | 89 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20891 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20891 | 1 | 1 | deiTUNEC101MMS2P--FR2-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
616 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P--FR2-BDP01-02 | 90 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20901 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20901 | 0 | 1 | deiTUNEC101MMS3P--FR2-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
617 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P--FR2-BDP01-02 | 90 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20901 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20901 | 1 | 1 | deiTUNEC101MMS3P--FR2-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
618 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P--FR2-BDP01-02 | 91 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20911 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20911 | 0 | 1 | deiTUNEC101MMS2P--FR2-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
619 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P--FR2-BDP01-02 | 91 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20911 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20911 | 1 | 1 | deiTUNEC101MMS2P--FR2-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
620 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-24 | 92 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20921 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20921 | 0 | 1 | deiTUNEC101MMSMSFD-CON-24McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
621 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-24 | 92 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20921 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20921 | 1 | 1 | deiTUNEC101MMSMSFD-CON-24McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
622 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-42 | 93 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20931 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20931 | 0 | 1 | deiTUNEC101MMSMSFD-CON-42McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
623 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-42 | 93 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20931 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20931 | 1 | 1 | deiTUNEC101MMSMSFD-CON-42McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
624 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-33 | 94 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20941 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20941 | 0 | 1 | deiTUNEC101MMSMSFD-CON-33McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
625 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-33 | 94 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20941 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20941 | 1 | 1 | deiTUNEC101MMSMSFD-CON-33McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
626 | EC101_RTU | TUN:EC101 | MMS | EL | EL2-IO01 | 95 | Relay | SIL0 | MODBUS:4:Read:Input Registers | 20951 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20951 | 0 | 1 | deiTUNEC101MMSEL2-IO01Relay | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay
627 | EC101_RTU | TUN:EC101 | MMS | EL | EL2-IO01 | 95 | Isolator | SIL0 | MODBUS:4:Read:Input Registers | 20951 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20951 | 1 | 1 | deiTUNEC101MMSEL2-IO01Isolator | 4 |  |  | 0 | $ComStatus , , | #LBS Main incomer isolator status
628 | EC101_RTU | TUN:EC101 | MMS | EL | EL2-IO01 | 95 | Supply | SIL0 | MODBUS:4:Read:Input Registers | 20951 | 2 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20951 | 2 | 1 | deiTUNEC101MMSEL2-IO01Supply | 4 |  |  | 0 | $ComStatus , , | #UPS supply status
629 | EC101_RTU | TUN:EC101 | MMS | EL | EL2-IO01 | 95 | Faulty | SIL0 | MODBUS:4:Read:Input Registers | 20951 | 3 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20951 | 3 | 1 | deiTUNEC101MMSEL2-IO01Faulty | 4 |  |  | 0 | $ComStatus , , | #UPS faulty
630 | EC101_RTU | TUN:EC101 | MMS | EL | EL2-IO01 | 95 | Power | SIL0 | MODBUS:4:Read:Input Registers | 20951 | 4 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20951 | 4 | 1 | deiTUNEC101MMSEL2-IO01Power | 4 |  |  | 0 | $ComStatus , , | #24VDC UPS power status
631 | EC101_RTU | TUN:EC101 | MMS | MCCB | EL2-UPS | 96 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20961 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20961 | 0 | 1 | deiTUNEC101MMSEL2-UPSTrip | 4 |  |  | 0 | $ComStatus , , | #MCCB trip status
632 | EC101_RTU | TUN:EC101 | MMS | MCCB | EL2-UPS | 96 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20961 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20961 | 1 | 1 | deiTUNEC101MMSEL2-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #MCCB closed status
633 | EC101_RTU | TUN:EC101 | MMS | LBS | EL2-UPS | 97 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20971 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20971 | 0 | 1 | deiTUNEC101MMSEL2-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #LBS closed status
634 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL2-VSD01 | 98 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20981 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20981 | 0 | 1 | deiTUNEC101MMSUPS_EL2-VSD01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
635 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL2-VSD01 | 98 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20981 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20981 | 1 | 1 | deiTUNEC101MMSUPS_EL2-VSD01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
636 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL2-VSD02 | 99 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20991 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20991 | 0 | 1 | deiTUNEC101MMSUPS_EL2-VSD02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
637 | EC101_RTU | TUN:EC101 | MMS | MCB | UPS_EL2-VSD02 | 99 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20991 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20991 | 1 | 1 | deiTUNEC101MMSUPS_EL2-VSD02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
638 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT1-IDP01 | 100 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21001 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21001 | 0 | 1 | deiTUNEC101MMS3P-VT1-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
639 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT1-IDP01 | 100 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21001 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21001 | 1 | 1 | deiTUNEC101MMS3P-VT1-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
640 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT1-IDP01 | 101 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21011 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21011 | 0 | 1 | deiTUNEC101MMS2P-VT1-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
641 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT1-IDP01 | 101 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21011 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21011 | 1 | 1 | deiTUNEC101MMS2P-VT1-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
642 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT2-IDP01 | 102 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21021 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21021 | 0 | 1 | deiTUNEC101MMS3P-VT2-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
643 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT2-IDP01 | 102 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21021 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21021 | 1 | 1 | deiTUNEC101MMS3P-VT2-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
644 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT2-IDP01 | 103 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21031 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21031 | 0 | 1 | deiTUNEC101MMS2P-VT2-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
645 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT2-IDP01 | 103 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21031 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21031 | 1 | 1 | deiTUNEC101MMS2P-VT2-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
646 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT5-IDP01-01 | 104 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21041 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21041 | 0 | 1 | deiTUNEC101MMS3P-VT5-IDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
647 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT5-IDP01-01 | 104 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21041 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21041 | 1 | 1 | deiTUNEC101MMS3P-VT5-IDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
648 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT5-IDP01-01 | 105 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21051 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21051 | 0 | 1 | deiTUNEC101MMS2P-VT5-IDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
649 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT5-IDP01-01 | 105 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21051 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21051 | 1 | 1 | deiTUNEC101MMS2P-VT5-IDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
650 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT5-IDP01-02 | 106 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21061 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21061 | 0 | 1 | deiTUNEC101MMS3P-VT5-IDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
651 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT5-IDP01-02 | 106 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21061 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21061 | 1 | 1 | deiTUNEC101MMS3P-VT5-IDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
652 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT5-IDP01-02 | 107 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21071 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21071 | 0 | 1 | deiTUNEC101MMS2P-VT5-IDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
653 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT5-IDP01-02 | 107 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21071 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21071 | 1 | 1 | deiTUNEC101MMS2P-VT5-IDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
654 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT5-IDP01-03 | 108 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21081 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21081 | 0 | 1 | deiTUNEC101MMS3P-VT5-IDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
655 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-VT5-IDP01-03 | 108 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21081 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21081 | 1 | 1 | deiTUNEC101MMS3P-VT5-IDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
656 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT5-IDP01-03 | 109 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21091 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21091 | 0 | 1 | deiTUNEC101MMS2P-VT5-IDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
657 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-VT5-IDP01-03 | 109 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21091 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21091 | 1 | 1 | deiTUNEC101MMS2P-VT5-IDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
658 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-FR1-BDP01-01 | 110 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21101 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21101 | 0 | 1 | deiTUNEC101MMS3P-FR1-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
659 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-FR1-BDP01-01 | 110 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21101 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21101 | 1 | 1 | deiTUNEC101MMS3P-FR1-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
660 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-FR1-BDP01-01 | 111 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21111 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21111 | 0 | 1 | deiTUNEC101MMS2P-FR1-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
661 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-FR1-BDP01-01 | 111 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21111 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21111 | 1 | 1 | deiTUNEC101MMS2P-FR1-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
662 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-FR1-BDP01-02 | 112 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21121 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21121 | 0 | 1 | deiTUNEC101MMS3P-FR1-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
663 | EC101_RTU | TUN:EC101 | MMS | MCB | 3P-FR1-BDP01-02 | 112 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21121 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21121 | 1 | 1 | deiTUNEC101MMS3P-FR1-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
664 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-FR1-BDP01-02 | 113 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21131 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21131 | 0 | 1 | deiTUNEC101MMS2P-FR1-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
665 | EC101_RTU | TUN:EC101 | MMS | MCB | 2P-FR1-BDP01-02 | 113 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21131 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21131 | 1 | 1 | deiTUNEC101MMS2P-FR1-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
666 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-79 | 114 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21141 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21141 | 0 | 1 | deiTUNEC101MMSMSFD-CON-79McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
667 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-79 | 114 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21141 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21141 | 1 | 1 | deiTUNEC101MMSMSFD-CON-79McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
668 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-34 | 115 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21151 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21151 | 0 | 1 | deiTUNEC101MMSMSFD-CON-34McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
669 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-34 | 115 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21151 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21151 | 1 | 1 | deiTUNEC101MMSMSFD-CON-34McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
670 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-68 | 116 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21161 | 0 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21161 | 0 | 1 | deiTUNEC101MMSMSFD-CON-68McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
671 | EC101_RTU | TUN:EC101 | MMS | MCB | MSFD-CON-68 | 116 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21161 | 1 | 1 | Check SWC Name |  | EC101-SIL0 |  | EC101_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21161 | 1 | 1 | deiTUNEC101MMSMSFD-CON-68McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
672 | EC10A_RTU | TUN:EC10A | SCR | LCP | LCP01 | 1 | ComFaultPlc | SIL0 | MODBUS:4:Read:Input Registers | 20011 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20011 | 0 | 1 | deiTUNEC10ASCRLCP01ComFaultPlc | 4 |  |  | 0 | $ComStatus , , | #COMMUNICATION FAULT WITH PLC
673 | EC10A_RTU | TUN:EC10A | SCR | LCP | LCP01 | 1 | LcpMode | SIL0 | MODBUS:4:Read:Input Registers | 20011 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20011 | 1 | 1 | deiTUNEC10ASCRLCP01LcpMode | 4 |  |  | 0 | $ComStatus , , | #LOCAL / REMOTE STATUS
674 | EC10A_RTU | TUN:EC10A | SCR | FMOP | FMOP01 | 2 | EmergNod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20021 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20021 | 0 | 1 | deiTUNEC10ASCRFMOP01EmergNod | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
675 | EC10A_RTU | TUN:EC10A | SCR | FMOP | FMOP01 | 2 | RightStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20021 | 1 | 1 | Check SWC Name |  | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20021 | 1 | 1 | deiTUNEC10ASCRFMOP01RightStat | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
676 | EC10A_RTU | TUN:EC10A | SCR | FMOP | FMOP01 | 2 | LeftStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20021 | 2 | 1 | Check SWC Name |  | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20021 | 2 | 1 | deiTUNEC10ASCRFMOP01LeftStat | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
677 | EC10A_RTU | TUN:EC10A | TEL | SPLC | PLC01 | 3 | PlcState | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 0 | 1 | deiTUNEC10ATELPLC01PlcState | 4 |  |  | 0 | $ComStatus , , | #PLC A/B OFFLINE
678 | EC10A_RTU | TUN:EC10A | TEL | SPLC | PLC01 | 3 | OpStatus | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 1 | 1 | deiTUNEC10ATELPLC01OpStatus | 4 |  |  | 0 | $ComStatus , , | #PLC RUNNING.
679 | EC10A_RTU | TUN:EC10A | TEL | SPLC | PLC01 | 3 | PwStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 2 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 2 | 1 | deiTUNEC10ATELPLC01PwStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: POWER SUPPLY FAULT
680 | EC10A_RTU | TUN:EC10A | TEL | SPLC | PLC01 | 3 | CpuStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 3 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 3 | 1 | deiTUNEC10ATELPLC01CpuStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CPU MODULE FAULT
681 | EC10A_RTU | TUN:EC10A | TEL | SPLC | PLC01 | 3 | CrpStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 4 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 4 | 1 | deiTUNEC10ATELPLC01CrpStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CRP MODULE FAULT
682 | EC10A_RTU | TUN:EC10A | TEL | SPLC | PLC01 | 3 | CraStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 5 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 5 | 1 | deiTUNEC10ATELPLC01CraStat | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
683 | EC10A_RTU | TUN:EC10A | TEL | SPLC | PLC01 | 3 | NrpStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 6 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 6 | 1 | deiTUNEC10ATELPLC01NrpStat | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
684 | EC10A_RTU | TUN:EC10A | TEL | SPLC | PLC01 | 3 | ComStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 7 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 7 | 1 | deiTUNEC10ATELPLC01ComStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
685 | EC10A_RTU | TUN:EC10A | TEL | SPLC | PLC01 | 3 | IoStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 8 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 8 | 1 | deiTUNEC10ATELPLC01IoStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
686 | EC10A_RTU | TUN:EC10A | TEL | SWI | SWI01 | 4 | SwStat | SIL0 | MODBUS:4:Read:Input Registers | 20041 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20041 | 0 | 1 | deiTUNEC10ATELSWI01SwStat | 4 |  |  | 0 | $ComStatus , , | #SWITCH FAULT
687 | EC10A_RTU | TUN:EC10A | OTS | OTS | OTS001 | 5 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20051 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20051 | 0 | 1 | deiTUNEC10AOTSOTS001AvailStat | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
688 | EC10A_RTU | TUN:EC10A | OTS | OTS | OTS001 | 5 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20051 | 2 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20051 | 2 | 1 | deiTUNEC10AOTSOTS001AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
689 | EC10A_RTU | TUN:EC10A | OTS | OTS | OTS001 | 5 | TemMeasure | SIL0 | MODBUS:4:Read:Input Registers | 20052 | 0 | 32 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20052 | 0 | 32 | aeiTUNEC10AOTSOTS001TemMeasure | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
690 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100421 | 6 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20061 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20061 | 0 | 1 | deiTUNEC10ASENSORTS100421Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
691 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100421 | 6 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20061 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20061 | 1 | 1 | deiTUNEC10ASENSORTS100421TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
692 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100421 | 6 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20061 | 2 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20061 | 2 | 1 | deiTUNEC10ASENSORTS100421HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
693 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100421 | 6 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20061 | 3 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20061 | 3 | 1 | deiTUNEC10ASENSORTS100421AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
694 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100421 | 6 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20062 | 0 | 32 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20062 | 0 | 32 | aeiTUNEC10ASENSORTS100421Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
695 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100421 | 6 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20064 | 0 | 32 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20064 | 0 | 32 | aeiTUNEC10ASENSORTS100421Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
696 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100521 | 7 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20071 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20071 | 0 | 1 | deiTUNEC10ASENSORTS100521Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
697 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100521 | 7 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20071 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20071 | 1 | 1 | deiTUNEC10ASENSORTS100521TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
698 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100521 | 7 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20071 | 2 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20071 | 2 | 1 | deiTUNEC10ASENSORTS100521HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
699 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100521 | 7 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20071 | 3 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20071 | 3 | 1 | deiTUNEC10ASENSORTS100521AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
700 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100521 | 7 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20072 | 0 | 32 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20072 | 0 | 32 | aeiTUNEC10ASENSORTS100521Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
701 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100521 | 7 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20074 | 0 | 32 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20074 | 0 | 32 | aeiTUNEC10ASENSORTS100521Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
702 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100767 | 8 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20081 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20081 | 0 | 1 | deiTUNEC10ASENSORTS100767Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
703 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100767 | 8 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20081 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20081 | 1 | 1 | deiTUNEC10ASENSORTS100767TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
704 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100767 | 8 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20081 | 2 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20081 | 2 | 1 | deiTUNEC10ASENSORTS100767HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
705 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100767 | 8 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20081 | 3 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20081 | 3 | 1 | deiTUNEC10ASENSORTS100767AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
706 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100767 | 8 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20082 | 0 | 32 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20082 | 0 | 32 | aeiTUNEC10ASENSORTS100767Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
707 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100767 | 8 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20084 | 0 | 32 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20084 | 0 | 32 | aeiTUNEC10ASENSORTS100767Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
708 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100906 | 9 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20091 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20091 | 0 | 1 | deiTUNEC10ASENSORTS100906Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
709 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100906 | 9 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20091 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20091 | 1 | 1 | deiTUNEC10ASENSORTS100906TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
710 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100906 | 9 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20091 | 2 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20091 | 2 | 1 | deiTUNEC10ASENSORTS100906HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
711 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100906 | 9 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20091 | 3 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20091 | 3 | 1 | deiTUNEC10ASENSORTS100906AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
712 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100906 | 9 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20092 | 0 | 32 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20092 | 0 | 32 | aeiTUNEC10ASENSORTS100906Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
713 | EC10A_RTU | TUN:EC10A | SENSOR | TTS | TS100906 | 9 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20094 | 0 | 32 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20094 | 0 | 32 | aeiTUNEC10ASENSORTS100906Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
714 | EC10A_RTU | TUN:EC10A | SENSOR | VS | VS100456 | 10 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20101 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20101 | 0 | 1 | deiTUNEC10ASENSORVS100456Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
715 | EC10A_RTU | TUN:EC10A | SENSOR | VS | VS100456 | 10 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20102 | 0 | 32 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20102 | 0 | 32 | aeiTUNEC10ASENSORVS100456Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
716 | EC10A_RTU | TUN:EC10A | SENSOR | VS | VS100862 | 11 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20111 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20111 | 0 | 1 | deiTUNEC10ASENSORVS100862Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
717 | EC10A_RTU | TUN:EC10A | SENSOR | VS | VS100862 | 11 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20112 | 0 | 32 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20112 | 0 | 32 | aeiTUNEC10ASENSORVS100862Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
718 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20121 | 0 | 2 | Check SWC Name |  | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20121 | 0 | 2 | deiTUNEC10ATVFVT1-TVF01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
719 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20121 | 2 | 1 | Check SWC Name |  | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20121 | 2 | 1 | deiTUNEC10ATVFVT1-TVF01OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
720 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20121 | 4 | 2 | Check SWC Name |  | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20121 | 4 | 2 | deiTUNEC10ATVFVT1-TVF01RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
721 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10241 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10241 | 0 | 1 | deoTUNEC10ATVFVT1-TVF01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
722 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10242 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10242 | 0 | 1 | deoTUNEC10ATVFVT1-TVF01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
723 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20121 | 6 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20121 | 6 | 2 | deiTUNEC10ATVFVT1-TVF01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
724 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10243 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10243 | 0 | 1 | deoTUNEC10ATVFVT1-TVF01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
725 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20121 | 8 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20121 | 8 | 2 | deiTUNEC10ATVFVT1-TVF01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
726 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20121 | 10 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20121 | 10 | 1 | deiTUNEC10ATVFVT1-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
727 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20121 | 12 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20121 | 12 | 1 | deiTUNEC10ATVFVT1-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
728 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20121 | 14 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20121 | 14 | 1 | deiTUNEC10ATVFVT1-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
729 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20122 | 0 | 32 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20122 | 0 | 32 | aeiTUNEC10ATVFVT1-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
730 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10244 | 0 | 2 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10244 | 0 | 2 | deoTUNEC10ATVFVT1-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
731 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10245 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10245 | 0 | 1 | deoTUNEC10ATVFVT1-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
732 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20124 | 0 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20124 | 0 | 2 | deiTUNEC10ATVFVT1-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
733 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10246 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10246 | 0 | 1 | deoTUNEC10ATVFVT1-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
734 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20124 | 2 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20124 | 2 | 2 | deiTUNEC10ATVFVT1-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
735 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10247 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10247 | 0 | 1 | deoTUNEC10ATVFVT1-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
736 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20124 | 4 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20124 | 4 | 2 | deiTUNEC10ATVFVT1-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
737 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10248 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10248 | 0 | 1 | deoTUNEC10ATVFVT1-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
738 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20124 | 6 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20124 | 6 | 2 | deiTUNEC10ATVFVT1-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
739 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10249 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10249 | 0 | 1 | deoTUNEC10ATVFVT1-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
740 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20124 | 8 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20124 | 8 | 2 | deiTUNEC10ATVFVT1-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
741 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10250 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10250 | 0 | 1 | deoTUNEC10ATVFVT1-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
742 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20124 | 10 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20124 | 10 | 2 | deiTUNEC10ATVFVT1-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
743 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20124 | 12 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20124 | 12 | 1 | deiTUNEC10ATVFVT1-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
744 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20124 | 14 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20124 | 14 | 1 | deiTUNEC10ATVFVT1-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
745 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20125 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20125 | 0 | 1 | deiTUNEC10ATVFVT1-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
746 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20125 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20125 | 1 | 1 | deiTUNEC10ATVFVT1-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
747 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20125 | 2 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20125 | 2 | 1 | deiTUNEC10ATVFVT1-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
748 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20125 | 3 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20125 | 3 | 1 | deiTUNEC10ATVFVT1-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
749 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20125 | 4 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20125 | 4 | 1 | deiTUNEC10ATVFVT1-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
750 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20125 | 5 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20125 | 5 | 1 | deiTUNEC10ATVFVT1-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
751 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20125 | 6 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20125 | 6 | 1 | deiTUNEC10ATVFVT1-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
752 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20125 | 7 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20125 | 7 | 1 | deiTUNEC10ATVFVT1-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
753 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20125 | 8 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20125 | 8 | 1 | deiTUNEC10ATVFVT1-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
754 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20125 | 9 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20125 | 9 | 1 | deiTUNEC10ATVFVT1-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
755 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20125 | 10 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20125 | 10 | 1 | deiTUNEC10ATVFVT1-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
756 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20125 | 11 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20125 | 11 | 1 | deiTUNEC10ATVFVT1-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
757 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT1-TVF01 | 12 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20126 | 0 | 16 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20126 | 0 | 16 | aeiTUNEC10ATVFVT1-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
758 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20131 | 0 | 2 | Check SWC Name |  | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20131 | 0 | 2 | deiTUNEC10ATVFVT2-TVF01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
759 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20131 | 2 | 1 | Check SWC Name |  | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20131 | 2 | 1 | deiTUNEC10ATVFVT2-TVF01OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
760 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20131 | 4 | 2 | Check SWC Name |  | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20131 | 4 | 2 | deiTUNEC10ATVFVT2-TVF01RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
761 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10261 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10261 | 0 | 1 | deoTUNEC10ATVFVT2-TVF01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
762 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10262 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10262 | 0 | 1 | deoTUNEC10ATVFVT2-TVF01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
763 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20131 | 6 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20131 | 6 | 2 | deiTUNEC10ATVFVT2-TVF01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
764 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10263 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10263 | 0 | 1 | deoTUNEC10ATVFVT2-TVF01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
765 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20131 | 8 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20131 | 8 | 2 | deiTUNEC10ATVFVT2-TVF01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
766 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20131 | 10 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20131 | 10 | 1 | deiTUNEC10ATVFVT2-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
767 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20131 | 12 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20131 | 12 | 1 | deiTUNEC10ATVFVT2-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
768 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20131 | 14 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20131 | 14 | 1 | deiTUNEC10ATVFVT2-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
769 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20132 | 0 | 32 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20132 | 0 | 32 | aeiTUNEC10ATVFVT2-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
770 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10264 | 0 | 2 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10264 | 0 | 2 | deoTUNEC10ATVFVT2-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
771 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10265 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10265 | 0 | 1 | deoTUNEC10ATVFVT2-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
772 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20134 | 0 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20134 | 0 | 2 | deiTUNEC10ATVFVT2-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
773 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10266 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10266 | 0 | 1 | deoTUNEC10ATVFVT2-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
774 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20134 | 2 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20134 | 2 | 2 | deiTUNEC10ATVFVT2-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
775 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10267 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10267 | 0 | 1 | deoTUNEC10ATVFVT2-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
776 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20134 | 4 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20134 | 4 | 2 | deiTUNEC10ATVFVT2-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
777 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10268 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10268 | 0 | 1 | deoTUNEC10ATVFVT2-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
778 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20134 | 6 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20134 | 6 | 2 | deiTUNEC10ATVFVT2-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
779 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10269 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10269 | 0 | 1 | deoTUNEC10ATVFVT2-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
780 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20134 | 8 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20134 | 8 | 2 | deiTUNEC10ATVFVT2-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
781 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10270 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10270 | 0 | 1 | deoTUNEC10ATVFVT2-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
782 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20134 | 10 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20134 | 10 | 2 | deiTUNEC10ATVFVT2-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
783 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20134 | 12 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20134 | 12 | 1 | deiTUNEC10ATVFVT2-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
784 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20134 | 14 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20134 | 14 | 1 | deiTUNEC10ATVFVT2-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
785 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20135 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20135 | 0 | 1 | deiTUNEC10ATVFVT2-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
786 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20135 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20135 | 1 | 1 | deiTUNEC10ATVFVT2-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
787 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20135 | 2 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20135 | 2 | 1 | deiTUNEC10ATVFVT2-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
788 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20135 | 3 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20135 | 3 | 1 | deiTUNEC10ATVFVT2-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
789 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20135 | 4 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20135 | 4 | 1 | deiTUNEC10ATVFVT2-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
790 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20135 | 5 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20135 | 5 | 1 | deiTUNEC10ATVFVT2-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
791 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20135 | 6 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20135 | 6 | 1 | deiTUNEC10ATVFVT2-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
792 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20135 | 7 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20135 | 7 | 1 | deiTUNEC10ATVFVT2-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
793 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20135 | 8 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20135 | 8 | 1 | deiTUNEC10ATVFVT2-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
794 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20135 | 9 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20135 | 9 | 1 | deiTUNEC10ATVFVT2-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
795 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20135 | 10 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20135 | 10 | 1 | deiTUNEC10ATVFVT2-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
796 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20135 | 11 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20135 | 11 | 1 | deiTUNEC10ATVFVT2-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
797 | EC10A_RTU | TUN:EC10A | TVF | TVF | VT2-TVF01 | 13 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20136 | 0 | 16 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20136 | 0 | 16 | aeiTUNEC10ATVFVT2-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
798 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT1-IDP01 | 14 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20141 | 0 | 2 | Check SWC Name |  | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20141 | 0 | 2 | deiTUNEC10ADAMPERVT1-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
799 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT1-IDP01 | 14 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20141 | 2 | 2 | Check SWC Name |  | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20141 | 2 | 2 | deiTUNEC10ADAMPERVT1-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
800 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT1-IDP01 | 14 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20141 | 4 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20141 | 4 | 1 | deiTUNEC10ADAMPERVT1-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
801 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT1-IDP01 | 14 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20141 | 6 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20141 | 6 | 1 | deiTUNEC10ADAMPERVT1-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
802 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT1-IDP01 | 14 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20141 | 8 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20141 | 8 | 1 | deiTUNEC10ADAMPERVT1-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
803 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT1-IDP01 | 14 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20141 | 10 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20141 | 10 | 1 | deiTUNEC10ADAMPERVT1-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
804 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT2-IDP01 | 15 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20151 | 0 | 2 | Check SWC Name |  | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20151 | 0 | 2 | deiTUNEC10ADAMPERVT2-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
805 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT2-IDP01 | 15 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20151 | 2 | 2 | Check SWC Name |  | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20151 | 2 | 2 | deiTUNEC10ADAMPERVT2-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
806 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT2-IDP01 | 15 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20151 | 4 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20151 | 4 | 1 | deiTUNEC10ADAMPERVT2-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
807 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT2-IDP01 | 15 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20151 | 6 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20151 | 6 | 1 | deiTUNEC10ADAMPERVT2-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
808 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT2-IDP01 | 15 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20151 | 8 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20151 | 8 | 1 | deiTUNEC10ADAMPERVT2-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
809 | EC10A_RTU | TUN:EC10A | DAMPER | IDP | VT2-IDP01 | 15 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20151 | 10 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20151 | 10 | 1 | deiTUNEC10ADAMPERVT2-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
810 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 16 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20161 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20161 | 0 | 1 | deiTUNEC10APFALPF-01ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
811 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 16 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20161 | 2 | 1 | Check SWC Name |  | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20161 | 2 | 1 | deiTUNEC10APFALPF-01OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
812 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 16 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20161 | 4 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20161 | 4 | 1 | deiTUNEC10APFALPF-01AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
813 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 16 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10321 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10321 | 0 | 1 | deoTUNEC10APFALPF-01CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
814 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 16 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10322 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10322 | 0 | 1 | deoTUNEC10APFALPF-01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
815 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 16 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20161 | 6 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20161 | 6 | 2 | deiTUNEC10APFALPF-01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
816 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 16 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10323 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10323 | 0 | 1 | deoTUNEC10APFALPF-01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
817 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 16 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20161 | 8 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20161 | 8 | 2 | deiTUNEC10APFALPF-01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
818 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 16 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10324 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10324 | 0 | 1 | deoTUNEC10APFALPF-01CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
819 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 16 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20161 | 10 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20161 | 10 | 2 | deiTUNEC10APFALPF-01AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
820 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 16 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10325 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10325 | 0 | 1 | deoTUNEC10APFALPF-01CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
821 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 16 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20161 | 12 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20161 | 12 | 2 | deiTUNEC10APFALPF-01AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
822 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 16 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10326 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10326 | 0 | 1 | deoTUNEC10APFALPF-01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
823 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 16 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20161 | 14 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20161 | 14 | 2 | deiTUNEC10APFALPF-01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
824 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 16 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10327 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10327 | 0 | 1 | deoTUNEC10APFALPF-01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
825 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 16 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20162 | 0 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20162 | 0 | 2 | deiTUNEC10APFALPF-01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
826 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 16 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20162 | 2 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20162 | 2 | 1 | deiTUNEC10APFALPF-01StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
827 | EC10A_RTU | TUN:EC10A | PFA | PFA | LPF-01 | 16 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20162 | 4 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20162 | 4 | 1 | deiTUNEC10APFALPF-01StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
828 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 17 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20171 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20171 | 0 | 1 | deiTUNEC10APFASPF-01ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
829 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 17 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20171 | 2 | 1 | Check SWC Name |  | EC10A-SIL2_Monitoring |  | EC10A_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20171 | 2 | 1 | deiTUNEC10APFASPF-01OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
830 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 17 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20171 | 4 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20171 | 4 | 1 | deiTUNEC10APFASPF-01AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
831 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 17 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10341 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10341 | 0 | 1 | deoTUNEC10APFASPF-01CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
832 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 17 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10342 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10342 | 0 | 1 | deoTUNEC10APFASPF-01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
833 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 17 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20171 | 6 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20171 | 6 | 2 | deiTUNEC10APFASPF-01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
834 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 17 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10343 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10343 | 0 | 1 | deoTUNEC10APFASPF-01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
835 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 17 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20171 | 8 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20171 | 8 | 2 | deiTUNEC10APFASPF-01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
836 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 17 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10344 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10344 | 0 | 1 | deoTUNEC10APFASPF-01CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
837 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 17 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20171 | 10 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20171 | 10 | 2 | deiTUNEC10APFASPF-01AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
838 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 17 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10345 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10345 | 0 | 1 | deoTUNEC10APFASPF-01CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
839 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 17 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20171 | 12 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20171 | 12 | 2 | deiTUNEC10APFASPF-01AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
840 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 17 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10346 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10346 | 0 | 1 | deoTUNEC10APFASPF-01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
841 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 17 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20171 | 14 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20171 | 14 | 2 | deiTUNEC10APFASPF-01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
842 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 17 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10347 | 0 | 1 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10347 | 0 | 1 | deoTUNEC10APFASPF-01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
843 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 17 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20172 | 0 | 2 | Check SWC Name |  | EC10A-SIL2_Control |  | EC10A_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20172 | 0 | 2 | deiTUNEC10APFASPF-01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
844 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 17 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20172 | 2 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20172 | 2 | 1 | deiTUNEC10APFASPF-01StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
845 | EC10A_RTU | TUN:EC10A | PFA | PFA | SPF-01 | 17 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20172 | 4 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20172 | 4 | 1 | deiTUNEC10APFASPF-01StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
846 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | Vac240SwOp | SIL0 | MODBUS:4:Read:Input Registers | 20181 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20181 | 0 | 1 | deiTUNEC10AMMSSPLC01Vac240SwOp | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY DISCONNECTING SWITCH - OPEN
847 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | Vac240Volt | SIL0 | MODBUS:4:Read:Input Registers | 20181 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20181 | 1 | 1 | deiTUNEC10AMMSSPLC01Vac240Volt | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY VOLTAGE PRESENCE
848 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | VolOpen | SIL0 | MODBUS:4:Read:Input Registers | 20181 | 2 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20181 | 2 | 1 | deiTUNEC10AMMSSPLC01VolOpen | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER OPEN
849 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | VolFault | SIL0 | MODBUS:4:Read:Input Registers | 20181 | 3 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20181 | 3 | 1 | deiTUNEC10AMMSSPLC01VolFault | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER FAULT
850 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | VolSupOpen | SIL0 | MODBUS:4:Read:Input Registers | 20181 | 4 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20181 | 4 | 1 | deiTUNEC10AMMSSPLC01VolSupOpen | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN
851 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | VolSupFault | SIL0 | MODBUS:4:Read:Input Registers | 20181 | 5 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20181 | 5 | 1 | deiTUNEC10AMMSSPLC01VolSupFault | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT
852 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | CabOpen | SIL0 | MODBUS:4:Read:Input Registers | 20181 | 6 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20181 | 6 | 1 | deiTUNEC10AMMSSPLC01CabOpen | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS OPEN
853 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | CabFault | SIL0 | MODBUS:4:Read:Input Registers | 20181 | 7 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20181 | 7 | 1 | deiTUNEC10AMMSSPLC01CabFault | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS FAULT
854 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | SerOpen | SIL0 | MODBUS:4:Read:Input Registers | 20181 | 8 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20181 | 8 | 1 | deiTUNEC10AMMSSPLC01SerOpen | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER OPEN
855 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | SerFault | SIL0 | MODBUS:4:Read:Input Registers | 20181 | 9 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20181 | 9 | 1 | deiTUNEC10AMMSSPLC01SerFault | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER FAULT
856 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | UpsBreOpen | SIL0 | MODBUS:4:Read:Input Registers | 20181 | 10 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20181 | 10 | 1 | deiTUNEC10AMMSSPLC01UpsBreOpen | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER OPEN
857 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | UpsBreFault | SIL0 | MODBUS:4:Read:Input Registers | 20181 | 11 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20181 | 11 | 1 | deiTUNEC10AMMSSPLC01UpsBreFault | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER FAULT
858 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | UpsSwOpen | SIL0 | MODBUS:4:Read:Input Registers | 20181 | 12 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20181 | 12 | 1 | deiTUNEC10AMMSSPLC01UpsSwOpen | 4 |  |  | 0 | $ComStatus , , | #UPS DISCONNECTING SWITCH OPEN
859 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | UpsFault | SIL0 | MODBUS:4:Read:Input Registers | 20181 | 13 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20181 | 13 | 1 | deiTUNEC10AMMSSPLC01UpsFault | 4 |  |  | 0 | $ComStatus , , | #UPS FAULT
860 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | Sup24Vdc1Open | SIL0 | MODBUS:4:Read:Input Registers | 20181 | 14 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20181 | 14 | 1 | deiTUNEC10AMMSSPLC01Sup24Vdc1Open | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN
861 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | Sup24Vdc1Fault | SIL0 | MODBUS:4:Read:Input Registers | 20181 | 15 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20181 | 15 | 1 | deiTUNEC10AMMSSPLC01Sup24Vdc1Fault | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT
862 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | Sup24Vdc1Volt | SIL0 | MODBUS:4:Read:Input Registers | 20182 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20182 | 0 | 1 | deiTUNEC10AMMSSPLC01Sup24Vdc1Volt | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 ABSENCE OF VOLTAGE
863 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | Sup24Vdc2Open | SIL0 | MODBUS:4:Read:Input Registers | 20182 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20182 | 1 | 1 | deiTUNEC10AMMSSPLC01Sup24Vdc2Open | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN
864 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | Sup24Vdc2Fault | SIL0 | MODBUS:4:Read:Input Registers | 20182 | 2 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20182 | 2 | 1 | deiTUNEC10AMMSSPLC01Sup24Vdc2Fault | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT
865 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | Sup24Vdc2Volt | SIL0 | MODBUS:4:Read:Input Registers | 20182 | 3 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20182 | 3 | 1 | deiTUNEC10AMMSSPLC01Sup24Vdc2Volt | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 ABSENCE OF VOLTAGE
866 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | SwOpen | SIL0 | MODBUS:4:Read:Input Registers | 20182 | 4 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20182 | 4 | 1 | deiTUNEC10AMMSSPLC01SwOpen | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER OPEN
867 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | SwFault | SIL0 | MODBUS:4:Read:Input Registers | 20182 | 5 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20182 | 5 | 1 | deiTUNEC10AMMSSPLC01SwFault | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER FAULT
868 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | LcpOpen | SIL0 | MODBUS:4:Read:Input Registers | 20182 | 6 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20182 | 6 | 1 | deiTUNEC10AMMSSPLC01LcpOpen | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER OPEN
869 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | LcpFault | SIL0 | MODBUS:4:Read:Input Registers | 20182 | 7 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20182 | 7 | 1 | deiTUNEC10AMMSSPLC01LcpFault | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER FAULT
870 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | Plc1Open | SIL0 | MODBUS:4:Read:Input Registers | 20182 | 8 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20182 | 8 | 1 | deiTUNEC10AMMSSPLC01Plc1Open | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER OPEN
871 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | Plc1Fault | SIL0 | MODBUS:4:Read:Input Registers | 20182 | 9 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20182 | 9 | 1 | deiTUNEC10AMMSSPLC01Plc1Fault | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER FAULT
872 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | Plc2Open | SIL0 | MODBUS:4:Read:Input Registers | 20182 | 10 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20182 | 10 | 1 | deiTUNEC10AMMSSPLC01Plc2Open | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER OPEN
873 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | Plc2Fault | SIL0 | MODBUS:4:Read:Input Registers | 20182 | 11 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20182 | 11 | 1 | deiTUNEC10AMMSSPLC01Plc2Fault | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER FAULT
874 | EC10A_RTU | TUN:EC10A | MMS | SPLCMMS | SPLC01 | 18 | SuArTrig | SIL0 | MODBUS:4:Read:Input Registers | 20182 | 12 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20182 | 12 | 1 | deiTUNEC10AMMSSPLC01SuArTrig | 4 |  |  | 0 | $ComStatus , , | #SURGE ARRESTER TRIGGERED
875 | EC10A_RTU | TUN:EC10A | MMS | ADS | EL3-LBW01 | 19 | LoadClose | SIL0 | MODBUS:4:Read:Input Registers | 20191 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20191 | 0 | 1 | deiTUNEC10AMMSEL3-LBW01LoadClose | 4 |  |  | 0 | $ComStatus , , | #Load breaker switched closed
876 | EC10A_RTU | TUN:EC10A | MMS | ADS | EL3-LBW01 | 19 | LbsPos | SIL0 | MODBUS:4:Read:Input Registers | 20191 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20191 | 1 | 1 | deiTUNEC10AMMSEL3-LBW01LbsPos | 4 |  |  | 0 | $ComStatus , , | #LBS Auxiliary Switch racked position
877 | EC10A_RTU | TUN:EC10A | MMS | ADS | EL3-LBW02 | 20 | LoadClose | SIL0 | MODBUS:4:Read:Input Registers | 20201 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20201 | 0 | 1 | deiTUNEC10AMMSEL3-LBW02LoadClose | 4 |  |  | 0 | $ComStatus , , | #Load breaker switched closed
878 | EC10A_RTU | TUN:EC10A | MMS | ADS | EL3-LBW02 | 20 | LbsPos | SIL0 | MODBUS:4:Read:Input Registers | 20201 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20201 | 1 | 1 | deiTUNEC10AMMSEL3-LBW02LbsPos | 4 |  |  | 0 | $ComStatus , , | #LBS Auxiliary Switch racked position
879 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF01 | 21 | EmOff | SIL0 | MODBUS:4:Read:Input Registers | 20211 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20211 | 0 | 1 | deiTUNEC10AMMSEL3-TRF01EmOff | 4 |  |  | 0 | $ComStatus , , | #Emergency power off
880 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF01 | 21 | TranFault | SIL0 | MODBUS:4:Read:Input Registers | 20211 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20211 | 1 | 1 | deiTUNEC10AMMSEL3-TRF01TranFault | 4 |  |  | 0 | $ComStatus , , | #Transformer fault
881 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF01 | 21 | EmCut | SIL0 | MODBUS:4:Read:Input Registers | 20211 | 2 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20211 | 2 | 1 | deiTUNEC10AMMSEL3-TRF01EmCut | 4 |  |  | 0 | $ComStatus , , | #Emergency power cut
882 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF01 | 21 | PAlarm | SIL0 | MODBUS:4:Read:Input Registers | 20211 | 3 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20211 | 3 | 1 | deiTUNEC10AMMSEL3-TRF01PAlarm | 4 |  |  | 0 | $ComStatus , , | #Transformer high Temperature pre alarm
883 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF01 | 21 | Alarm | SIL0 | MODBUS:4:Read:Input Registers | 20211 | 4 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20211 | 4 | 1 | deiTUNEC10AMMSEL3-TRF01Alarm | 4 |  |  | 0 | $ComStatus , , | #Transformer high Temperature Alarm
884 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF02 | 22 | EmOff | SIL0 | MODBUS:4:Read:Input Registers | 20221 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20221 | 0 | 1 | deiTUNEC10AMMSEL3-TRF02EmOff | 4 |  |  | 0 | $ComStatus , , | #Emergency power off
885 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF02 | 22 | TranFault | SIL0 | MODBUS:4:Read:Input Registers | 20221 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20221 | 1 | 1 | deiTUNEC10AMMSEL3-TRF02TranFault | 4 |  |  | 0 | $ComStatus , , | #Transformer fault
886 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF02 | 22 | EmCut | SIL0 | MODBUS:4:Read:Input Registers | 20221 | 2 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20221 | 2 | 1 | deiTUNEC10AMMSEL3-TRF02EmCut | 4 |  |  | 0 | $ComStatus , , | #Emergency power cut
887 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF02 | 22 | PAlarm | SIL0 | MODBUS:4:Read:Input Registers | 20221 | 3 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20221 | 3 | 1 | deiTUNEC10AMMSEL3-TRF02PAlarm | 4 |  |  | 0 | $ComStatus , , | #Transformer high Temperature pre alarm
888 | EC10A_RTU | TUN:EC10A | MMS | TRF | EL3-TRF02 | 22 | Alarm | SIL0 | MODBUS:4:Read:Input Registers | 20221 | 4 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20221 | 4 | 1 | deiTUNEC10AMMSEL3-TRF02Alarm | 4 |  |  | 0 | $ComStatus , , | #Transformer high Temperature Alarm
889 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 23 | Mcsd1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20231 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20231 | 0 | 1 | deiTUNEC10AMMSEL3-MDB01Mcsd1Stat | 4 |  |  | 0 | $ComStatus , , | #Power normal MCSD 1 status
890 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 23 | Mcsd2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20231 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20231 | 1 | 1 | deiTUNEC10AMMSEL3-MDB01Mcsd2Stat | 4 |  |  | 0 | $ComStatus , , | #Power replacement MCSD 2 status
891 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 23 | Mcsd1pos | SIL0 | MODBUS:4:Read:Input Registers | 20231 | 2 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20231 | 2 | 1 | deiTUNEC10AMMSEL3-MDB01Mcsd1pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 1 racked position
892 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 23 | Mcsd2pos | SIL0 | MODBUS:4:Read:Input Registers | 20231 | 3 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20231 | 3 | 1 | deiTUNEC10AMMSEL3-MDB01Mcsd2pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 2 racked position
893 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 23 | Change | SIL0 | MODBUS:4:Read:Input Registers | 20231 | 4 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20231 | 4 | 1 | deiTUNEC10AMMSEL3-MDB01Change | 4 |  |  | 0 | $ComStatus , , | #Change over
894 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 23 | relay1 | SIL0 | MODBUS:4:Read:Input Registers | 20231 | 5 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20231 | 5 | 1 | deiTUNEC10AMMSEL3-MDB01relay1 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 1
895 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 23 | relay2 | SIL0 | MODBUS:4:Read:Input Registers | 20231 | 6 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20231 | 6 | 1 | deiTUNEC10AMMSEL3-MDB01relay2 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 2
896 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 23 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20231 | 7 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20231 | 7 | 1 | deiTUNEC10AMMSEL3-MDB01Closed | 4 |  |  | 0 | $ComStatus , , | #MCB closed status
897 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 23 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20231 | 8 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20231 | 8 | 1 | deiTUNEC10AMMSEL3-MDB01Trip | 4 |  |  | 0 | $ComStatus , , | #MCB tripped status
898 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 23 | PowerCut | SIL0 | MODBUS:4:Read:Input Registers | 20231 | 9 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20231 | 9 | 1 | deiTUNEC10AMMSEL3-MDB01PowerCut | 4 |  |  | 0 | $ComStatus , , | #Emergency power cut (push button)
899 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 23 | Mccb1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20231 | 10 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20231 | 10 | 1 | deiTUNEC10AMMSEL3-MDB01Mccb1Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 status
900 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 23 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20231 | 11 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20231 | 11 | 1 | deiTUNEC10AMMSEL3-MDB01Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 trip
901 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 23 | Mccb2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20231 | 12 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20231 | 12 | 1 | deiTUNEC10AMMSEL3-MDB01Mccb2Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 status
902 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 23 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20231 | 13 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20231 | 13 | 1 | deiTUNEC10AMMSEL3-MDB01Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 trip
903 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 23 | Mccb3Stat | SIL0 | MODBUS:4:Read:Input Registers | 20231 | 14 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20231 | 14 | 1 | deiTUNEC10AMMSEL3-MDB01Mccb3Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 status
904 | EC10A_RTU | TUN:EC10A | MMS | MDB | EL3-MDB01 | 23 | Mccb3Trip | SIL0 | MODBUS:4:Read:Input Registers | 20231 | 15 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20231 | 15 | 1 | deiTUNEC10AMMSEL3-MDB01Mccb3Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 trip
905 | EC10A_RTU | TUN:EC10A | MMS | EL | EL3-PLC01 | 24 | Relay | SIL0 | MODBUS:4:Read:Input Registers | 20241 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20241 | 0 | 1 | deiTUNEC10AMMSEL3-PLC01Relay | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay
906 | EC10A_RTU | TUN:EC10A | MMS | EL | EL3-PLC01 | 24 | Isolator | SIL0 | MODBUS:4:Read:Input Registers | 20241 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20241 | 1 | 1 | deiTUNEC10AMMSEL3-PLC01Isolator | 4 |  |  | 0 | $ComStatus , , | #LBS Main incomer isolator status
907 | EC10A_RTU | TUN:EC10A | MMS | EL | EL3-PLC01 | 24 | Supply | SIL0 | MODBUS:4:Read:Input Registers | 20241 | 2 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20241 | 2 | 1 | deiTUNEC10AMMSEL3-PLC01Supply | 4 |  |  | 0 | $ComStatus , , | #UPS supply status
908 | EC10A_RTU | TUN:EC10A | MMS | EL | EL3-PLC01 | 24 | Faulty | SIL0 | MODBUS:4:Read:Input Registers | 20241 | 3 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20241 | 3 | 1 | deiTUNEC10AMMSEL3-PLC01Faulty | 4 |  |  | 0 | $ComStatus , , | #UPS faulty
909 | EC10A_RTU | TUN:EC10A | MMS | EL | EL3-PLC01 | 24 | Power | SIL0 | MODBUS:4:Read:Input Registers | 20241 | 4 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20241 | 4 | 1 | deiTUNEC10AMMSEL3-PLC01Power | 4 |  |  | 0 | $ComStatus , , | #24VDC UPS power status
910 | EC10A_RTU | TUN:EC10A | MMS | MCB | EL3-LBW01 | 25 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20251 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20251 | 0 | 1 | deiTUNEC10AMMSEL3-LBW01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
911 | EC10A_RTU | TUN:EC10A | MMS | MCB | EL3-LBW01 | 25 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20251 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20251 | 1 | 1 | deiTUNEC10AMMSEL3-LBW01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
912 | EC10A_RTU | TUN:EC10A | MMS | MCB | EL3-LBW02 | 26 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20261 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20261 | 0 | 1 | deiTUNEC10AMMSEL3-LBW02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
913 | EC10A_RTU | TUN:EC10A | MMS | MCB | EL3-LBW02 | 26 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20261 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20261 | 1 | 1 | deiTUNEC10AMMSEL3-LBW02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
914 | EC10A_RTU | TUN:EC10A | MMS | MCCB | EL3-UPS | 27 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20271 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20271 | 0 | 1 | deiTUNEC10AMMSEL3-UPSTrip | 4 |  |  | 0 | $ComStatus , , | #MCCB trip status
915 | EC10A_RTU | TUN:EC10A | MMS | MCCB | EL3-UPS | 27 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20271 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20271 | 1 | 1 | deiTUNEC10AMMSEL3-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #MCCB closed status
916 | EC10A_RTU | TUN:EC10A | MMS | LBS | EL3-UPS | 28 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20281 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20281 | 0 | 1 | deiTUNEC10AMMSEL3-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #LBS closed status
917 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-VSD01 | 29 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20291 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20291 | 0 | 1 | deiTUNEC10AMMSUPS_EL3-VSD01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
918 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-VSD01 | 29 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20291 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20291 | 1 | 1 | deiTUNEC10AMMSUPS_EL3-VSD01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
919 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-VSD02 | 30 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20301 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20301 | 0 | 1 | deiTUNEC10AMMSUPS_EL3-VSD02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
920 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-VSD02 | 30 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20301 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20301 | 1 | 1 | deiTUNEC10AMMSUPS_EL3-VSD02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
921 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-LBW01 | 31 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 0 | 1 | deiTUNEC10AMMSUPS_EL3-LBW01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
922 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-LBW01 | 31 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 1 | 1 | deiTUNEC10AMMSUPS_EL3-LBW01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
923 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-LBW02 | 32 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 0 | 1 | deiTUNEC10AMMSUPS_EL3-LBW02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
924 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-LBW02 | 32 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 1 | 1 | deiTUNEC10AMMSUPS_EL3-LBW02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
925 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-MDB01 | 33 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 0 | 1 | deiTUNEC10AMMSUPS_EL3-MDB01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
926 | EC10A_RTU | TUN:EC10A | MMS | MCB | UPS_EL3-MDB01 | 33 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 1 | 1 | deiTUNEC10AMMSUPS_EL3-MDB01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
927 | EC10A_RTU | TUN:EC10A | MMS | MCB | 3P-VT1-IDP01 | 34 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 0 | 1 | deiTUNEC10AMMS3P-VT1-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
928 | EC10A_RTU | TUN:EC10A | MMS | MCB | 3P-VT1-IDP01 | 34 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 1 | 1 | deiTUNEC10AMMS3P-VT1-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
929 | EC10A_RTU | TUN:EC10A | MMS | MCB | 2P-VT1-IDP01 | 35 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20351 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20351 | 0 | 1 | deiTUNEC10AMMS2P-VT1-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
930 | EC10A_RTU | TUN:EC10A | MMS | MCB | 2P-VT1-IDP01 | 35 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20351 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20351 | 1 | 1 | deiTUNEC10AMMS2P-VT1-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
931 | EC10A_RTU | TUN:EC10A | MMS | MCB | 3P-VT2-IDP01 | 36 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20361 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20361 | 0 | 1 | deiTUNEC10AMMS3P-VT2-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
932 | EC10A_RTU | TUN:EC10A | MMS | MCB | 3P-VT2-IDP01 | 36 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20361 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20361 | 1 | 1 | deiTUNEC10AMMS3P-VT2-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
933 | EC10A_RTU | TUN:EC10A | MMS | MCB | 2P-VT2-IDP01 | 37 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20371 | 0 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20371 | 0 | 1 | deiTUNEC10AMMS2P-VT2-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
934 | EC10A_RTU | TUN:EC10A | MMS | MCB | 2P-VT2-IDP01 | 37 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20371 | 1 | 1 | Check SWC Name |  | EC10A-SIL0 |  | EC10A_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20371 | 1 | 1 | deiTUNEC10AMMS2P-VT2-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
935 | QAP01_RTU | TUN:QAP01 | SCR | LCP | LCP01 | 1 | ComFaultPlc | SIL0 | MODBUS:4:Read:Input Registers | 20011 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20011 | 0 | 1 | deiTUNQAP01SCRLCP01ComFaultPlc | 4 |  |  | 0 | $ComStatus , , | #COMMUNICATION FAULT WITH PLC
936 | QAP01_RTU | TUN:QAP01 | SCR | LCP | LCP01 | 1 | LcpMode | SIL0 | MODBUS:4:Read:Input Registers | 20011 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20011 | 1 | 1 | deiTUNQAP01SCRLCP01LcpMode | 4 |  |  | 0 | $ComStatus , , | #LOCAL / REMOTE STATUS
937 | QAP01_RTU | TUN:QAP01 | SCR | FMOP | FMOP01 | 2 | EmergNod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20021 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20021 | 0 | 1 | deiTUNQAP01SCRFMOP01EmergNod | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
938 | QAP01_RTU | TUN:QAP01 | SCR | FMOP | FMOP01 | 2 | RightStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20021 | 1 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20021 | 1 | 1 | deiTUNQAP01SCRFMOP01RightStat | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
939 | QAP01_RTU | TUN:QAP01 | SCR | FMOP | FMOP01 | 2 | LeftStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20021 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20021 | 2 | 1 | deiTUNQAP01SCRFMOP01LeftStat | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
940 | QAP01_RTU | TUN:QAP01 | TEL | SPLC | PLC01 | 3 | PlcState | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 0 | 1 | deiTUNQAP01TELPLC01PlcState | 4 |  |  | 0 | $ComStatus , , | #PLC A/B OFFLINE
941 | QAP01_RTU | TUN:QAP01 | TEL | SPLC | PLC01 | 3 | OpStatus | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 1 | 1 | deiTUNQAP01TELPLC01OpStatus | 4 |  |  | 0 | $ComStatus , , | #PLC RUNNING.
942 | QAP01_RTU | TUN:QAP01 | TEL | SPLC | PLC01 | 3 | PwStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 2 | 1 | deiTUNQAP01TELPLC01PwStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: POWER SUPPLY FAULT
943 | QAP01_RTU | TUN:QAP01 | TEL | SPLC | PLC01 | 3 | CpuStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 3 | 1 | deiTUNQAP01TELPLC01CpuStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CPU MODULE FAULT
944 | QAP01_RTU | TUN:QAP01 | TEL | SPLC | PLC01 | 3 | CrpStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 4 | 1 | deiTUNQAP01TELPLC01CrpStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CRP MODULE FAULT
945 | QAP01_RTU | TUN:QAP01 | TEL | SPLC | PLC01 | 3 | CraStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 5 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 5 | 1 | deiTUNQAP01TELPLC01CraStat | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
946 | QAP01_RTU | TUN:QAP01 | TEL | SPLC | PLC01 | 3 | NrpStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 6 | 1 | deiTUNQAP01TELPLC01NrpStat | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
947 | QAP01_RTU | TUN:QAP01 | TEL | SPLC | PLC01 | 3 | ComStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 7 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 7 | 1 | deiTUNQAP01TELPLC01ComStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
948 | QAP01_RTU | TUN:QAP01 | TEL | SPLC | PLC01 | 3 | IoStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 8 | 1 | deiTUNQAP01TELPLC01IoStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
949 | QAP01_RTU | TUN:QAP01 | TEL | SWI | SWI01 | 4 | SwStat | SIL0 | MODBUS:4:Read:Input Registers | 20041 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20041 | 0 | 1 | deiTUNQAP01TELSWI01SwStat | 4 |  |  | 0 | $ComStatus , , | #SWITCH FAULT
950 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 5 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20051 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20051 | 0 | 1 | deiTUNQAP01SS01PFACON-03ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
951 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 5 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20051 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20051 | 2 | 1 | deiTUNQAP01SS01PFACON-03OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
952 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 5 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20051 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20051 | 4 | 1 | deiTUNQAP01SS01PFACON-03AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
953 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 5 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10101 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10101 | 0 | 1 | deoTUNQAP01SS01PFACON-03CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
954 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 5 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10102 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10102 | 0 | 1 | deoTUNQAP01SS01PFACON-03CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
955 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 5 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 6 | 2 | deiTUNQAP01SS01PFACON-03AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
956 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 5 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10103 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10103 | 0 | 1 | deoTUNQAP01SS01PFACON-03CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
957 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 5 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 8 | 2 | deiTUNQAP01SS01PFACON-03AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
958 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 5 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10104 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10104 | 0 | 1 | deoTUNQAP01SS01PFACON-03CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
959 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 5 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 10 | 2 | deiTUNQAP01SS01PFACON-03AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
960 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 5 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10105 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10105 | 0 | 1 | deoTUNQAP01SS01PFACON-03CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
961 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 5 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 12 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 12 | 2 | deiTUNQAP01SS01PFACON-03AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
962 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 5 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10106 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10106 | 0 | 1 | deoTUNQAP01SS01PFACON-03CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
963 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 5 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 14 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 14 | 2 | deiTUNQAP01SS01PFACON-03AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
964 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 5 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10107 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10107 | 0 | 1 | deoTUNQAP01SS01PFACON-03CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
965 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 5 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20052 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20052 | 0 | 2 | deiTUNQAP01SS01PFACON-03AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
966 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 5 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20052 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20052 | 2 | 1 | deiTUNQAP01SS01PFACON-03StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
967 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | CON-03 | 5 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20052 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20052 | 4 | 1 | deiTUNQAP01SS01PFACON-03StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
968 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 6 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20061 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20061 | 0 | 1 | deiTUNQAP01SS01PFAGRD-01ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
969 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 6 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20061 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20061 | 2 | 1 | deiTUNQAP01SS01PFAGRD-01OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
970 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 6 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20061 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20061 | 4 | 1 | deiTUNQAP01SS01PFAGRD-01AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
971 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 6 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10121 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10121 | 0 | 1 | deoTUNQAP01SS01PFAGRD-01CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
972 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 6 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10122 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10122 | 0 | 1 | deoTUNQAP01SS01PFAGRD-01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
973 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 6 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 6 | 2 | deiTUNQAP01SS01PFAGRD-01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
974 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 6 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10123 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10123 | 0 | 1 | deoTUNQAP01SS01PFAGRD-01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
975 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 6 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 8 | 2 | deiTUNQAP01SS01PFAGRD-01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
976 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 6 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10124 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10124 | 0 | 1 | deoTUNQAP01SS01PFAGRD-01CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
977 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 6 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 10 | 2 | deiTUNQAP01SS01PFAGRD-01AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
978 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 6 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10125 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10125 | 0 | 1 | deoTUNQAP01SS01PFAGRD-01CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
979 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 6 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 12 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 12 | 2 | deiTUNQAP01SS01PFAGRD-01AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
980 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 6 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10126 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10126 | 0 | 1 | deoTUNQAP01SS01PFAGRD-01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
981 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 6 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 14 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 14 | 2 | deiTUNQAP01SS01PFAGRD-01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
982 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 6 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10127 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10127 | 0 | 1 | deoTUNQAP01SS01PFAGRD-01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
983 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 6 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20062 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20062 | 0 | 2 | deiTUNQAP01SS01PFAGRD-01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
984 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 6 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20062 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20062 | 2 | 1 | deiTUNQAP01SS01PFAGRD-01StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
985 | QAP01_RTU | TUN:QAP01 | SS01:PFA | PFA | GRD-01 | 6 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20062 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20062 | 4 | 1 | deiTUNQAP01SS01PFAGRD-01StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
986 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 7 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20071 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20071 | 0 | 1 | deiTUNQAP01NS01PFACON-02ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
987 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 7 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20071 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20071 | 2 | 1 | deiTUNQAP01NS01PFACON-02OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
988 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 7 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20071 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20071 | 4 | 1 | deiTUNQAP01NS01PFACON-02AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
989 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 7 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10141 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10141 | 0 | 1 | deoTUNQAP01NS01PFACON-02CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
990 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 7 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10142 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10142 | 0 | 1 | deoTUNQAP01NS01PFACON-02CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
991 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 7 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 6 | 2 | deiTUNQAP01NS01PFACON-02AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
992 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 7 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10143 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10143 | 0 | 1 | deoTUNQAP01NS01PFACON-02CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
993 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 7 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 8 | 2 | deiTUNQAP01NS01PFACON-02AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
994 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 7 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10144 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10144 | 0 | 1 | deoTUNQAP01NS01PFACON-02CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
995 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 7 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 10 | 2 | deiTUNQAP01NS01PFACON-02AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
996 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 7 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10145 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10145 | 0 | 1 | deoTUNQAP01NS01PFACON-02CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
997 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 7 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 12 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 12 | 2 | deiTUNQAP01NS01PFACON-02AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
998 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 7 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10146 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10146 | 0 | 1 | deoTUNQAP01NS01PFACON-02CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
999 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 7 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 14 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 14 | 2 | deiTUNQAP01NS01PFACON-02AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1000 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 7 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10147 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10147 | 0 | 1 | deoTUNQAP01NS01PFACON-02CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1001 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 7 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20072 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20072 | 0 | 2 | deiTUNQAP01NS01PFACON-02AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1002 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 7 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20072 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20072 | 2 | 1 | deiTUNQAP01NS01PFACON-02StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
1003 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-02 | 7 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20072 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20072 | 4 | 1 | deiTUNQAP01NS01PFACON-02StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
1004 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 8 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20081 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20081 | 0 | 1 | deiTUNQAP01NS01PFAGRD-03ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1005 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 8 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20081 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20081 | 2 | 1 | deiTUNQAP01NS01PFAGRD-03OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1006 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 8 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20081 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20081 | 4 | 1 | deiTUNQAP01NS01PFAGRD-03AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
1007 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 8 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10161 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10161 | 0 | 1 | deoTUNQAP01NS01PFAGRD-03CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1008 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 8 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10162 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10162 | 0 | 1 | deoTUNQAP01NS01PFAGRD-03CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1009 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 8 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 6 | 2 | deiTUNQAP01NS01PFAGRD-03AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1010 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 8 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10163 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10163 | 0 | 1 | deoTUNQAP01NS01PFAGRD-03CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1011 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 8 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 8 | 2 | deiTUNQAP01NS01PFAGRD-03AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1012 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 8 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10164 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10164 | 0 | 1 | deoTUNQAP01NS01PFAGRD-03CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
1013 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 8 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 10 | 2 | deiTUNQAP01NS01PFAGRD-03AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
1014 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 8 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10165 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10165 | 0 | 1 | deoTUNQAP01NS01PFAGRD-03CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
1015 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 8 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 12 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 12 | 2 | deiTUNQAP01NS01PFAGRD-03AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
1016 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 8 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10166 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10166 | 0 | 1 | deoTUNQAP01NS01PFAGRD-03CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1017 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 8 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 14 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 14 | 2 | deiTUNQAP01NS01PFAGRD-03AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1018 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 8 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10167 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10167 | 0 | 1 | deoTUNQAP01NS01PFAGRD-03CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1019 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 8 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20082 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20082 | 0 | 2 | deiTUNQAP01NS01PFAGRD-03AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1020 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 8 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20082 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20082 | 2 | 1 | deiTUNQAP01NS01PFAGRD-03StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
1021 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | GRD-03 | 8 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20082 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20082 | 4 | 1 | deiTUNQAP01NS01PFAGRD-03StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
1022 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 9 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20091 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20091 | 0 | 1 | deiTUNQAP01NS01PFACON-04ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1023 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 9 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20091 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20091 | 2 | 1 | deiTUNQAP01NS01PFACON-04OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1024 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 9 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20091 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20091 | 4 | 1 | deiTUNQAP01NS01PFACON-04AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
1025 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 9 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10181 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10181 | 0 | 1 | deoTUNQAP01NS01PFACON-04CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1026 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 9 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10182 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10182 | 0 | 1 | deoTUNQAP01NS01PFACON-04CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1027 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 9 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 6 | 2 | deiTUNQAP01NS01PFACON-04AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1028 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 9 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10183 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10183 | 0 | 1 | deoTUNQAP01NS01PFACON-04CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1029 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 9 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 8 | 2 | deiTUNQAP01NS01PFACON-04AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1030 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 9 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10184 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10184 | 0 | 1 | deoTUNQAP01NS01PFACON-04CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
1031 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 9 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 10 | 2 | deiTUNQAP01NS01PFACON-04AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
1032 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 9 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10185 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10185 | 0 | 1 | deoTUNQAP01NS01PFACON-04CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
1033 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 9 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 12 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 12 | 2 | deiTUNQAP01NS01PFACON-04AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
1034 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 9 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10186 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10186 | 0 | 1 | deoTUNQAP01NS01PFACON-04CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1035 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 9 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 14 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 14 | 2 | deiTUNQAP01NS01PFACON-04AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1036 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 9 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10187 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10187 | 0 | 1 | deoTUNQAP01NS01PFACON-04CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1037 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 9 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20092 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20092 | 0 | 2 | deiTUNQAP01NS01PFACON-04AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1038 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 9 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20092 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20092 | 2 | 1 | deiTUNQAP01NS01PFACON-04StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
1039 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-04 | 9 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20092 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20092 | 4 | 1 | deiTUNQAP01NS01PFACON-04StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
1040 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 10 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20101 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20101 | 0 | 1 | deiTUNQAP01NS01PFACON-05ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1041 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 10 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20101 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20101 | 2 | 1 | deiTUNQAP01NS01PFACON-05OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1042 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 10 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20101 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20101 | 4 | 1 | deiTUNQAP01NS01PFACON-05AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
1043 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 10 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10201 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10201 | 0 | 1 | deoTUNQAP01NS01PFACON-05CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1044 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 10 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10202 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10202 | 0 | 1 | deoTUNQAP01NS01PFACON-05CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1045 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 10 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 6 | 2 | deiTUNQAP01NS01PFACON-05AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1046 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 10 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10203 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10203 | 0 | 1 | deoTUNQAP01NS01PFACON-05CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1047 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 10 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 8 | 2 | deiTUNQAP01NS01PFACON-05AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1048 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 10 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10204 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10204 | 0 | 1 | deoTUNQAP01NS01PFACON-05CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
1049 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 10 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 10 | 2 | deiTUNQAP01NS01PFACON-05AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
1050 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 10 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10205 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10205 | 0 | 1 | deoTUNQAP01NS01PFACON-05CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
1051 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 10 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 12 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 12 | 2 | deiTUNQAP01NS01PFACON-05AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
1052 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 10 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10206 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10206 | 0 | 1 | deoTUNQAP01NS01PFACON-05CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1053 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 10 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 14 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 14 | 2 | deiTUNQAP01NS01PFACON-05AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1054 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 10 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10207 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10207 | 0 | 1 | deoTUNQAP01NS01PFACON-05CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1055 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 10 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20102 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20102 | 0 | 2 | deiTUNQAP01NS01PFACON-05AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1056 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 10 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20102 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20102 | 2 | 1 | deiTUNQAP01NS01PFACON-05StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
1057 | QAP01_RTU | TUN:QAP01 | NS01:PFA | PFA | CON-05 | 10 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20102 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20102 | 4 | 1 | deiTUNQAP01NS01PFACON-05StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
1058 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC01 | 11 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20111 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20111 | 0 | 1 | deiTUNQAP01SMCSMC01State | 4 |  |  | 0 | $ComStatus , , | #STATE
1059 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC02 | 12 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20121 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20121 | 0 | 1 | deiTUNQAP01SMCSMC02State | 4 |  |  | 0 | $ComStatus , , | #STATE
1060 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC03 | 13 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20131 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20131 | 0 | 1 | deiTUNQAP01SMCSMC03State | 4 |  |  | 0 | $ComStatus , , | #STATE
1061 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC04 | 14 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20141 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20141 | 0 | 1 | deiTUNQAP01SMCSMC04State | 4 |  |  | 0 | $ComStatus , , | #STATE
1062 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC05 | 15 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20151 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20151 | 0 | 1 | deiTUNQAP01SMCSMC05State | 4 |  |  | 0 | $ComStatus , , | #STATE
1063 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC06 | 16 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20161 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20161 | 0 | 1 | deiTUNQAP01SMCSMC06State | 4 |  |  | 0 | $ComStatus , , | #STATE
1064 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC07 | 17 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20171 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20171 | 0 | 1 | deiTUNQAP01SMCSMC07State | 4 |  |  | 0 | $ComStatus , , | #STATE
1065 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC08 | 18 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20181 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20181 | 0 | 1 | deiTUNQAP01SMCSMC08State | 4 |  |  | 0 | $ComStatus , , | #STATE
1066 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC09 | 19 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20191 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20191 | 0 | 1 | deiTUNQAP01SMCSMC09State | 4 |  |  | 0 | $ComStatus , , | #STATE
1067 | QAP01_RTU | TUN:QAP01 | SMC | SMC | SMC10 | 20 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20201 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20201 | 0 | 1 | deiTUNQAP01SMCSMC10State | 4 |  |  | 0 | $ComStatus , , | #STATE
1068 | QAP01_RTU | TUN:QAP01 | SED | SED | SED01 | 21 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20211 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20211 | 0 | 1 | deiTUNQAP01SEDSED01State | 4 |  |  | 0 | $ComStatus , , | #STATE
1069 | QAP01_RTU | TUN:QAP01 | SED | SED | SED01 | 21 | Open | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20211 | 1 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20211 | 1 | 1 | deiTUNQAP01SEDSED01Open | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
1070 | QAP01_RTU | TUN:QAP01 | SED | SED | SED02 | 22 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20221 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20221 | 0 | 1 | deiTUNQAP01SEDSED02State | 4 |  |  | 0 | $ComStatus , , | #STATE
1071 | QAP01_RTU | TUN:QAP01 | SED | SED | SED02 | 22 | Open | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20221 | 1 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20221 | 1 | 1 | deiTUNQAP01SEDSED02Open | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
1072 | QAP01_RTU | TUN:QAP01 | SED | SED | SED03 | 23 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20231 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20231 | 0 | 1 | deiTUNQAP01SEDSED03State | 4 |  |  | 0 | $ComStatus , , | #STATE
1073 | QAP01_RTU | TUN:QAP01 | SED | SED | SED03 | 23 | Open | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20231 | 1 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20231 | 1 | 1 | deiTUNQAP01SEDSED03Open | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
1074 | QAP01_RTU | TUN:QAP01 | SED | SED | SED04 | 24 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20241 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20241 | 0 | 1 | deiTUNQAP01SEDSED04State | 4 |  |  | 0 | $ComStatus , , | #STATE
1075 | QAP01_RTU | TUN:QAP01 | SED | SED | SED04 | 24 | Open | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20241 | 1 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20241 | 1 | 1 | deiTUNQAP01SEDSED04Open | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
1076 | QAP01_RTU | TUN:QAP01 | OTS | OTS | OTS001 | 25 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20251 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20251 | 0 | 1 | deiTUNQAP01OTSOTS001AvailStat | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1077 | QAP01_RTU | TUN:QAP01 | OTS | OTS | OTS001 | 25 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20251 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20251 | 2 | 1 | deiTUNQAP01OTSOTS001AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1078 | QAP01_RTU | TUN:QAP01 | OTS | OTS | OTS001 | 25 | TemMeasure | SIL0 | MODBUS:4:Read:Input Registers | 20252 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20252 | 0 | 32 | aeiTUNQAP01OTSOTS001TemMeasure | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1079 | QAP01_RTU | TUN:QAP01 | OTS | OTS | OTS002 | 26 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20261 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20261 | 0 | 1 | deiTUNQAP01OTSOTS002AvailStat | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1080 | QAP01_RTU | TUN:QAP01 | OTS | OTS | OTS002 | 26 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20261 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20261 | 2 | 1 | deiTUNQAP01OTSOTS002AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1081 | QAP01_RTU | TUN:QAP01 | OTS | OTS | OTS002 | 26 | TemMeasure | SIL0 | MODBUS:4:Read:Input Registers | 20262 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20262 | 0 | 32 | aeiTUNQAP01OTSOTS002TemMeasure | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1082 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20271 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20271 | 0 | 2 | deiTUNQAP01SS01TVFVT1-TVF01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1083 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20271 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20271 | 2 | 1 | deiTUNQAP01SS01TVFVT1-TVF01OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1084 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20271 | 4 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20271 | 4 | 2 | deiTUNQAP01SS01TVFVT1-TVF01RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
1085 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10541 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10541 | 0 | 1 | deoTUNQAP01SS01TVFVT1-TVF01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1086 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10542 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10542 | 0 | 1 | deoTUNQAP01SS01TVFVT1-TVF01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1087 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20271 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20271 | 6 | 2 | deiTUNQAP01SS01TVFVT1-TVF01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1088 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10543 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10543 | 0 | 1 | deoTUNQAP01SS01TVFVT1-TVF01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1089 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20271 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20271 | 8 | 2 | deiTUNQAP01SS01TVFVT1-TVF01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1090 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20271 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20271 | 10 | 1 | deiTUNQAP01SS01TVFVT1-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
1091 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20271 | 12 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20271 | 12 | 1 | deiTUNQAP01SS01TVFVT1-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
1092 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20271 | 14 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20271 | 14 | 1 | deiTUNQAP01SS01TVFVT1-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
1093 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20272 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20272 | 0 | 32 | aeiTUNQAP01SS01TVFVT1-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
1094 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10544 | 0 | 2 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10544 | 0 | 2 | deoTUNQAP01SS01TVFVT1-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
1095 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10545 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10545 | 0 | 1 | deoTUNQAP01SS01TVFVT1-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1096 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 0 | 2 | deiTUNQAP01SS01TVFVT1-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1097 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10546 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10546 | 0 | 1 | deoTUNQAP01SS01TVFVT1-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1098 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 2 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 2 | 2 | deiTUNQAP01SS01TVFVT1-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1099 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10547 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10547 | 0 | 1 | deoTUNQAP01SS01TVFVT1-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
1100 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 4 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 4 | 2 | deiTUNQAP01SS01TVFVT1-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
1101 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10548 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10548 | 0 | 1 | deoTUNQAP01SS01TVFVT1-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
1102 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 6 | 2 | deiTUNQAP01SS01TVFVT1-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
1103 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10549 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10549 | 0 | 1 | deoTUNQAP01SS01TVFVT1-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
1104 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 8 | 2 | deiTUNQAP01SS01TVFVT1-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
1105 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10550 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10550 | 0 | 1 | deoTUNQAP01SS01TVFVT1-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
1106 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 10 | 2 | deiTUNQAP01SS01TVFVT1-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
1107 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20274 | 12 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20274 | 12 | 1 | deiTUNQAP01SS01TVFVT1-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
1108 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20274 | 14 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20274 | 14 | 1 | deiTUNQAP01SS01TVFVT1-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
1109 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 0 | 1 | deiTUNQAP01SS01TVFVT1-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
1110 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 1 | 1 | deiTUNQAP01SS01TVFVT1-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
1111 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 2 | 1 | deiTUNQAP01SS01TVFVT1-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
1112 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 3 | 1 | deiTUNQAP01SS01TVFVT1-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
1113 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 4 | 1 | deiTUNQAP01SS01TVFVT1-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
1114 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 5 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 5 | 1 | deiTUNQAP01SS01TVFVT1-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
1115 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 6 | 1 | deiTUNQAP01SS01TVFVT1-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
1116 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 7 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 7 | 1 | deiTUNQAP01SS01TVFVT1-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
1117 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 8 | 1 | deiTUNQAP01SS01TVFVT1-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
1118 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 9 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 9 | 1 | deiTUNQAP01SS01TVFVT1-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
1119 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 10 | 1 | deiTUNQAP01SS01TVFVT1-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
1120 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 11 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 11 | 1 | deiTUNQAP01SS01TVFVT1-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
1121 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT1-TVF01 | 27 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20276 | 0 | 16 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20276 | 0 | 16 | aeiTUNQAP01SS01TVFVT1-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
1122 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20281 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20281 | 0 | 2 | deiTUNQAP01SS01TVFVT2-TVF01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1123 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20281 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20281 | 2 | 1 | deiTUNQAP01SS01TVFVT2-TVF01OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1124 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20281 | 4 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20281 | 4 | 2 | deiTUNQAP01SS01TVFVT2-TVF01RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
1125 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10561 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10561 | 0 | 1 | deoTUNQAP01SS01TVFVT2-TVF01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1126 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10562 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10562 | 0 | 1 | deoTUNQAP01SS01TVFVT2-TVF01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1127 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20281 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20281 | 6 | 2 | deiTUNQAP01SS01TVFVT2-TVF01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1128 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10563 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10563 | 0 | 1 | deoTUNQAP01SS01TVFVT2-TVF01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1129 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20281 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20281 | 8 | 2 | deiTUNQAP01SS01TVFVT2-TVF01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1130 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20281 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20281 | 10 | 1 | deiTUNQAP01SS01TVFVT2-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
1131 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20281 | 12 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20281 | 12 | 1 | deiTUNQAP01SS01TVFVT2-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
1132 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20281 | 14 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20281 | 14 | 1 | deiTUNQAP01SS01TVFVT2-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
1133 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20282 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20282 | 0 | 32 | aeiTUNQAP01SS01TVFVT2-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
1134 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10564 | 0 | 2 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10564 | 0 | 2 | deoTUNQAP01SS01TVFVT2-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
1135 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10565 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10565 | 0 | 1 | deoTUNQAP01SS01TVFVT2-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1136 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 0 | 2 | deiTUNQAP01SS01TVFVT2-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1137 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10566 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10566 | 0 | 1 | deoTUNQAP01SS01TVFVT2-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1138 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 2 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 2 | 2 | deiTUNQAP01SS01TVFVT2-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1139 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10567 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10567 | 0 | 1 | deoTUNQAP01SS01TVFVT2-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
1140 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 4 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 4 | 2 | deiTUNQAP01SS01TVFVT2-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
1141 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10568 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10568 | 0 | 1 | deoTUNQAP01SS01TVFVT2-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
1142 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 6 | 2 | deiTUNQAP01SS01TVFVT2-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
1143 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10569 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10569 | 0 | 1 | deoTUNQAP01SS01TVFVT2-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
1144 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 8 | 2 | deiTUNQAP01SS01TVFVT2-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
1145 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10570 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10570 | 0 | 1 | deoTUNQAP01SS01TVFVT2-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
1146 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 10 | 2 | deiTUNQAP01SS01TVFVT2-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
1147 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20284 | 12 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20284 | 12 | 1 | deiTUNQAP01SS01TVFVT2-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
1148 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20284 | 14 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20284 | 14 | 1 | deiTUNQAP01SS01TVFVT2-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
1149 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 0 | 1 | deiTUNQAP01SS01TVFVT2-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
1150 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 1 | 1 | deiTUNQAP01SS01TVFVT2-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
1151 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 2 | 1 | deiTUNQAP01SS01TVFVT2-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
1152 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 3 | 1 | deiTUNQAP01SS01TVFVT2-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
1153 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 4 | 1 | deiTUNQAP01SS01TVFVT2-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
1154 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 5 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 5 | 1 | deiTUNQAP01SS01TVFVT2-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
1155 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 6 | 1 | deiTUNQAP01SS01TVFVT2-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
1156 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 7 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 7 | 1 | deiTUNQAP01SS01TVFVT2-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
1157 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 8 | 1 | deiTUNQAP01SS01TVFVT2-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
1158 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 9 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 9 | 1 | deiTUNQAP01SS01TVFVT2-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
1159 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 10 | 1 | deiTUNQAP01SS01TVFVT2-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
1160 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 11 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 11 | 1 | deiTUNQAP01SS01TVFVT2-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
1161 | QAP01_RTU | TUN:QAP01 | SS01:TVF | TVF | VT2-TVF01 | 28 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20286 | 0 | 16 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20286 | 0 | 16 | aeiTUNQAP01SS01TVFVT2-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
1162 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20291 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20291 | 0 | 2 | deiTUNQAP01NS01TVFVT3-TVF01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1163 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20291 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20291 | 2 | 1 | deiTUNQAP01NS01TVFVT3-TVF01OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1164 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20291 | 4 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20291 | 4 | 2 | deiTUNQAP01NS01TVFVT3-TVF01RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
1165 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10581 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10581 | 0 | 1 | deoTUNQAP01NS01TVFVT3-TVF01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1166 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10582 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10582 | 0 | 1 | deoTUNQAP01NS01TVFVT3-TVF01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1167 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20291 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20291 | 6 | 2 | deiTUNQAP01NS01TVFVT3-TVF01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1168 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10583 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10583 | 0 | 1 | deoTUNQAP01NS01TVFVT3-TVF01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1169 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20291 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20291 | 8 | 2 | deiTUNQAP01NS01TVFVT3-TVF01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1170 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20291 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20291 | 10 | 1 | deiTUNQAP01NS01TVFVT3-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
1171 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20291 | 12 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20291 | 12 | 1 | deiTUNQAP01NS01TVFVT3-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
1172 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20291 | 14 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20291 | 14 | 1 | deiTUNQAP01NS01TVFVT3-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
1173 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20292 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20292 | 0 | 32 | aeiTUNQAP01NS01TVFVT3-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
1174 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10584 | 0 | 2 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10584 | 0 | 2 | deoTUNQAP01NS01TVFVT3-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
1175 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10585 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10585 | 0 | 1 | deoTUNQAP01NS01TVFVT3-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1176 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 0 | 2 | deiTUNQAP01NS01TVFVT3-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1177 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10586 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10586 | 0 | 1 | deoTUNQAP01NS01TVFVT3-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1178 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 2 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 2 | 2 | deiTUNQAP01NS01TVFVT3-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1179 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10587 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10587 | 0 | 1 | deoTUNQAP01NS01TVFVT3-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
1180 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 4 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 4 | 2 | deiTUNQAP01NS01TVFVT3-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
1181 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10588 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10588 | 0 | 1 | deoTUNQAP01NS01TVFVT3-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
1182 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 6 | 2 | deiTUNQAP01NS01TVFVT3-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
1183 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10589 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10589 | 0 | 1 | deoTUNQAP01NS01TVFVT3-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
1184 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 8 | 2 | deiTUNQAP01NS01TVFVT3-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
1185 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10590 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10590 | 0 | 1 | deoTUNQAP01NS01TVFVT3-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
1186 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 10 | 2 | deiTUNQAP01NS01TVFVT3-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
1187 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20294 | 12 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20294 | 12 | 1 | deiTUNQAP01NS01TVFVT3-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
1188 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20294 | 14 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20294 | 14 | 1 | deiTUNQAP01NS01TVFVT3-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
1189 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 0 | 1 | deiTUNQAP01NS01TVFVT3-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
1190 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 1 | 1 | deiTUNQAP01NS01TVFVT3-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
1191 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 2 | 1 | deiTUNQAP01NS01TVFVT3-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
1192 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 3 | 1 | deiTUNQAP01NS01TVFVT3-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
1193 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 4 | 1 | deiTUNQAP01NS01TVFVT3-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
1194 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 5 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 5 | 1 | deiTUNQAP01NS01TVFVT3-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
1195 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 6 | 1 | deiTUNQAP01NS01TVFVT3-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
1196 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 7 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 7 | 1 | deiTUNQAP01NS01TVFVT3-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
1197 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 8 | 1 | deiTUNQAP01NS01TVFVT3-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
1198 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 9 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 9 | 1 | deiTUNQAP01NS01TVFVT3-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
1199 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 10 | 1 | deiTUNQAP01NS01TVFVT3-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
1200 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 11 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 11 | 1 | deiTUNQAP01NS01TVFVT3-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
1201 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT3-TVF01 | 29 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20296 | 0 | 16 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20296 | 0 | 16 | aeiTUNQAP01NS01TVFVT3-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
1202 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20301 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20301 | 0 | 2 | deiTUNQAP01NS01TVFVT4-TVF01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1203 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20301 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20301 | 2 | 1 | deiTUNQAP01NS01TVFVT4-TVF01OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1204 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20301 | 4 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20301 | 4 | 2 | deiTUNQAP01NS01TVFVT4-TVF01RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
1205 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10601 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10601 | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1206 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10602 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10602 | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1207 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20301 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20301 | 6 | 2 | deiTUNQAP01NS01TVFVT4-TVF01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1208 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10603 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10603 | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1209 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20301 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20301 | 8 | 2 | deiTUNQAP01NS01TVFVT4-TVF01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1210 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20301 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20301 | 10 | 1 | deiTUNQAP01NS01TVFVT4-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
1211 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20301 | 12 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20301 | 12 | 1 | deiTUNQAP01NS01TVFVT4-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
1212 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20301 | 14 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20301 | 14 | 1 | deiTUNQAP01NS01TVFVT4-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
1213 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20302 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20302 | 0 | 32 | aeiTUNQAP01NS01TVFVT4-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
1214 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10604 | 0 | 2 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10604 | 0 | 2 | deoTUNQAP01NS01TVFVT4-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
1215 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10605 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10605 | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1216 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 0 | 2 | deiTUNQAP01NS01TVFVT4-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1217 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10606 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10606 | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1218 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 2 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 2 | 2 | deiTUNQAP01NS01TVFVT4-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1219 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10607 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10607 | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
1220 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 4 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 4 | 2 | deiTUNQAP01NS01TVFVT4-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
1221 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10608 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10608 | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
1222 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 6 | 2 | deiTUNQAP01NS01TVFVT4-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
1223 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10609 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10609 | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
1224 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 8 | 2 | deiTUNQAP01NS01TVFVT4-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
1225 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10610 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10610 | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
1226 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 10 | 2 | deiTUNQAP01NS01TVFVT4-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
1227 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20304 | 12 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20304 | 12 | 1 | deiTUNQAP01NS01TVFVT4-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
1228 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20304 | 14 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20304 | 14 | 1 | deiTUNQAP01NS01TVFVT4-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
1229 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
1230 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 1 | 1 | deiTUNQAP01NS01TVFVT4-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
1231 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 2 | 1 | deiTUNQAP01NS01TVFVT4-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
1232 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 3 | 1 | deiTUNQAP01NS01TVFVT4-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
1233 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 4 | 1 | deiTUNQAP01NS01TVFVT4-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
1234 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 5 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 5 | 1 | deiTUNQAP01NS01TVFVT4-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
1235 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 6 | 1 | deiTUNQAP01NS01TVFVT4-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
1236 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 7 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 7 | 1 | deiTUNQAP01NS01TVFVT4-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
1237 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 8 | 1 | deiTUNQAP01NS01TVFVT4-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
1238 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 9 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 9 | 1 | deiTUNQAP01NS01TVFVT4-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
1239 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 10 | 1 | deiTUNQAP01NS01TVFVT4-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
1240 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 11 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 11 | 1 | deiTUNQAP01NS01TVFVT4-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
1241 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20306 | 0 | 16 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20306 | 0 | 16 | aeiTUNQAP01NS01TVFVT4-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
1242 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | 31 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 0 | 1 | deiTUNQAP01SS01SENSORTS101733Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1243 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | 31 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 1 | 1 | deiTUNQAP01SS01SENSORTS101733TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1244 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | 31 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 2 | 1 | deiTUNQAP01SS01SENSORTS101733HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1245 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | 31 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 3 | 1 | deiTUNQAP01SS01SENSORTS101733AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1246 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | 31 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20312 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20312 | 0 | 32 | aeiTUNQAP01SS01SENSORTS101733Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1247 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | 31 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20314 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20314 | 0 | 32 | aeiTUNQAP01SS01SENSORTS101733Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1248 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | 32 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 0 | 1 | deiTUNQAP01SS01SENSORTS101817Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1249 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | 32 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 1 | 1 | deiTUNQAP01SS01SENSORTS101817TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1250 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | 32 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 2 | 1 | deiTUNQAP01SS01SENSORTS101817HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1251 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | 32 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 3 | 1 | deiTUNQAP01SS01SENSORTS101817AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1252 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | 32 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20322 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20322 | 0 | 32 | aeiTUNQAP01SS01SENSORTS101817Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1253 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | 32 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20324 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20324 | 0 | 32 | aeiTUNQAP01SS01SENSORTS101817Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1254 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | 33 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 0 | 1 | deiTUNQAP01NS01SENSORTS102057Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1255 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | 33 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 1 | 1 | deiTUNQAP01NS01SENSORTS102057TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1256 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | 33 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 2 | 1 | deiTUNQAP01NS01SENSORTS102057HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1257 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | 33 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 3 | 1 | deiTUNQAP01NS01SENSORTS102057AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1258 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | 33 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20332 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20332 | 0 | 32 | aeiTUNQAP01NS01SENSORTS102057Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1259 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | 33 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20334 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20334 | 0 | 32 | aeiTUNQAP01NS01SENSORTS102057Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1260 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | 34 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 0 | 1 | deiTUNQAP01NS01SENSORTS102121Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1261 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | 34 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 1 | 1 | deiTUNQAP01NS01SENSORTS102121TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1262 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | 34 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 2 | 1 | deiTUNQAP01NS01SENSORTS102121HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1263 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | 34 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 3 | 1 | deiTUNQAP01NS01SENSORTS102121AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1264 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | 34 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20342 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20342 | 0 | 32 | aeiTUNQAP01NS01SENSORTS102121Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1265 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | 34 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20344 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20344 | 0 | 32 | aeiTUNQAP01NS01SENSORTS102121Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1266 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | VS | VS101763 | 35 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20351 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20351 | 0 | 1 | deiTUNQAP01SS01SENSORVS101763Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1267 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | VS | VS101763 | 35 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20352 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20352 | 0 | 32 | aeiTUNQAP01SS01SENSORVS101763Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
1268 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | VS | VS102092 | 36 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20361 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20361 | 0 | 1 | deiTUNQAP01NS01SENSORVS102092Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1269 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | VS | VS102092 | 36 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20362 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20362 | 0 | 32 | aeiTUNQAP01NS01SENSORVS102092Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
1270 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20371 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20371 | 0 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1271 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20371 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20371 | 2 | 1 | deiTUNQAP01SS01DAMPERVT5-TDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1272 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20371 | 4 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20371 | 4 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1273 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10741 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10741 | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1274 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10742 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10742 | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1275 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20371 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20371 | 6 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1276 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10743 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10743 | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1277 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20371 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20371 | 8 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1278 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10744 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10744 | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
1279 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20371 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20371 | 10 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
1280 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10745 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10745 | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
1281 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20371 | 12 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20371 | 12 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
1282 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10746 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10746 | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
1283 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20371 | 14 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20371 | 14 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
1284 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10747 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10747 | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
1285 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20372 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20372 | 0 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
1286 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20372 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20372 | 2 | 1 | deiTUNQAP01SS01DAMPERVT5-TDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
1287 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20372 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20372 | 4 | 1 | deiTUNQAP01SS01DAMPERVT5-TDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
1288 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20372 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20372 | 6 | 1 | deiTUNQAP01SS01DAMPERVT5-TDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1289 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20372 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20372 | 8 | 1 | deiTUNQAP01SS01DAMPERVT5-TDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1290 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20381 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20381 | 0 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1291 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20381 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20381 | 2 | 1 | deiTUNQAP01NS01DAMPERVT6-TDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1292 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20381 | 4 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20381 | 4 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1293 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10761 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10761 | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1294 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10762 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10762 | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1295 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20381 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20381 | 6 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1296 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10763 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10763 | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1297 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20381 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20381 | 8 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1298 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10764 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10764 | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
1299 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20381 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20381 | 10 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
1300 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10765 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10765 | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
1301 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20381 | 12 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20381 | 12 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
1302 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10766 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10766 | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
1303 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20381 | 14 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20381 | 14 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
1304 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10767 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10767 | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
1305 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20382 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20382 | 0 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
1306 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20382 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20382 | 2 | 1 | deiTUNQAP01NS01DAMPERVT6-TDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
1307 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20382 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20382 | 4 | 1 | deiTUNQAP01NS01DAMPERVT6-TDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
1308 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20382 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20382 | 6 | 1 | deiTUNQAP01NS01DAMPERVT6-TDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1309 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20382 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20382 | 8 | 1 | deiTUNQAP01NS01DAMPERVT6-TDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1310 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | 39 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20391 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20391 | 0 | 2 | deiTUNQAP01SS01DAMPERVT1-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1311 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | 39 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20391 | 2 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20391 | 2 | 2 | deiTUNQAP01SS01DAMPERVT1-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1312 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | 39 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 4 | 1 | deiTUNQAP01SS01DAMPERVT1-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
1313 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | 39 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 6 | 1 | deiTUNQAP01SS01DAMPERVT1-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
1314 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | 39 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 8 | 1 | deiTUNQAP01SS01DAMPERVT1-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1315 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | 39 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 10 | 1 | deiTUNQAP01SS01DAMPERVT1-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1316 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | 40 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20401 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20401 | 0 | 2 | deiTUNQAP01SS01DAMPERVT2-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1317 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | 40 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20401 | 2 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20401 | 2 | 2 | deiTUNQAP01SS01DAMPERVT2-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1318 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | 40 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 4 | 1 | deiTUNQAP01SS01DAMPERVT2-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
1319 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | 40 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 6 | 1 | deiTUNQAP01SS01DAMPERVT2-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
1320 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | 40 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 8 | 1 | deiTUNQAP01SS01DAMPERVT2-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1321 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | 40 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 10 | 1 | deiTUNQAP01SS01DAMPERVT2-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1322 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | 41 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20411 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20411 | 0 | 2 | deiTUNQAP01NS01DAMPERVT3-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1323 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | 41 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20411 | 2 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20411 | 2 | 2 | deiTUNQAP01NS01DAMPERVT3-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1324 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | 41 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20411 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20411 | 4 | 1 | deiTUNQAP01NS01DAMPERVT3-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
1325 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | 41 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20411 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20411 | 6 | 1 | deiTUNQAP01NS01DAMPERVT3-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
1326 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | 41 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20411 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20411 | 8 | 1 | deiTUNQAP01NS01DAMPERVT3-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1327 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | 41 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20411 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20411 | 10 | 1 | deiTUNQAP01NS01DAMPERVT3-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1328 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | 42 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20421 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20421 | 0 | 2 | deiTUNQAP01NS01DAMPERVT4-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1329 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | 42 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20421 | 2 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20421 | 2 | 2 | deiTUNQAP01NS01DAMPERVT4-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1330 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | 42 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20421 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20421 | 4 | 1 | deiTUNQAP01NS01DAMPERVT4-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
1331 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | 42 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20421 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20421 | 6 | 1 | deiTUNQAP01NS01DAMPERVT4-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
1332 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | 42 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20421 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20421 | 8 | 1 | deiTUNQAP01NS01DAMPERVT4-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1333 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | 42 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20421 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20421 | 10 | 1 | deiTUNQAP01NS01DAMPERVT4-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1334 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20431 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20431 | 0 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1335 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20431 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20431 | 2 | 1 | deiTUNQAP01SS01DAMPERFR1-BDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1336 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20431 | 4 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20431 | 4 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1337 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10861 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10861 | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1338 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10862 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10862 | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1339 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20431 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20431 | 6 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1340 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10863 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10863 | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1341 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20431 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20431 | 8 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1342 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10864 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10864 | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
1343 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20431 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20431 | 10 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
1344 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10865 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10865 | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
1345 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20431 | 12 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20431 | 12 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
1346 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10866 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10866 | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
1347 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20431 | 14 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20431 | 14 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
1348 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10867 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10867 | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
1349 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20432 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20432 | 0 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
1350 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20432 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20432 | 2 | 1 | deiTUNQAP01SS01DAMPERFR1-BDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
1351 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20432 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20432 | 4 | 1 | deiTUNQAP01SS01DAMPERFR1-BDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
1352 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20432 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20432 | 6 | 1 | deiTUNQAP01SS01DAMPERFR1-BDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1353 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20432 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20432 | 8 | 1 | deiTUNQAP01SS01DAMPERFR1-BDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1354 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20441 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20441 | 0 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1355 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20441 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20441 | 2 | 1 | deiTUNQAP01NS01DAMPERFR2-BDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1356 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20441 | 4 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20441 | 4 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1357 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10881 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10881 | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1358 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10882 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10882 | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1359 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20441 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20441 | 6 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1360 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10883 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10883 | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1361 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20441 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20441 | 8 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1362 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10884 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10884 | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
1363 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20441 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20441 | 10 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
1364 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10885 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10885 | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
1365 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20441 | 12 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20441 | 12 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
1366 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10886 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10886 | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
1367 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20441 | 14 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20441 | 14 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
1368 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10887 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10887 | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
1369 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20442 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20442 | 0 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
1370 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20442 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20442 | 2 | 1 | deiTUNQAP01NS01DAMPERFR2-BDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
1371 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20442 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20442 | 4 | 1 | deiTUNQAP01NS01DAMPERFR2-BDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
1372 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20442 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20442 | 6 | 1 | deiTUNQAP01NS01DAMPERFR2-BDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1373 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20442 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20442 | 8 | 1 | deiTUNQAP01NS01DAMPERFR2-BDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1374 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-63 | 45 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20451 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20451 | 0 | 2 | deiTUNQAP01SS01DAMPERCON-63Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1375 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-63 | 45 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20451 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20451 | 2 | 1 | deiTUNQAP01SS01DAMPERCON-63CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1376 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-63 | 45 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20451 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20451 | 4 | 1 | deiTUNQAP01SS01DAMPERCON-63TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1377 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-63 | 45 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20451 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20451 | 6 | 1 | deiTUNQAP01SS01DAMPERCON-63LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
1378 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-54 | 46 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20461 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20461 | 0 | 2 | deiTUNQAP01NS01DAMPERCON-54Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1379 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-54 | 46 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20461 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20461 | 2 | 1 | deiTUNQAP01NS01DAMPERCON-54CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1380 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-54 | 46 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20461 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20461 | 4 | 1 | deiTUNQAP01NS01DAMPERCON-54TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1381 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-54 | 46 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20461 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20461 | 6 | 1 | deiTUNQAP01NS01DAMPERCON-54LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
1382 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-66 | 47 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20471 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20471 | 0 | 2 | deiTUNQAP01SS01DAMPERCON-66Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1383 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-66 | 47 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20471 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20471 | 2 | 1 | deiTUNQAP01SS01DAMPERCON-66CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1384 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-66 | 47 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20471 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20471 | 4 | 1 | deiTUNQAP01SS01DAMPERCON-66TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1385 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-66 | 47 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20471 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20471 | 6 | 1 | deiTUNQAP01SS01DAMPERCON-66LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
1386 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-61 | 48 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20481 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20481 | 0 | 2 | deiTUNQAP01SS01DAMPERCON-61Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1387 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-61 | 48 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20481 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20481 | 2 | 1 | deiTUNQAP01SS01DAMPERCON-61CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1388 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-61 | 48 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20481 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20481 | 4 | 1 | deiTUNQAP01SS01DAMPERCON-61TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1389 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-61 | 48 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20481 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20481 | 6 | 1 | deiTUNQAP01SS01DAMPERCON-61LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
1390 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-56 | 49 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20491 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20491 | 0 | 2 | deiTUNQAP01NS01DAMPERCON-56Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1391 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-56 | 49 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20491 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20491 | 2 | 1 | deiTUNQAP01NS01DAMPERCON-56CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1392 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-56 | 49 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20491 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20491 | 4 | 1 | deiTUNQAP01NS01DAMPERCON-56TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1393 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-56 | 49 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20491 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20491 | 6 | 1 | deiTUNQAP01NS01DAMPERCON-56LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
1394 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-51 | 50 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20501 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20501 | 0 | 2 | deiTUNQAP01NS01DAMPERCON-51Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1395 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-51 | 50 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20501 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20501 | 2 | 1 | deiTUNQAP01NS01DAMPERCON-51CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1396 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-51 | 50 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20501 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20501 | 4 | 1 | deiTUNQAP01NS01DAMPERCON-51TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1397 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-51 | 50 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20501 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20501 | 6 | 1 | deiTUNQAP01NS01DAMPERCON-51LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
1398 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-67 | 51 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20511 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20511 | 0 | 2 | deiTUNQAP01SS01DAMPERCON-67Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1399 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-67 | 51 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20511 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20511 | 2 | 1 | deiTUNQAP01SS01DAMPERCON-67CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1400 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-67 | 51 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20511 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20511 | 4 | 1 | deiTUNQAP01SS01DAMPERCON-67TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1401 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-67 | 51 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20511 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20511 | 6 | 1 | deiTUNQAP01SS01DAMPERCON-67LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
1402 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-59 | 52 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20521 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20521 | 0 | 2 | deiTUNQAP01SS01DAMPERCON-59Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1403 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-59 | 52 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20521 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20521 | 2 | 1 | deiTUNQAP01SS01DAMPERCON-59CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1404 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-59 | 52 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20521 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20521 | 4 | 1 | deiTUNQAP01SS01DAMPERCON-59TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1405 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-59 | 52 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20521 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20521 | 6 | 1 | deiTUNQAP01SS01DAMPERCON-59LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
1406 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-58 | 53 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20531 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20531 | 0 | 2 | deiTUNQAP01NS01DAMPERCON-58Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1407 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-58 | 53 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20531 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20531 | 2 | 1 | deiTUNQAP01NS01DAMPERCON-58CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1408 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-58 | 53 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20531 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20531 | 4 | 1 | deiTUNQAP01NS01DAMPERCON-58TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1409 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-58 | 53 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20531 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20531 | 6 | 1 | deiTUNQAP01NS01DAMPERCON-58LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
1410 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-52 | 54 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20541 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20541 | 0 | 2 | deiTUNQAP01NS01DAMPERCON-52Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1411 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-52 | 54 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20541 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20541 | 2 | 1 | deiTUNQAP01NS01DAMPERCON-52CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
1412 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-52 | 54 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20541 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20541 | 4 | 1 | deiTUNQAP01NS01DAMPERCON-52TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
1413 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-52 | 54 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20541 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20541 | 6 | 1 | deiTUNQAP01NS01DAMPERCON-52LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
1414 | QAP01_RTU | TUN:QAP01 | SS01:AHU | AHU | CON-08 | 55 | ControlMod | SIL0 | MODBUS:4:Read:Input Registers | 20551 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20551 | 0 | 1 | deiTUNQAP01SS01AHUCON-08ControlMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1415 | QAP01_RTU | TUN:QAP01 | SS01:AHU | AHU | CON-08 | 55 | RunStat | SIL0 | MODBUS:4:Read:Input Registers | 20551 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20551 | 1 | 1 | deiTUNQAP01SS01AHUCON-08RunStat | 4 |  |  | 0 | $ComStatus , , | #RUN
1416 | QAP01_RTU | TUN:QAP01 | SS01:AHU | AHU | CON-07 | 56 | ControlMod | SIL0 | MODBUS:4:Read:Input Registers | 20561 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20561 | 0 | 1 | deiTUNQAP01SS01AHUCON-07ControlMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1417 | QAP01_RTU | TUN:QAP01 | SS01:AHU | AHU | CON-07 | 56 | RunStat | SIL0 | MODBUS:4:Read:Input Registers | 20561 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20561 | 1 | 1 | deiTUNQAP01SS01AHUCON-07RunStat | 4 |  |  | 0 | $ComStatus , , | #RUN
1418 | QAP01_RTU | TUN:QAP01 | NS01:AHU | AHU | CON-06 | 57 | ControlMod | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 0 | 1 | deiTUNQAP01NS01AHUCON-06ControlMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1419 | QAP01_RTU | TUN:QAP01 | NS01:AHU | AHU | CON-06 | 57 | RunStat | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 1 | 1 | deiTUNQAP01NS01AHUCON-06RunStat | 4 |  |  | 0 | $ComStatus , , | #RUN
1420 | QAP01_RTU | TUN:QAP01 | NS01:AHU | AHU | CON-05 | 58 | ControlMod | SIL0 | MODBUS:4:Read:Input Registers | 20581 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20581 | 0 | 1 | deiTUNQAP01NS01AHUCON-05ControlMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1421 | QAP01_RTU | TUN:QAP01 | NS01:AHU | AHU | CON-05 | 58 | RunStat | SIL0 | MODBUS:4:Read:Input Registers | 20581 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20581 | 1 | 1 | deiTUNQAP01NS01AHUCON-05RunStat | 4 |  |  | 0 | $ComStatus , , | #RUN
1422 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Vac240SwOp | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 0 | 1 | deiTUNQAP01MMSSPLC01Vac240SwOp | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY DISCONNECTING SWITCH - OPEN
1423 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Vac240Volt | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 1 | 1 | deiTUNQAP01MMSSPLC01Vac240Volt | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY VOLTAGE PRESENCE
1424 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | VolOpen | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 2 | 1 | deiTUNQAP01MMSSPLC01VolOpen | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER OPEN
1425 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | VolFault | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 3 | 1 | deiTUNQAP01MMSSPLC01VolFault | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER FAULT
1426 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | VolSupOpen | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 4 | 1 | deiTUNQAP01MMSSPLC01VolSupOpen | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN
1427 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | VolSupFault | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 5 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 5 | 1 | deiTUNQAP01MMSSPLC01VolSupFault | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT
1428 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | CabOpen | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 6 | 1 | deiTUNQAP01MMSSPLC01CabOpen | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS OPEN
1429 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | CabFault | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 7 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 7 | 1 | deiTUNQAP01MMSSPLC01CabFault | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS FAULT
1430 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | SerOpen | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 8 | 1 | deiTUNQAP01MMSSPLC01SerOpen | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER OPEN
1431 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | SerFault | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 9 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 9 | 1 | deiTUNQAP01MMSSPLC01SerFault | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER FAULT
1432 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | UpsBreOpen | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 10 | 1 | deiTUNQAP01MMSSPLC01UpsBreOpen | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER OPEN
1433 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | UpsBreFault | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 11 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 11 | 1 | deiTUNQAP01MMSSPLC01UpsBreFault | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER FAULT
1434 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | UpsSwOpen | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 12 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 12 | 1 | deiTUNQAP01MMSSPLC01UpsSwOpen | 4 |  |  | 0 | $ComStatus , , | #UPS DISCONNECTING SWITCH OPEN
1435 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | UpsFault | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 13 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 13 | 1 | deiTUNQAP01MMSSPLC01UpsFault | 4 |  |  | 0 | $ComStatus , , | #UPS FAULT
1436 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Sup24Vdc1Open | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 14 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 14 | 1 | deiTUNQAP01MMSSPLC01Sup24Vdc1Open | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN
1437 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Sup24Vdc1Fault | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 15 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 15 | 1 | deiTUNQAP01MMSSPLC01Sup24Vdc1Fault | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT
1438 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Sup24Vdc1Volt | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 0 | 1 | deiTUNQAP01MMSSPLC01Sup24Vdc1Volt | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 ABSENCE OF VOLTAGE
1439 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Sup24Vdc2Open | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 1 | 1 | deiTUNQAP01MMSSPLC01Sup24Vdc2Open | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN
1440 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Sup24Vdc2Fault | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 2 | 1 | deiTUNQAP01MMSSPLC01Sup24Vdc2Fault | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT
1441 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Sup24Vdc2Volt | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 3 | 1 | deiTUNQAP01MMSSPLC01Sup24Vdc2Volt | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 ABSENCE OF VOLTAGE
1442 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | SwOpen | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 4 | 1 | deiTUNQAP01MMSSPLC01SwOpen | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER OPEN
1443 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | SwFault | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 5 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 5 | 1 | deiTUNQAP01MMSSPLC01SwFault | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER FAULT
1444 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | LcpOpen | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 6 | 1 | deiTUNQAP01MMSSPLC01LcpOpen | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER OPEN
1445 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | LcpFault | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 7 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 7 | 1 | deiTUNQAP01MMSSPLC01LcpFault | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER FAULT
1446 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Plc1Open | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 8 | 1 | deiTUNQAP01MMSSPLC01Plc1Open | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER OPEN
1447 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Plc1Fault | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 9 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 9 | 1 | deiTUNQAP01MMSSPLC01Plc1Fault | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER FAULT
1448 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Plc2Open | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 10 | 1 | deiTUNQAP01MMSSPLC01Plc2Open | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER OPEN
1449 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Plc2Fault | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 11 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 11 | 1 | deiTUNQAP01MMSSPLC01Plc2Fault | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER FAULT
1450 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | SuArTrig | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 12 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 12 | 1 | deiTUNQAP01MMSSPLC01SuArTrig | 4 |  |  | 0 | $ComStatus , , | #SURGE ARRESTER TRIGGERED
1451 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mcsd1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 0 | 1 | deiTUNQAP01MMSLPS-MDB01Mcsd1Stat | 4 |  |  | 0 | $ComStatus , , | #Power normal MCSD 1 status
1452 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mcsd2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 1 | 1 | deiTUNQAP01MMSLPS-MDB01Mcsd2Stat | 4 |  |  | 0 | $ComStatus , , | #Power replacement MCSD 2 status
1453 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mcsd1pos | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 2 | 1 | deiTUNQAP01MMSLPS-MDB01Mcsd1pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 1 racked position
1454 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mcsd2pos | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 3 | 1 | deiTUNQAP01MMSLPS-MDB01Mcsd2pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 2 racked position
1455 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Change | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 4 | 1 | deiTUNQAP01MMSLPS-MDB01Change | 4 |  |  | 0 | $ComStatus , , | #Change over
1456 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | relay1 | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 5 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 5 | 1 | deiTUNQAP01MMSLPS-MDB01relay1 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 1
1457 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | relay2 | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 6 | 1 | deiTUNQAP01MMSLPS-MDB01relay2 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 2
1458 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 7 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 7 | 1 | deiTUNQAP01MMSLPS-MDB01Closed | 4 |  |  | 0 | $ComStatus , , | #MCB closed status
1459 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 8 | 1 | deiTUNQAP01MMSLPS-MDB01Trip | 4 |  |  | 0 | $ComStatus , , | #MCB tripped status
1460 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | PowerCut | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 9 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 9 | 1 | deiTUNQAP01MMSLPS-MDB01PowerCut | 4 |  |  | 0 | $ComStatus , , | #Emergency power cut (push button)
1461 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mccb1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 10 | 1 | deiTUNQAP01MMSLPS-MDB01Mccb1Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 status
1462 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 11 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 11 | 1 | deiTUNQAP01MMSLPS-MDB01Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 trip
1463 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mccb2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 12 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 12 | 1 | deiTUNQAP01MMSLPS-MDB01Mccb2Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 status
1464 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 13 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 13 | 1 | deiTUNQAP01MMSLPS-MDB01Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 trip
1465 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mccb3Stat | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 14 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 14 | 1 | deiTUNQAP01MMSLPS-MDB01Mccb3Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 status
1466 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mccb3Trip | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 15 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 15 | 1 | deiTUNQAP01MMSLPS-MDB01Mccb3Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 trip
1467 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mcsd1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 0 | 1 | deiTUNQAP01MMSLPS-MDB02Mcsd1Stat | 4 |  |  | 0 | $ComStatus , , | #Power normal MCSD 1 status
1468 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mcsd2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 1 | 1 | deiTUNQAP01MMSLPS-MDB02Mcsd2Stat | 4 |  |  | 0 | $ComStatus , , | #Power replacement MCSD 2 status
1469 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mcsd1pos | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 2 | 1 | deiTUNQAP01MMSLPS-MDB02Mcsd1pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 1 racked position
1470 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mcsd2pos | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 3 | 1 | deiTUNQAP01MMSLPS-MDB02Mcsd2pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 2 racked position
1471 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Change | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 4 | 1 | deiTUNQAP01MMSLPS-MDB02Change | 4 |  |  | 0 | $ComStatus , , | #Change over
1472 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | relay1 | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 5 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 5 | 1 | deiTUNQAP01MMSLPS-MDB02relay1 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 1
1473 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | relay2 | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 6 | 1 | deiTUNQAP01MMSLPS-MDB02relay2 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 2
1474 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 7 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 7 | 1 | deiTUNQAP01MMSLPS-MDB02Closed | 4 |  |  | 0 | $ComStatus , , | #MCB closed status
1475 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 8 | 1 | deiTUNQAP01MMSLPS-MDB02Trip | 4 |  |  | 0 | $ComStatus , , | #MCB tripped status
1476 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | PowerCut | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 9 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 9 | 1 | deiTUNQAP01MMSLPS-MDB02PowerCut | 4 |  |  | 0 | $ComStatus , , | #Emergency power cut (push button)
1477 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mccb1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 10 | 1 | deiTUNQAP01MMSLPS-MDB02Mccb1Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 status
1478 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 11 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 11 | 1 | deiTUNQAP01MMSLPS-MDB02Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 trip
1479 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mccb2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 12 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 12 | 1 | deiTUNQAP01MMSLPS-MDB02Mccb2Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 status
1480 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 13 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 13 | 1 | deiTUNQAP01MMSLPS-MDB02Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 trip
1481 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mccb3Stat | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 14 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 14 | 1 | deiTUNQAP01MMSLPS-MDB02Mccb3Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 status
1482 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mccb3Trip | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 15 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 15 | 1 | deiTUNQAP01MMSLPS-MDB02Mccb3Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 trip
1483 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL1-IO01 | 62 | Relay | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 0 | 1 | deiTUNQAP01MMSEL1-IO01Relay | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay
1484 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL1-IO01 | 62 | Isolator | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 1 | 1 | deiTUNQAP01MMSEL1-IO01Isolator | 4 |  |  | 0 | $ComStatus , , | #LBS Main incomer isolator status
1485 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL1-IO01 | 62 | Supply | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 2 | 1 | deiTUNQAP01MMSEL1-IO01Supply | 4 |  |  | 0 | $ComStatus , , | #UPS supply status
1486 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL1-IO01 | 62 | Faulty | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 3 | 1 | deiTUNQAP01MMSEL1-IO01Faulty | 4 |  |  | 0 | $ComStatus , , | #UPS faulty
1487 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL1-IO01 | 62 | Power | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 4 | 1 | deiTUNQAP01MMSEL1-IO01Power | 4 |  |  | 0 | $ComStatus , , | #24VDC UPS power status
1488 | QAP01_RTU | TUN:QAP01 | MMS | MCCB | EL1-UPS | 63 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20631 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20631 | 0 | 1 | deiTUNQAP01MMSEL1-UPSTrip | 4 |  |  | 0 | $ComStatus , , | #MCCB trip status
1489 | QAP01_RTU | TUN:QAP01 | MMS | MCCB | EL1-UPS | 63 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20631 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20631 | 1 | 1 | deiTUNQAP01MMSEL1-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #MCCB closed status
1490 | QAP01_RTU | TUN:QAP01 | MMS | LBS | EL1-UPS | 64 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 0 | 1 | deiTUNQAP01MMSEL1-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #LBS closed status
1491 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL1-VSD01 | 65 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 0 | 1 | deiTUNQAP01MMSUPS_EL1-VSD01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1492 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL1-VSD01 | 65 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 1 | 1 | deiTUNQAP01MMSUPS_EL1-VSD01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1493 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL1-VSD02 | 66 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20661 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20661 | 0 | 1 | deiTUNQAP01MMSUPS_EL1-VSD02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1494 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL1-VSD02 | 66 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20661 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20661 | 1 | 1 | deiTUNQAP01MMSUPS_EL1-VSD02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1495 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT3-IDP01 | 67 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 0 | 1 | deiTUNQAP01MMS3P-VT3-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1496 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT3-IDP01 | 67 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 1 | 1 | deiTUNQAP01MMS3P-VT3-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1497 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT3-IDP01 | 68 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20681 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20681 | 0 | 1 | deiTUNQAP01MMS2P-VT3-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1498 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT3-IDP01 | 68 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20681 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20681 | 1 | 1 | deiTUNQAP01MMS2P-VT3-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1499 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT4-IDP01 | 69 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20691 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20691 | 0 | 1 | deiTUNQAP01MMS3P-VT4-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1500 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT4-IDP01 | 69 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20691 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20691 | 1 | 1 | deiTUNQAP01MMS3P-VT4-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1501 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT4-IDP01 | 70 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20701 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20701 | 0 | 1 | deiTUNQAP01MMS2P-VT4-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1502 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT4-IDP01 | 70 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20701 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20701 | 1 | 1 | deiTUNQAP01MMS2P-VT4-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1503 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-01 | 71 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20711 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20711 | 0 | 1 | deiTUNQAP01MMS3P-VT6-TDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1504 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-01 | 71 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20711 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20711 | 1 | 1 | deiTUNQAP01MMS3P-VT6-TDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1505 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-01 | 72 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20721 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20721 | 0 | 1 | deiTUNQAP01MMS2P-VT6-TDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1506 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-01 | 72 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20721 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20721 | 1 | 1 | deiTUNQAP01MMS2P-VT6-TDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1507 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-02 | 73 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20731 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20731 | 0 | 1 | deiTUNQAP01MMS3P-VT6-TDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1508 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-02 | 73 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20731 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20731 | 1 | 1 | deiTUNQAP01MMS3P-VT6-TDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1509 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-02 | 74 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 0 | 1 | deiTUNQAP01MMS2P-VT6-TDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1510 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-02 | 74 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 1 | 1 | deiTUNQAP01MMS2P-VT6-TDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1511 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-03 | 75 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 0 | 1 | deiTUNQAP01MMS3P-VT6-TDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1512 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-03 | 75 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 1 | 1 | deiTUNQAP01MMS3P-VT6-TDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1513 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-03 | 76 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 0 | 1 | deiTUNQAP01MMS2P-VT6-TDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1514 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-03 | 76 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 1 | 1 | deiTUNQAP01MMS2P-VT6-TDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1515 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P--FR2-BDP01-01 | 77 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20771 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20771 | 0 | 1 | deiTUNQAP01MMS3P--FR2-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1516 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P--FR2-BDP01-01 | 77 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20771 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20771 | 1 | 1 | deiTUNQAP01MMS3P--FR2-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1517 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P--FR2-BDP01-01 | 78 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20781 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20781 | 0 | 1 | deiTUNQAP01MMS2P--FR2-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1518 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P--FR2-BDP01-01 | 78 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20781 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20781 | 1 | 1 | deiTUNQAP01MMS2P--FR2-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1519 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P--FR2-BDP01-02 | 79 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20791 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20791 | 0 | 1 | deiTUNQAP01MMS3P--FR2-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1520 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P--FR2-BDP01-02 | 79 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20791 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20791 | 1 | 1 | deiTUNQAP01MMS3P--FR2-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1521 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P--FR2-BDP01-02 | 80 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20801 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20801 | 0 | 1 | deiTUNQAP01MMS2P--FR2-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1522 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P--FR2-BDP01-02 | 80 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20801 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20801 | 1 | 1 | deiTUNQAP01MMS2P--FR2-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1523 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-54 | 81 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20811 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20811 | 0 | 1 | deiTUNQAP01MMSMSFD-CON-54McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1524 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-54 | 81 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20811 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20811 | 1 | 1 | deiTUNQAP01MMSMSFD-CON-54McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1525 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-52 | 82 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20821 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20821 | 0 | 1 | deiTUNQAP01MMSMSFD-CON-52McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1526 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-52 | 82 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20821 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20821 | 1 | 1 | deiTUNQAP01MMSMSFD-CON-52McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1527 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-58 | 83 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20831 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20831 | 0 | 1 | deiTUNQAP01MMSMSFD-CON-58McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1528 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-58 | 83 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20831 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20831 | 1 | 1 | deiTUNQAP01MMSMSFD-CON-58McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1529 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL2-IO01 | 84 | Relay | SIL0 | MODBUS:4:Read:Input Registers | 20841 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20841 | 0 | 1 | deiTUNQAP01MMSEL2-IO01Relay | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay
1530 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL2-IO01 | 84 | Isolator | SIL0 | MODBUS:4:Read:Input Registers | 20841 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20841 | 1 | 1 | deiTUNQAP01MMSEL2-IO01Isolator | 4 |  |  | 0 | $ComStatus , , | #LBS Main incomer isolator status
1531 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL2-IO01 | 84 | Supply | SIL0 | MODBUS:4:Read:Input Registers | 20841 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20841 | 2 | 1 | deiTUNQAP01MMSEL2-IO01Supply | 4 |  |  | 0 | $ComStatus , , | #UPS supply status
1532 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL2-IO01 | 84 | Faulty | SIL0 | MODBUS:4:Read:Input Registers | 20841 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20841 | 3 | 1 | deiTUNQAP01MMSEL2-IO01Faulty | 4 |  |  | 0 | $ComStatus , , | #UPS faulty
1533 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL2-IO01 | 84 | Power | SIL0 | MODBUS:4:Read:Input Registers | 20841 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20841 | 4 | 1 | deiTUNQAP01MMSEL2-IO01Power | 4 |  |  | 0 | $ComStatus , , | #24VDC UPS power status
1534 | QAP01_RTU | TUN:QAP01 | MMS | MCCB | EL2-UPS | 85 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20851 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20851 | 0 | 1 | deiTUNQAP01MMSEL2-UPSTrip | 4 |  |  | 0 | $ComStatus , , | #MCCB trip status
1535 | QAP01_RTU | TUN:QAP01 | MMS | MCCB | EL2-UPS | 85 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20851 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20851 | 1 | 1 | deiTUNQAP01MMSEL2-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #MCCB closed status
1536 | QAP01_RTU | TUN:QAP01 | MMS | LBS | EL2-UPS | 86 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20861 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20861 | 0 | 1 | deiTUNQAP01MMSEL2-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #LBS closed status
1537 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL2-VSD01 | 87 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20871 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20871 | 0 | 1 | deiTUNQAP01MMSUPS_EL2-VSD01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1538 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL2-VSD01 | 87 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20871 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20871 | 1 | 1 | deiTUNQAP01MMSUPS_EL2-VSD01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1539 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL2-VSD02 | 88 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20881 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20881 | 0 | 1 | deiTUNQAP01MMSUPS_EL2-VSD02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1540 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL2-VSD02 | 88 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20881 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20881 | 1 | 1 | deiTUNQAP01MMSUPS_EL2-VSD02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1541 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT1-IDP01 | 89 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20891 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20891 | 0 | 1 | deiTUNQAP01MMS3P-VT1-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1542 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT1-IDP01 | 89 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20891 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20891 | 1 | 1 | deiTUNQAP01MMS3P-VT1-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1543 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT1-IDP01 | 90 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20901 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20901 | 0 | 1 | deiTUNQAP01MMS2P-VT1-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1544 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT1-IDP01 | 90 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20901 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20901 | 1 | 1 | deiTUNQAP01MMS2P-VT1-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1545 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT2-IDP01 | 91 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20911 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20911 | 0 | 1 | deiTUNQAP01MMS3P-VT2-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1546 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT2-IDP01 | 91 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20911 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20911 | 1 | 1 | deiTUNQAP01MMS3P-VT2-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1547 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT2-IDP01 | 92 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20921 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20921 | 0 | 1 | deiTUNQAP01MMS2P-VT2-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1548 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT2-IDP01 | 92 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20921 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20921 | 1 | 1 | deiTUNQAP01MMS2P-VT2-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1549 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-01 | 93 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20931 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20931 | 0 | 1 | deiTUNQAP01MMS3P-VT5-TDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1550 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-01 | 93 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20931 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20931 | 1 | 1 | deiTUNQAP01MMS3P-VT5-TDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1551 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-01 | 94 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20941 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20941 | 0 | 1 | deiTUNQAP01MMS2P-VT5-TDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1552 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-01 | 94 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20941 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20941 | 1 | 1 | deiTUNQAP01MMS2P-VT5-TDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1553 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-02 | 95 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20951 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20951 | 0 | 1 | deiTUNQAP01MMS3P-VT5-TDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1554 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-02 | 95 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20951 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20951 | 1 | 1 | deiTUNQAP01MMS3P-VT5-TDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1555 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-02 | 96 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20961 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20961 | 0 | 1 | deiTUNQAP01MMS2P-VT5-TDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1556 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-02 | 96 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20961 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20961 | 1 | 1 | deiTUNQAP01MMS2P-VT5-TDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1557 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-03 | 97 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20971 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20971 | 0 | 1 | deiTUNQAP01MMS3P-VT5-TDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1558 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-03 | 97 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20971 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20971 | 1 | 1 | deiTUNQAP01MMS3P-VT5-TDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1559 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-03 | 98 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20981 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20981 | 0 | 1 | deiTUNQAP01MMS2P-VT5-TDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1560 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-03 | 98 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20981 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20981 | 1 | 1 | deiTUNQAP01MMS2P-VT5-TDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1561 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-FR1-BDP01-01 | 99 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20991 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20991 | 0 | 1 | deiTUNQAP01MMS3P-FR1-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1562 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-FR1-BDP01-01 | 99 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20991 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20991 | 1 | 1 | deiTUNQAP01MMS3P-FR1-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1563 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-FR1-BDP01-01 | 100 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21001 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21001 | 0 | 1 | deiTUNQAP01MMS2P-FR1-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1564 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-FR1-BDP01-01 | 100 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21001 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21001 | 1 | 1 | deiTUNQAP01MMS2P-FR1-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1565 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-FR1-BDP01-02 | 101 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21011 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21011 | 0 | 1 | deiTUNQAP01MMS3P-FR1-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1566 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-FR1-BDP01-02 | 101 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21011 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21011 | 1 | 1 | deiTUNQAP01MMS3P-FR1-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1567 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-FR1-BDP01-02 | 102 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21021 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21021 | 0 | 1 | deiTUNQAP01MMS2P-FR1-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1568 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-FR1-BDP01-02 | 102 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21021 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21021 | 1 | 1 | deiTUNQAP01MMS2P-FR1-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1569 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-63 | 103 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21031 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21031 | 0 | 1 | deiTUNQAP01MMSMSFD-CON-63McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1570 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-63 | 103 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21031 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21031 | 1 | 1 | deiTUNQAP01MMSMSFD-CON-63McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1571 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-59 | 104 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21041 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21041 | 0 | 1 | deiTUNQAP01MMSMSFD-CON-59McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1572 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-59 | 104 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21041 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21041 | 1 | 1 | deiTUNQAP01MMSMSFD-CON-59McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1573 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-67 | 105 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21051 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21051 | 0 | 1 | deiTUNQAP01MMSMSFD-CON-67McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
1574 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-67 | 105 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21051 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21051 | 1 | 1 | deiTUNQAP01MMSMSFD-CON-67McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
1575 | QEC01_RTU | TUN:QEC01 | SCR | LCP | LCP01 | 1 | ComFaultPlc | SIL0 | MODBUS:4:Read:Input Registers | 20011 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20011 | 0 | 1 | deiTUNQEC01SCRLCP01ComFaultPlc | 4 |  |  | 0 | $ComStatus , , | #COMMUNICATION FAULT WITH PLC
1576 | QEC01_RTU | TUN:QEC01 | SCR | LCP | LCP01 | 1 | LcpMode | SIL0 | MODBUS:4:Read:Input Registers | 20011 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20011 | 1 | 1 | deiTUNQEC01SCRLCP01LcpMode | 4 |  |  | 0 | $ComStatus , , | #LOCAL / REMOTE STATUS
1577 | QEC01_RTU | TUN:QEC01 | SCR | FMOP | FMOP01 | 2 | EmergNod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20021 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20021 | 0 | 1 | deiTUNQEC01SCRFMOP01EmergNod | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
1578 | QEC01_RTU | TUN:QEC01 | SCR | FMOP | FMOP01 | 2 | RightStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20021 | 1 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20021 | 1 | 1 | deiTUNQEC01SCRFMOP01RightStat | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
1579 | QEC01_RTU | TUN:QEC01 | SCR | FMOP | FMOP01 | 2 | LeftStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20021 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20021 | 2 | 1 | deiTUNQEC01SCRFMOP01LeftStat | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
1580 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 3 | PlcState | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 0 | 1 | deiTUNQEC01TELPLC01PlcState | 4 |  |  | 0 | $ComStatus , , | #PLC A/B OFFLINE
1581 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 3 | OpStatus | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 1 | 1 | deiTUNQEC01TELPLC01OpStatus | 4 |  |  | 0 | $ComStatus , , | #PLC RUNNING.
1582 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 3 | PwStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 2 | 1 | deiTUNQEC01TELPLC01PwStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: POWER SUPPLY FAULT
1583 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 3 | CpuStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 3 | 1 | deiTUNQEC01TELPLC01CpuStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CPU MODULE FAULT
1584 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 3 | CrpStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 4 | 1 | deiTUNQEC01TELPLC01CrpStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CRP MODULE FAULT
1585 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 3 | CraStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 5 | 1 | deiTUNQEC01TELPLC01CraStat | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
1586 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 3 | NrpStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 6 | 1 | deiTUNQEC01TELPLC01NrpStat | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
1587 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 3 | ComStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 7 | 1 | deiTUNQEC01TELPLC01ComStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
1588 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 3 | IoStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 8 | 1 | deiTUNQEC01TELPLC01IoStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
1589 | QEC01_RTU | TUN:QEC01 | TEL | SWI | SWI01 | 4 | SwStat | SIL0 | MODBUS:4:Read:Input Registers | 20041 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20041 | 0 | 1 | deiTUNQEC01TELSWI01SwStat | 4 |  |  | 0 | $ComStatus , , | #SWITCH FAULT
1590 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20051 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20051 | 0 | 1 | deiTUNQEC01SS01PFAPLA-01ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1591 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20051 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20051 | 2 | 1 | deiTUNQEC01SS01PFAPLA-01OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1592 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20051 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20051 | 4 | 1 | deiTUNQEC01SS01PFAPLA-01AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
1593 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10101 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10101 | 0 | 1 | deoTUNQEC01SS01PFAPLA-01CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1594 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10102 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10102 | 0 | 1 | deoTUNQEC01SS01PFAPLA-01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1595 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 6 | 2 | deiTUNQEC01SS01PFAPLA-01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1596 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10103 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10103 | 0 | 1 | deoTUNQEC01SS01PFAPLA-01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1597 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 8 | 2 | deiTUNQEC01SS01PFAPLA-01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1598 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10104 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10104 | 0 | 1 | deoTUNQEC01SS01PFAPLA-01CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
1599 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 10 | 2 | deiTUNQEC01SS01PFAPLA-01AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
1600 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10105 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10105 | 0 | 1 | deoTUNQEC01SS01PFAPLA-01CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
1601 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 12 | 2 | deiTUNQEC01SS01PFAPLA-01AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
1602 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10106 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10106 | 0 | 1 | deoTUNQEC01SS01PFAPLA-01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1603 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 14 | 2 | deiTUNQEC01SS01PFAPLA-01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1604 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10107 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10107 | 0 | 1 | deoTUNQEC01SS01PFAPLA-01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1605 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20052 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20052 | 0 | 2 | deiTUNQEC01SS01PFAPLA-01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1606 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20052 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20052 | 2 | 1 | deiTUNQEC01SS01PFAPLA-01StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
1607 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20052 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20052 | 4 | 1 | deiTUNQEC01SS01PFAPLA-01StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
1608 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20061 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20061 | 0 | 1 | deiTUNQEC01SS01PFAGRD-01ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1609 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20061 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20061 | 2 | 1 | deiTUNQEC01SS01PFAGRD-01OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1610 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20061 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20061 | 4 | 1 | deiTUNQEC01SS01PFAGRD-01AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
1611 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10121 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10121 | 0 | 1 | deoTUNQEC01SS01PFAGRD-01CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1612 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10122 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10122 | 0 | 1 | deoTUNQEC01SS01PFAGRD-01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1613 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 6 | 2 | deiTUNQEC01SS01PFAGRD-01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1614 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10123 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10123 | 0 | 1 | deoTUNQEC01SS01PFAGRD-01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1615 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 8 | 2 | deiTUNQEC01SS01PFAGRD-01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1616 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10124 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10124 | 0 | 1 | deoTUNQEC01SS01PFAGRD-01CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
1617 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 10 | 2 | deiTUNQEC01SS01PFAGRD-01AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
1618 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10125 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10125 | 0 | 1 | deoTUNQEC01SS01PFAGRD-01CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
1619 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 12 | 2 | deiTUNQEC01SS01PFAGRD-01AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
1620 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10126 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10126 | 0 | 1 | deoTUNQEC01SS01PFAGRD-01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1621 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 14 | 2 | deiTUNQEC01SS01PFAGRD-01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1622 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10127 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10127 | 0 | 1 | deoTUNQEC01SS01PFAGRD-01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1623 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20062 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20062 | 0 | 2 | deiTUNQEC01SS01PFAGRD-01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1624 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20062 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20062 | 2 | 1 | deiTUNQEC01SS01PFAGRD-01StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
1625 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20062 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20062 | 4 | 1 | deiTUNQEC01SS01PFAGRD-01StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
1626 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20071 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20071 | 0 | 1 | deiTUNQEC01NS01PFAPLA-02ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1627 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20071 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20071 | 2 | 1 | deiTUNQEC01NS01PFAPLA-02OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1628 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20071 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20071 | 4 | 1 | deiTUNQEC01NS01PFAPLA-02AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
1629 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10141 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10141 | 0 | 1 | deoTUNQEC01NS01PFAPLA-02CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1630 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10142 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10142 | 0 | 1 | deoTUNQEC01NS01PFAPLA-02CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1631 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 6 | 2 | deiTUNQEC01NS01PFAPLA-02AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1632 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10143 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10143 | 0 | 1 | deoTUNQEC01NS01PFAPLA-02CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1633 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 8 | 2 | deiTUNQEC01NS01PFAPLA-02AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1634 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10144 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10144 | 0 | 1 | deoTUNQEC01NS01PFAPLA-02CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
1635 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 10 | 2 | deiTUNQEC01NS01PFAPLA-02AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
1636 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10145 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10145 | 0 | 1 | deoTUNQEC01NS01PFAPLA-02CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
1637 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 12 | 2 | deiTUNQEC01NS01PFAPLA-02AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
1638 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10146 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10146 | 0 | 1 | deoTUNQEC01NS01PFAPLA-02CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1639 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 14 | 2 | deiTUNQEC01NS01PFAPLA-02AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1640 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10147 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10147 | 0 | 1 | deoTUNQEC01NS01PFAPLA-02CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1641 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20072 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20072 | 0 | 2 | deiTUNQEC01NS01PFAPLA-02AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1642 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20072 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20072 | 2 | 1 | deiTUNQEC01NS01PFAPLA-02StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
1643 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20072 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20072 | 4 | 1 | deiTUNQEC01NS01PFAPLA-02StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
1644 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20081 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20081 | 0 | 1 | deiTUNQEC01NS01PFACON-04ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1645 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20081 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20081 | 2 | 1 | deiTUNQEC01NS01PFACON-04OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1646 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20081 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20081 | 4 | 1 | deiTUNQEC01NS01PFACON-04AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
1647 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10161 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10161 | 0 | 1 | deoTUNQEC01NS01PFACON-04CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1648 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10162 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10162 | 0 | 1 | deoTUNQEC01NS01PFACON-04CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1649 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 6 | 2 | deiTUNQEC01NS01PFACON-04AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1650 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10163 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10163 | 0 | 1 | deoTUNQEC01NS01PFACON-04CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1651 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 8 | 2 | deiTUNQEC01NS01PFACON-04AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1652 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10164 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10164 | 0 | 1 | deoTUNQEC01NS01PFACON-04CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
1653 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 10 | 2 | deiTUNQEC01NS01PFACON-04AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
1654 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10165 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10165 | 0 | 1 | deoTUNQEC01NS01PFACON-04CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
1655 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 12 | 2 | deiTUNQEC01NS01PFACON-04AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
1656 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10166 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10166 | 0 | 1 | deoTUNQEC01NS01PFACON-04CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1657 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 14 | 2 | deiTUNQEC01NS01PFACON-04AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1658 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10167 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10167 | 0 | 1 | deoTUNQEC01NS01PFACON-04CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1659 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20082 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20082 | 0 | 2 | deiTUNQEC01NS01PFACON-04AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1660 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20082 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20082 | 2 | 1 | deiTUNQEC01NS01PFACON-04StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
1661 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20082 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20082 | 4 | 1 | deiTUNQEC01NS01PFACON-04StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
1662 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20091 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20091 | 0 | 1 | deiTUNQEC01NS01PFACON-03ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1663 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20091 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20091 | 2 | 1 | deiTUNQEC01NS01PFACON-03OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1664 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20091 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20091 | 4 | 1 | deiTUNQEC01NS01PFACON-03AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
1665 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10181 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10181 | 0 | 1 | deoTUNQEC01NS01PFACON-03CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1666 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10182 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10182 | 0 | 1 | deoTUNQEC01NS01PFACON-03CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1667 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 6 | 2 | deiTUNQEC01NS01PFACON-03AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1668 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10183 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10183 | 0 | 1 | deoTUNQEC01NS01PFACON-03CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1669 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 8 | 2 | deiTUNQEC01NS01PFACON-03AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1670 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10184 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10184 | 0 | 1 | deoTUNQEC01NS01PFACON-03CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
1671 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 10 | 2 | deiTUNQEC01NS01PFACON-03AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
1672 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10185 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10185 | 0 | 1 | deoTUNQEC01NS01PFACON-03CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
1673 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 12 | 2 | deiTUNQEC01NS01PFACON-03AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
1674 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10186 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10186 | 0 | 1 | deoTUNQEC01NS01PFACON-03CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1675 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 14 | 2 | deiTUNQEC01NS01PFACON-03AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1676 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10187 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10187 | 0 | 1 | deoTUNQEC01NS01PFACON-03CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1677 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20092 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20092 | 0 | 2 | deiTUNQEC01NS01PFACON-03AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1678 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20092 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20092 | 2 | 1 | deiTUNQEC01NS01PFACON-03StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
1679 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20092 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20092 | 4 | 1 | deiTUNQEC01NS01PFACON-03StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
1680 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20101 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20101 | 0 | 1 | deiTUNQEC01NS01PFAGRD-03ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1681 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20101 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20101 | 2 | 1 | deiTUNQEC01NS01PFAGRD-03OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1682 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20101 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20101 | 4 | 1 | deiTUNQEC01NS01PFAGRD-03AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
1683 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | CmdMan | SIL0 | MODBUS:16:Write:Holding Registers | 10201 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10201 | 0 | 1 | deoTUNQEC01NS01PFAGRD-03CmdMan | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1684 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10202 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10202 | 0 | 1 | deoTUNQEC01NS01PFAGRD-03CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1685 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 6 | 2 | deiTUNQEC01NS01PFAGRD-03AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1686 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10203 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10203 | 0 | 1 | deoTUNQEC01NS01PFAGRD-03CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1687 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 8 | 2 | deiTUNQEC01NS01PFAGRD-03AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1688 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10204 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10204 | 0 | 1 | deoTUNQEC01NS01PFAGRD-03CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
1689 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 10 | 2 | deiTUNQEC01NS01PFAGRD-03AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
1690 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10205 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10205 | 0 | 1 | deoTUNQEC01NS01PFAGRD-03CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
1691 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 12 | 2 | deiTUNQEC01NS01PFAGRD-03AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
1692 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10206 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10206 | 0 | 1 | deoTUNQEC01NS01PFAGRD-03CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1693 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 14 | 2 | deiTUNQEC01NS01PFAGRD-03AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1694 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10207 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10207 | 0 | 1 | deoTUNQEC01NS01PFAGRD-03CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1695 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20102 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20102 | 0 | 2 | deiTUNQEC01NS01PFAGRD-03AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1696 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20102 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20102 | 2 | 1 | deiTUNQEC01NS01PFAGRD-03StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
1697 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20102 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20102 | 4 | 1 | deiTUNQEC01NS01PFAGRD-03StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
1698 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC01 | 11 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20111 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20111 | 0 | 1 | deiTUNQEC01SMCSMC01State | 4 |  |  | 0 | $ComStatus , , | #STATE
1699 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC02 | 12 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20121 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20121 | 0 | 1 | deiTUNQEC01SMCSMC02State | 4 |  |  | 0 | $ComStatus , , | #STATE
1700 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC03 | 13 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20131 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20131 | 0 | 1 | deiTUNQEC01SMCSMC03State | 4 |  |  | 0 | $ComStatus , , | #STATE
1701 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC04 | 14 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20141 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20141 | 0 | 1 | deiTUNQEC01SMCSMC04State | 4 |  |  | 0 | $ComStatus , , | #STATE
1702 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC05 | 15 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20151 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20151 | 0 | 1 | deiTUNQEC01SMCSMC05State | 4 |  |  | 0 | $ComStatus , , | #STATE
1703 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC06 | 16 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20161 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20161 | 0 | 1 | deiTUNQEC01SMCSMC06State | 4 |  |  | 0 | $ComStatus , , | #STATE
1704 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC07 | 17 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20171 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20171 | 0 | 1 | deiTUNQEC01SMCSMC07State | 4 |  |  | 0 | $ComStatus , , | #STATE
1705 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC08 | 18 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20181 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20181 | 0 | 1 | deiTUNQEC01SMCSMC08State | 4 |  |  | 0 | $ComStatus , , | #STATE
1706 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC09 | 19 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20191 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20191 | 0 | 1 | deiTUNQEC01SMCSMC09State | 4 |  |  | 0 | $ComStatus , , | #STATE
1707 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC10 | 20 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20201 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20201 | 0 | 1 | deiTUNQEC01SMCSMC10State | 4 |  |  | 0 | $ComStatus , , | #STATE
1708 | QEC01_RTU | TUN:QEC01 | SED | SED | SED01 | 21 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20211 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20211 | 0 | 1 | deiTUNQEC01SEDSED01State | 4 |  |  | 0 | $ComStatus , , | #STATE
1709 | QEC01_RTU | TUN:QEC01 | SED | SED | SED01 | 21 | Open | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20211 | 1 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20211 | 1 | 1 | deiTUNQEC01SEDSED01Open | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
1710 | QEC01_RTU | TUN:QEC01 | SED | SED | SED02 | 22 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20221 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20221 | 0 | 1 | deiTUNQEC01SEDSED02State | 4 |  |  | 0 | $ComStatus , , | #STATE
1711 | QEC01_RTU | TUN:QEC01 | SED | SED | SED02 | 22 | Open | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20221 | 1 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20221 | 1 | 1 | deiTUNQEC01SEDSED02Open | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
1712 | QEC01_RTU | TUN:QEC01 | SED | SED | SED03 | 23 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20231 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20231 | 0 | 1 | deiTUNQEC01SEDSED03State | 4 |  |  | 0 | $ComStatus , , | #STATE
1713 | QEC01_RTU | TUN:QEC01 | SED | SED | SED03 | 23 | Open | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20231 | 1 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20231 | 1 | 1 | deiTUNQEC01SEDSED03Open | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
1714 | QEC01_RTU | TUN:QEC01 | SED | SED | SED04 | 24 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20241 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20241 | 0 | 1 | deiTUNQEC01SEDSED04State | 4 |  |  | 0 | $ComStatus , , | #STATE
1715 | QEC01_RTU | TUN:QEC01 | SED | SED | SED04 | 24 | Open | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20241 | 1 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20241 | 1 | 1 | deiTUNQEC01SEDSED04Open | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
1716 | QEC01_RTU | TUN:QEC01 | OTS | OTS | OTS001 | 25 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20251 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20251 | 0 | 1 | deiTUNQEC01OTSOTS001AvailStat | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1717 | QEC01_RTU | TUN:QEC01 | OTS | OTS | OTS001 | 25 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20251 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20251 | 2 | 1 | deiTUNQEC01OTSOTS001AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1718 | QEC01_RTU | TUN:QEC01 | OTS | OTS | OTS001 | 25 | TemMeasure | SIL0 | MODBUS:4:Read:Input Registers | 20252 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20252 | 0 | 32 | aeiTUNQEC01OTSOTS001TemMeasure | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1719 | QEC01_RTU | TUN:QEC01 | OTS | OTS | OTS002 | 26 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20261 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20261 | 0 | 1 | deiTUNQEC01OTSOTS002AvailStat | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1720 | QEC01_RTU | TUN:QEC01 | OTS | OTS | OTS002 | 26 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20261 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20261 | 2 | 1 | deiTUNQEC01OTSOTS002AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1721 | QEC01_RTU | TUN:QEC01 | OTS | OTS | OTS002 | 26 | TemMeasure | SIL0 | MODBUS:4:Read:Input Registers | 20262 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20262 | 0 | 32 | aeiTUNQEC01OTSOTS002TemMeasure | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1722 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20271 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20271 | 0 | 2 | deiTUNQEC01SS01TVFVT1-TVF01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1723 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20271 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20271 | 2 | 1 | deiTUNQEC01SS01TVFVT1-TVF01OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1724 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20271 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20271 | 4 | 2 | deiTUNQEC01SS01TVFVT1-TVF01RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
1725 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10541 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10541 | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1726 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10542 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10542 | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1727 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20271 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20271 | 6 | 2 | deiTUNQEC01SS01TVFVT1-TVF01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1728 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10543 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10543 | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1729 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20271 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20271 | 8 | 2 | deiTUNQEC01SS01TVFVT1-TVF01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1730 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20271 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20271 | 10 | 1 | deiTUNQEC01SS01TVFVT1-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
1731 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20271 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20271 | 12 | 1 | deiTUNQEC01SS01TVFVT1-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
1732 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20271 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20271 | 14 | 1 | deiTUNQEC01SS01TVFVT1-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
1733 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20272 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20272 | 0 | 32 | aeiTUNQEC01SS01TVFVT1-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
1734 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10544 | 0 | 2 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10544 | 0 | 2 | deoTUNQEC01SS01TVFVT1-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
1735 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10545 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10545 | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1736 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 0 | 2 | deiTUNQEC01SS01TVFVT1-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1737 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10546 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10546 | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1738 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 2 | 2 | deiTUNQEC01SS01TVFVT1-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1739 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10547 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10547 | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
1740 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 4 | 2 | deiTUNQEC01SS01TVFVT1-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
1741 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10548 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10548 | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
1742 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 6 | 2 | deiTUNQEC01SS01TVFVT1-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
1743 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10549 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10549 | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
1744 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 8 | 2 | deiTUNQEC01SS01TVFVT1-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
1745 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10550 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10550 | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
1746 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 10 | 2 | deiTUNQEC01SS01TVFVT1-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
1747 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20274 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20274 | 12 | 1 | deiTUNQEC01SS01TVFVT1-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
1748 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20274 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20274 | 14 | 1 | deiTUNQEC01SS01TVFVT1-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
1749 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
1750 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 1 | 1 | deiTUNQEC01SS01TVFVT1-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
1751 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 2 | 1 | deiTUNQEC01SS01TVFVT1-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
1752 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 3 | 1 | deiTUNQEC01SS01TVFVT1-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
1753 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 4 | 1 | deiTUNQEC01SS01TVFVT1-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
1754 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 5 | 1 | deiTUNQEC01SS01TVFVT1-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
1755 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 6 | 1 | deiTUNQEC01SS01TVFVT1-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
1756 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 7 | 1 | deiTUNQEC01SS01TVFVT1-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
1757 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 8 | 1 | deiTUNQEC01SS01TVFVT1-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
1758 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 9 | 1 | deiTUNQEC01SS01TVFVT1-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
1759 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 10 | 1 | deiTUNQEC01SS01TVFVT1-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
1760 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 11 | 1 | deiTUNQEC01SS01TVFVT1-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
1761 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20276 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20276 | 0 | 16 | aeiTUNQEC01SS01TVFVT1-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
1762 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20281 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20281 | 0 | 2 | deiTUNQEC01SS01TVFVT2-TVF01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1763 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20281 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20281 | 2 | 1 | deiTUNQEC01SS01TVFVT2-TVF01OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1764 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20281 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20281 | 4 | 2 | deiTUNQEC01SS01TVFVT2-TVF01RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
1765 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10561 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10561 | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1766 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10562 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10562 | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1767 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20281 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20281 | 6 | 2 | deiTUNQEC01SS01TVFVT2-TVF01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1768 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10563 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10563 | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1769 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20281 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20281 | 8 | 2 | deiTUNQEC01SS01TVFVT2-TVF01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1770 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20281 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20281 | 10 | 1 | deiTUNQEC01SS01TVFVT2-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
1771 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20281 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20281 | 12 | 1 | deiTUNQEC01SS01TVFVT2-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
1772 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20281 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20281 | 14 | 1 | deiTUNQEC01SS01TVFVT2-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
1773 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20282 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20282 | 0 | 32 | aeiTUNQEC01SS01TVFVT2-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
1774 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10564 | 0 | 2 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10564 | 0 | 2 | deoTUNQEC01SS01TVFVT2-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
1775 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10565 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10565 | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1776 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 0 | 2 | deiTUNQEC01SS01TVFVT2-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1777 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10566 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10566 | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1778 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 2 | 2 | deiTUNQEC01SS01TVFVT2-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1779 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10567 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10567 | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
1780 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 4 | 2 | deiTUNQEC01SS01TVFVT2-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
1781 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10568 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10568 | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
1782 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 6 | 2 | deiTUNQEC01SS01TVFVT2-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
1783 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10569 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10569 | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
1784 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 8 | 2 | deiTUNQEC01SS01TVFVT2-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
1785 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10570 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10570 | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
1786 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 10 | 2 | deiTUNQEC01SS01TVFVT2-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
1787 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20284 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20284 | 12 | 1 | deiTUNQEC01SS01TVFVT2-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
1788 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20284 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20284 | 14 | 1 | deiTUNQEC01SS01TVFVT2-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
1789 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
1790 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 1 | 1 | deiTUNQEC01SS01TVFVT2-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
1791 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 2 | 1 | deiTUNQEC01SS01TVFVT2-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
1792 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 3 | 1 | deiTUNQEC01SS01TVFVT2-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
1793 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 4 | 1 | deiTUNQEC01SS01TVFVT2-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
1794 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 5 | 1 | deiTUNQEC01SS01TVFVT2-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
1795 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 6 | 1 | deiTUNQEC01SS01TVFVT2-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
1796 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 7 | 1 | deiTUNQEC01SS01TVFVT2-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
1797 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 8 | 1 | deiTUNQEC01SS01TVFVT2-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
1798 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 9 | 1 | deiTUNQEC01SS01TVFVT2-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
1799 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 10 | 1 | deiTUNQEC01SS01TVFVT2-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
1800 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 11 | 1 | deiTUNQEC01SS01TVFVT2-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
1801 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20286 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20286 | 0 | 16 | aeiTUNQEC01SS01TVFVT2-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
1802 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20291 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20291 | 0 | 2 | deiTUNQEC01NS01TVFVT3-TVF01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1803 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20291 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20291 | 2 | 1 | deiTUNQEC01NS01TVFVT3-TVF01OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1804 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20291 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20291 | 4 | 2 | deiTUNQEC01NS01TVFVT3-TVF01RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
1805 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10581 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10581 | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1806 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10582 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10582 | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1807 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20291 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20291 | 6 | 2 | deiTUNQEC01NS01TVFVT3-TVF01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1808 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10583 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10583 | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1809 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20291 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20291 | 8 | 2 | deiTUNQEC01NS01TVFVT3-TVF01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1810 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20291 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20291 | 10 | 1 | deiTUNQEC01NS01TVFVT3-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
1811 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20291 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20291 | 12 | 1 | deiTUNQEC01NS01TVFVT3-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
1812 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20291 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20291 | 14 | 1 | deiTUNQEC01NS01TVFVT3-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
1813 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20292 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20292 | 0 | 32 | aeiTUNQEC01NS01TVFVT3-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
1814 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10584 | 0 | 2 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10584 | 0 | 2 | deoTUNQEC01NS01TVFVT3-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
1815 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10585 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10585 | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1816 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 0 | 2 | deiTUNQEC01NS01TVFVT3-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1817 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10586 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10586 | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1818 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 2 | 2 | deiTUNQEC01NS01TVFVT3-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1819 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10587 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10587 | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
1820 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 4 | 2 | deiTUNQEC01NS01TVFVT3-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
1821 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10588 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10588 | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
1822 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 6 | 2 | deiTUNQEC01NS01TVFVT3-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
1823 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10589 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10589 | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
1824 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 8 | 2 | deiTUNQEC01NS01TVFVT3-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
1825 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10590 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10590 | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
1826 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 10 | 2 | deiTUNQEC01NS01TVFVT3-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
1827 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20294 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20294 | 12 | 1 | deiTUNQEC01NS01TVFVT3-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
1828 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20294 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20294 | 14 | 1 | deiTUNQEC01NS01TVFVT3-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
1829 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
1830 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 1 | 1 | deiTUNQEC01NS01TVFVT3-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
1831 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 2 | 1 | deiTUNQEC01NS01TVFVT3-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
1832 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 3 | 1 | deiTUNQEC01NS01TVFVT3-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
1833 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 4 | 1 | deiTUNQEC01NS01TVFVT3-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
1834 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 5 | 1 | deiTUNQEC01NS01TVFVT3-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
1835 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 6 | 1 | deiTUNQEC01NS01TVFVT3-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
1836 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 7 | 1 | deiTUNQEC01NS01TVFVT3-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
1837 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 8 | 1 | deiTUNQEC01NS01TVFVT3-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
1838 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 9 | 1 | deiTUNQEC01NS01TVFVT3-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
1839 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 10 | 1 | deiTUNQEC01NS01TVFVT3-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
1840 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 11 | 1 | deiTUNQEC01NS01TVFVT3-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
1841 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20296 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20296 | 0 | 16 | aeiTUNQEC01NS01TVFVT3-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
1842 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20301 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20301 | 0 | 2 | deiTUNQEC01NS01TVFVT4-TVF01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1843 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20301 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20301 | 2 | 1 | deiTUNQEC01NS01TVFVT4-TVF01OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1844 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20301 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20301 | 4 | 2 | deiTUNQEC01NS01TVFVT4-TVF01RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
1845 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10601 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10601 | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1846 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10602 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10602 | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1847 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20301 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20301 | 6 | 2 | deiTUNQEC01NS01TVFVT4-TVF01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1848 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10603 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10603 | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1849 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20301 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20301 | 8 | 2 | deiTUNQEC01NS01TVFVT4-TVF01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1850 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20301 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20301 | 10 | 1 | deiTUNQEC01NS01TVFVT4-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
1851 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20301 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20301 | 12 | 1 | deiTUNQEC01NS01TVFVT4-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
1852 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20301 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20301 | 14 | 1 | deiTUNQEC01NS01TVFVT4-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
1853 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20302 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20302 | 0 | 32 | aeiTUNQEC01NS01TVFVT4-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
1854 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10604 | 0 | 2 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10604 | 0 | 2 | deoTUNQEC01NS01TVFVT4-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
1855 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10605 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10605 | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
1856 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 0 | 2 | deiTUNQEC01NS01TVFVT4-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
1857 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10606 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10606 | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
1858 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 2 | 2 | deiTUNQEC01NS01TVFVT4-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
1859 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10607 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10607 | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
1860 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 4 | 2 | deiTUNQEC01NS01TVFVT4-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
1861 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10608 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10608 | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
1862 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 6 | 2 | deiTUNQEC01NS01TVFVT4-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
1863 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10609 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10609 | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
1864 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 8 | 2 | deiTUNQEC01NS01TVFVT4-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
1865 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10610 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10610 | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
1866 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 10 | 2 | deiTUNQEC01NS01TVFVT4-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
1867 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20304 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20304 | 12 | 1 | deiTUNQEC01NS01TVFVT4-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
1868 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20304 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20304 | 14 | 1 | deiTUNQEC01NS01TVFVT4-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
1869 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
1870 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 1 | 1 | deiTUNQEC01NS01TVFVT4-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
1871 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 2 | 1 | deiTUNQEC01NS01TVFVT4-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
1872 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 3 | 1 | deiTUNQEC01NS01TVFVT4-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
1873 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 4 | 1 | deiTUNQEC01NS01TVFVT4-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
1874 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 5 | 1 | deiTUNQEC01NS01TVFVT4-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
1875 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 6 | 1 | deiTUNQEC01NS01TVFVT4-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
1876 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 7 | 1 | deiTUNQEC01NS01TVFVT4-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
1877 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 8 | 1 | deiTUNQEC01NS01TVFVT4-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
1878 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 9 | 1 | deiTUNQEC01NS01TVFVT4-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
1879 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 10 | 1 | deiTUNQEC01NS01TVFVT4-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
1880 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 11 | 1 | deiTUNQEC01NS01TVFVT4-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
1881 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20306 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20306 | 0 | 16 | aeiTUNQEC01NS01TVFVT4-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
1882 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | 31 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 0 | 1 | deiTUNQEC01SS01SENSORTS101871Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1883 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | 31 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 1 | 1 | deiTUNQEC01SS01SENSORTS101871TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1884 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | 31 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 2 | 1 | deiTUNQEC01SS01SENSORTS101871HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1885 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | 31 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 3 | 1 | deiTUNQEC01SS01SENSORTS101871AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1886 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | 31 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20312 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20312 | 0 | 32 | aeiTUNQEC01SS01SENSORTS101871Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1887 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | 31 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20314 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20314 | 0 | 32 | aeiTUNQEC01SS01SENSORTS101871Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1888 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | 32 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 0 | 1 | deiTUNQEC01SS01SENSORTS101984Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1889 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | 32 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 1 | 1 | deiTUNQEC01SS01SENSORTS101984TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1890 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | 32 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 2 | 1 | deiTUNQEC01SS01SENSORTS101984HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1891 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | 32 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 3 | 1 | deiTUNQEC01SS01SENSORTS101984AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1892 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | 32 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20322 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20322 | 0 | 32 | aeiTUNQEC01SS01SENSORTS101984Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1893 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | 32 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20324 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20324 | 0 | 32 | aeiTUNQEC01SS01SENSORTS101984Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1894 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | 33 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 0 | 1 | deiTUNQEC01NS01SENSORTS102441Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1895 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | 33 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 1 | 1 | deiTUNQEC01NS01SENSORTS102441TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1896 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | 33 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 2 | 1 | deiTUNQEC01NS01SENSORTS102441HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1897 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | 33 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 3 | 1 | deiTUNQEC01NS01SENSORTS102441AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1898 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | 33 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20332 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20332 | 0 | 32 | aeiTUNQEC01NS01SENSORTS102441Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1899 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | 33 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20334 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20334 | 0 | 32 | aeiTUNQEC01NS01SENSORTS102441Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1900 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | 34 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 0 | 1 | deiTUNQEC01NS01SENSORTS102499Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1901 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | 34 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 1 | 1 | deiTUNQEC01NS01SENSORTS102499TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1902 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | 34 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 2 | 1 | deiTUNQEC01NS01SENSORTS102499HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1903 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | 34 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 3 | 1 | deiTUNQEC01NS01SENSORTS102499AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1904 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | 34 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20342 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20342 | 0 | 32 | aeiTUNQEC01NS01SENSORTS102499Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1905 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | 34 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20344 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20344 | 0 | 32 | aeiTUNQEC01NS01SENSORTS102499Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1906 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | 35 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20351 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20351 | 0 | 1 | deiTUNQEC01NS01SENSORTS102261Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1907 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | 35 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20351 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20351 | 1 | 1 | deiTUNQEC01NS01SENSORTS102261TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1908 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | 35 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20351 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20351 | 2 | 1 | deiTUNQEC01NS01SENSORTS102261HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1909 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | 35 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20351 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20351 | 3 | 1 | deiTUNQEC01NS01SENSORTS102261AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1910 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | 35 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20352 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20352 | 0 | 32 | aeiTUNQEC01NS01SENSORTS102261Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1911 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | 35 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20354 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20354 | 0 | 32 | aeiTUNQEC01NS01SENSORTS102261Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1912 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | 36 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20361 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20361 | 0 | 1 | deiTUNQEC01NS01SENSORTS100023Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1913 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | 36 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20361 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20361 | 1 | 1 | deiTUNQEC01NS01SENSORTS100023TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1914 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | 36 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20361 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20361 | 2 | 1 | deiTUNQEC01NS01SENSORTS100023HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1915 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | 36 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20361 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20361 | 3 | 1 | deiTUNQEC01NS01SENSORTS100023AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1916 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | 36 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20362 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20362 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100023Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1917 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | 36 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20364 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20364 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100023Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1918 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | 37 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20371 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20371 | 0 | 1 | deiTUNQEC01NS01SENSORTS100062Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1919 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | 37 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20371 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20371 | 1 | 1 | deiTUNQEC01NS01SENSORTS100062TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1920 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | 37 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20371 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20371 | 2 | 1 | deiTUNQEC01NS01SENSORTS100062HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1921 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | 37 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20371 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20371 | 3 | 1 | deiTUNQEC01NS01SENSORTS100062AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1922 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | 37 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20372 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20372 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100062Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1923 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | 37 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20374 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20374 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100062Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1924 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | 38 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20381 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20381 | 0 | 1 | deiTUNQEC01NS01SENSORTS100108Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1925 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | 38 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20381 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20381 | 1 | 1 | deiTUNQEC01NS01SENSORTS100108TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1926 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | 38 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20381 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20381 | 2 | 1 | deiTUNQEC01NS01SENSORTS100108HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1927 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | 38 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20381 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20381 | 3 | 1 | deiTUNQEC01NS01SENSORTS100108AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1928 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | 38 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20382 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20382 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100108Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1929 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | 38 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20384 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20384 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100108Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1930 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | 39 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 0 | 1 | deiTUNQEC01NS01SENSORTS100230Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1931 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | 39 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 1 | 1 | deiTUNQEC01NS01SENSORTS100230TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1932 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | 39 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 2 | 1 | deiTUNQEC01NS01SENSORTS100230HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1933 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | 39 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 3 | 1 | deiTUNQEC01NS01SENSORTS100230AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1934 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | 39 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20392 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20392 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100230Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1935 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | 39 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20394 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20394 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100230Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1936 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | 40 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 0 | 1 | deiTUNQEC01NS01SENSORTS100335Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1937 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | 40 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 1 | 1 | deiTUNQEC01NS01SENSORTS100335TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
1938 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | 40 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 2 | 1 | deiTUNQEC01NS01SENSORTS100335HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
1939 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | 40 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 3 | 1 | deiTUNQEC01NS01SENSORTS100335AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
1940 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | 40 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20402 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20402 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100335Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
1941 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | 40 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20404 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20404 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100335Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
1942 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | VS | VS101909 | 41 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20411 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20411 | 0 | 1 | deiTUNQEC01SS01SENSORVS101909Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1943 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | VS | VS101909 | 41 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20412 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20412 | 0 | 32 | aeiTUNQEC01SS01SENSORVS101909Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
1944 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS102357 | 42 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20421 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20421 | 0 | 1 | deiTUNQEC01NS01SENSORVS102357Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1945 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS102357 | 42 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20422 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20422 | 0 | 32 | aeiTUNQEC01NS01SENSORVS102357Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
1946 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS102467 | 43 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20431 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20431 | 0 | 1 | deiTUNQEC01NS01SENSORVS102467Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1947 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS102467 | 43 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20432 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20432 | 0 | 32 | aeiTUNQEC01NS01SENSORVS102467Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
1948 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS102276 | 44 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20441 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20441 | 0 | 1 | deiTUNQEC01NS01SENSORVS102276Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1949 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS102276 | 44 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20442 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20442 | 0 | 32 | aeiTUNQEC01NS01SENSORVS102276Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
1950 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS100080 | 45 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20451 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20451 | 0 | 1 | deiTUNQEC01NS01SENSORVS100080Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1951 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS100080 | 45 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20452 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20452 | 0 | 32 | aeiTUNQEC01NS01SENSORVS100080Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
1952 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS100285 | 46 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20461 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20461 | 0 | 1 | deiTUNQEC01NS01SENSORVS100285Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
1953 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS100285 | 46 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20462 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20462 | 0 | 32 | aeiTUNQEC01NS01SENSORVS100285Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
1954 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20471 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20471 | 0 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1955 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20471 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20471 | 2 | 1 | deiTUNQEC01SS01DAMPERVT5-TDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1956 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20471 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20471 | 4 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1957 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10941 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10941 | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1958 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10942 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10942 | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1959 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20471 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20471 | 6 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1960 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10943 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10943 | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1961 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20471 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20471 | 8 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1962 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10944 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10944 | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
1963 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20471 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20471 | 10 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
1964 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10945 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10945 | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
1965 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20471 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20471 | 12 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
1966 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10946 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10946 | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
1967 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20471 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20471 | 14 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
1968 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10947 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10947 | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
1969 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20472 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20472 | 0 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
1970 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20472 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20472 | 2 | 1 | deiTUNQEC01SS01DAMPERVT5-TDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
1971 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20472 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20472 | 4 | 1 | deiTUNQEC01SS01DAMPERVT5-TDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
1972 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20472 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20472 | 6 | 1 | deiTUNQEC01SS01DAMPERVT5-TDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1973 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20472 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20472 | 8 | 1 | deiTUNQEC01SS01DAMPERVT5-TDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1974 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20481 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20481 | 0 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1975 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20481 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20481 | 2 | 1 | deiTUNQEC01NS01DAMPERVT6-TDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
1976 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20481 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20481 | 4 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1977 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 10961 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10961 | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
1978 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10962 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10962 | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
1979 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20481 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20481 | 6 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
1980 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 10963 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10963 | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
1981 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20481 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20481 | 8 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
1982 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10964 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10964 | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
1983 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20481 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20481 | 10 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
1984 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10965 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10965 | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
1985 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20481 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20481 | 12 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
1986 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10966 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10966 | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
1987 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20481 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20481 | 14 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
1988 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10967 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10967 | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
1989 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20482 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20482 | 0 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
1990 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20482 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20482 | 2 | 1 | deiTUNQEC01NS01DAMPERVT6-TDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
1991 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20482 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20482 | 4 | 1 | deiTUNQEC01NS01DAMPERVT6-TDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
1992 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20482 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20482 | 6 | 1 | deiTUNQEC01NS01DAMPERVT6-TDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1993 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20482 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20482 | 8 | 1 | deiTUNQEC01NS01DAMPERVT6-TDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
1994 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | 49 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20491 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20491 | 0 | 2 | deiTUNQEC01SS01DAMPERVT1-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
1995 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | 49 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20491 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20491 | 2 | 2 | deiTUNQEC01SS01DAMPERVT1-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
1996 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | 49 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20491 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20491 | 4 | 1 | deiTUNQEC01SS01DAMPERVT1-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
1997 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | 49 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20491 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20491 | 6 | 1 | deiTUNQEC01SS01DAMPERVT1-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
1998 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | 49 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20491 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20491 | 8 | 1 | deiTUNQEC01SS01DAMPERVT1-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
1999 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | 49 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20491 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20491 | 10 | 1 | deiTUNQEC01SS01DAMPERVT1-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2000 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | 50 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20501 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20501 | 0 | 2 | deiTUNQEC01SS01DAMPERVT2-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2001 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | 50 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20501 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20501 | 2 | 2 | deiTUNQEC01SS01DAMPERVT2-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2002 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | 50 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20501 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20501 | 4 | 1 | deiTUNQEC01SS01DAMPERVT2-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
2003 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | 50 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20501 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20501 | 6 | 1 | deiTUNQEC01SS01DAMPERVT2-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
2004 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | 50 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20501 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20501 | 8 | 1 | deiTUNQEC01SS01DAMPERVT2-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2005 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | 50 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20501 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20501 | 10 | 1 | deiTUNQEC01SS01DAMPERVT2-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2006 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | 51 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20511 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20511 | 0 | 2 | deiTUNQEC01NS01DAMPERVT3-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2007 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | 51 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20511 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20511 | 2 | 2 | deiTUNQEC01NS01DAMPERVT3-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2008 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | 51 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20511 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20511 | 4 | 1 | deiTUNQEC01NS01DAMPERVT3-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
2009 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | 51 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20511 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20511 | 6 | 1 | deiTUNQEC01NS01DAMPERVT3-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
2010 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | 51 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20511 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20511 | 8 | 1 | deiTUNQEC01NS01DAMPERVT3-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2011 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | 51 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20511 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20511 | 10 | 1 | deiTUNQEC01NS01DAMPERVT3-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2012 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | 52 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20521 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20521 | 0 | 2 | deiTUNQEC01NS01DAMPERVT4-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2013 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | 52 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20521 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20521 | 2 | 2 | deiTUNQEC01NS01DAMPERVT4-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2014 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | 52 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20521 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20521 | 4 | 1 | deiTUNQEC01NS01DAMPERVT4-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
2015 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | 52 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20521 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20521 | 6 | 1 | deiTUNQEC01NS01DAMPERVT4-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
2016 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | 52 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20521 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20521 | 8 | 1 | deiTUNQEC01NS01DAMPERVT4-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2017 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | 52 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20521 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20521 | 10 | 1 | deiTUNQEC01NS01DAMPERVT4-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2018 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20531 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20531 | 0 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2019 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20531 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20531 | 2 | 1 | deiTUNQEC01SS01DAMPERFR1-BDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2020 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20531 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20531 | 4 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2021 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 11061 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11061 | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2022 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 11062 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11062 | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2023 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20531 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20531 | 6 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2024 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 11063 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11063 | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2025 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20531 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20531 | 8 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2026 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 11064 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11064 | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
2027 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20531 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20531 | 10 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
2028 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 11065 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11065 | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
2029 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20531 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20531 | 12 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
2030 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 11066 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11066 | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
2031 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20531 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20531 | 14 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
2032 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 11067 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11067 | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
2033 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20532 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20532 | 0 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
2034 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20532 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20532 | 2 | 1 | deiTUNQEC01SS01DAMPERFR1-BDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
2035 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20532 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20532 | 4 | 1 | deiTUNQEC01SS01DAMPERFR1-BDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
2036 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20532 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20532 | 6 | 1 | deiTUNQEC01SS01DAMPERFR1-BDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2037 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20532 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20532 | 8 | 1 | deiTUNQEC01SS01DAMPERFR1-BDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2038 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20541 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20541 | 0 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2039 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20541 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20541 | 2 | 1 | deiTUNQEC01NS01DAMPERFR2-BDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2040 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20541 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20541 | 4 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2041 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | CmdAuto | SIL0 | MODBUS:16:Write:Holding Registers | 11081 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11081 | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01CmdAuto | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2042 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 11082 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11082 | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2043 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20541 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20541 | 6 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2044 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 11083 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11083 | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2045 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20541 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20541 | 8 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2046 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 11084 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11084 | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
2047 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20541 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20541 | 10 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
2048 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 11085 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11085 | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
2049 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20541 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20541 | 12 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
2050 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 11086 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11086 | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
2051 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20541 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20541 | 14 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
2052 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 11087 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11087 | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
2053 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20542 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20542 | 0 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
2054 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20542 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20542 | 2 | 1 | deiTUNQEC01NS01DAMPERFR2-BDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
2055 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20542 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20542 | 4 | 1 | deiTUNQEC01NS01DAMPERFR2-BDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
2056 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20542 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20542 | 6 | 1 | deiTUNQEC01NS01DAMPERFR2-BDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2057 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20542 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20542 | 8 | 1 | deiTUNQEC01NS01DAMPERFR2-BDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2058 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-95 | 55 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20551 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20551 | 0 | 2 | deiTUNQEC01SS01DAMPERCON-95Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2059 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-95 | 55 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20551 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20551 | 2 | 1 | deiTUNQEC01SS01DAMPERCON-95CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2060 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-95 | 55 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20551 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20551 | 4 | 1 | deiTUNQEC01SS01DAMPERCON-95TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2061 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-95 | 55 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20551 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20551 | 6 | 1 | deiTUNQEC01SS01DAMPERCON-95LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2062 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-94 | 56 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20561 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20561 | 0 | 2 | deiTUNQEC01NS01DAMPERCON-94Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2063 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-94 | 56 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20561 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20561 | 2 | 1 | deiTUNQEC01NS01DAMPERCON-94CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2064 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-94 | 56 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20561 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20561 | 4 | 1 | deiTUNQEC01NS01DAMPERCON-94TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2065 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-94 | 56 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20561 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20561 | 6 | 1 | deiTUNQEC01NS01DAMPERCON-94LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2066 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-51 | 57 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20571 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20571 | 0 | 2 | deiTUNQEC01SS01DAMPERCON-51Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2067 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-51 | 57 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 2 | 1 | deiTUNQEC01SS01DAMPERCON-51CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2068 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-51 | 57 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 4 | 1 | deiTUNQEC01SS01DAMPERCON-51TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2069 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-51 | 57 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 6 | 1 | deiTUNQEC01SS01DAMPERCON-51LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2070 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-49 | 58 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20581 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20581 | 0 | 2 | deiTUNQEC01SS01DAMPERCON-49Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2071 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-49 | 58 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20581 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20581 | 2 | 1 | deiTUNQEC01SS01DAMPERCON-49CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2072 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-49 | 58 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20581 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20581 | 4 | 1 | deiTUNQEC01SS01DAMPERCON-49TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2073 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-49 | 58 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20581 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20581 | 6 | 1 | deiTUNQEC01SS01DAMPERCON-49LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2074 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-34 | 59 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20591 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20591 | 0 | 2 | deiTUNQEC01NS01DAMPERCON-34Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2075 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-34 | 59 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 2 | 1 | deiTUNQEC01NS01DAMPERCON-34CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2076 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-34 | 59 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 4 | 1 | deiTUNQEC01NS01DAMPERCON-34TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2077 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-34 | 59 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 6 | 1 | deiTUNQEC01NS01DAMPERCON-34LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2078 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-53 | 60 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20601 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20601 | 0 | 2 | deiTUNQEC01NS01DAMPERCON-53Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2079 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-53 | 60 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 2 | 1 | deiTUNQEC01NS01DAMPERCON-53CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2080 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-53 | 60 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 4 | 1 | deiTUNQEC01NS01DAMPERCON-53TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2081 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-53 | 60 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 6 | 1 | deiTUNQEC01NS01DAMPERCON-53LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2082 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-52 | 61 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20611 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20611 | 0 | 2 | deiTUNQEC01SS01DAMPERCON-52Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2083 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-52 | 61 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 2 | 1 | deiTUNQEC01SS01DAMPERCON-52CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2084 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-52 | 61 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 4 | 1 | deiTUNQEC01SS01DAMPERCON-52TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2085 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-52 | 61 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 6 | 1 | deiTUNQEC01SS01DAMPERCON-52LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2086 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-50 | 62 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20621 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20621 | 0 | 2 | deiTUNQEC01SS01DAMPERCON-50Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2087 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-50 | 62 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 2 | 1 | deiTUNQEC01SS01DAMPERCON-50CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2088 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-50 | 62 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 4 | 1 | deiTUNQEC01SS01DAMPERCON-50TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2089 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-50 | 62 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 6 | 1 | deiTUNQEC01SS01DAMPERCON-50LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2090 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-88 | 63 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20631 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20631 | 0 | 2 | deiTUNQEC01NS01DAMPERCON-88Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2091 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-88 | 63 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20631 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20631 | 2 | 1 | deiTUNQEC01NS01DAMPERCON-88CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2092 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-88 | 63 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20631 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20631 | 4 | 1 | deiTUNQEC01NS01DAMPERCON-88TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2093 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-88 | 63 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20631 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20631 | 6 | 1 | deiTUNQEC01NS01DAMPERCON-88LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2094 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-58 | 64 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20641 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20641 | 0 | 2 | deiTUNQEC01NS01DAMPERCON-58Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2095 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-58 | 64 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 2 | 1 | deiTUNQEC01NS01DAMPERCON-58CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2096 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-58 | 64 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 4 | 1 | deiTUNQEC01NS01DAMPERCON-58TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2097 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-58 | 64 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 6 | 1 | deiTUNQEC01NS01DAMPERCON-58LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2098 | QEC01_RTU | TUN:QEC01 | SS01:AHU | AHU | CON-02 | 65 | ControlMod | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 0 | 1 | deiTUNQEC01SS01AHUCON-02ControlMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2099 | QEC01_RTU | TUN:QEC01 | SS01:AHU | AHU | CON-02 | 65 | RunStat | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 1 | 1 | deiTUNQEC01SS01AHUCON-02RunStat | 4 |  |  | 0 | $ComStatus , , | #RUN
2100 | QEC01_RTU | TUN:QEC01 | NS01:AHU | AHU | PLA-02 | 66 | ControlMod | SIL0 | MODBUS:4:Read:Input Registers | 20661 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20661 | 0 | 1 | deiTUNQEC01NS01AHUPLA-02ControlMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2101 | QEC01_RTU | TUN:QEC01 | NS01:AHU | AHU | PLA-02 | 66 | RunStat | SIL0 | MODBUS:4:Read:Input Registers | 20661 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20661 | 1 | 1 | deiTUNQEC01NS01AHUPLA-02RunStat | 4 |  |  | 0 | $ComStatus , , | #RUN
2102 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 67 | PlcState | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 0 | 1 | deiTUNQEC01SCRJETPLC01PlcState | 4 |  |  | 0 | $ComStatus , , | #PLC A/B OFFLINE
2103 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 67 | OpStatus | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 1 | 1 | deiTUNQEC01SCRJETPLC01OpStatus | 4 |  |  | 0 | $ComStatus , , | #PLC RUNNING.
2104 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 67 | PwStat | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 2 | 1 | deiTUNQEC01SCRJETPLC01PwStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: POWER SUPPLY FAULT
2105 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 67 | CpuStat | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 3 | 1 | deiTUNQEC01SCRJETPLC01CpuStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CPU MODULE FAULT
2106 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 67 | CrpStat | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 4 | 1 | deiTUNQEC01SCRJETPLC01CrpStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CRP MODULE FAULT
2107 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 67 | CraStat | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 5 | 1 | deiTUNQEC01SCRJETPLC01CraStat | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
2108 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 67 | NrpStat | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 6 | 1 | deiTUNQEC01SCRJETPLC01NrpStat | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
2109 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 67 | ComStat | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 7 | 1 | deiTUNQEC01SCRJETPLC01ComStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
2110 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 67 | IoStat | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 8 | 1 | deiTUNQEC01SCRJETPLC01IoStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
2111 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20681 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20681 | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2112 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20681 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20681 | 2 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2113 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20681 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20681 | 4 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
2114 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 11361 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11361 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2115 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 11362 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11362 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2116 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20681 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20681 | 6 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2117 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 11363 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11363 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2118 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20681 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20681 | 8 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2119 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20681 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20681 | 10 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
2120 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | FailStart | SIL0 | MODBUS:4:Read:Input Registers | 20681 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20681 | 12 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132FailStart | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
2121 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | FailStop | SIL0 | MODBUS:4:Read:Input Registers | 20681 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20681 | 14 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132FailStop | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
2122 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | SpeedFrep | SIL0 | MODBUS:4:Read:Input Registers | 20682 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20682 | 0 | 32 | aeiTUNQEC01QEC1BJETQEC1B-JET100132SpeedFrep | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
2123 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 11364 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11364 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
2124 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11365 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11365 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2125 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20684 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20684 | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2126 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11366 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11366 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2127 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20684 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20684 | 2 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2128 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11367 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11367 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
2129 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20684 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20684 | 4 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
2130 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11368 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11368 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
2131 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20684 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20684 | 6 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
2132 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11369 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11369 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
2133 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20684 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20684 | 8 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
2134 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11370 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11370 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
2135 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20684 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20684 | 10 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
2136 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
2137 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CirOpen | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 1 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132CirOpen | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
2138 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CirOut | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 2 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132CirOut | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
2139 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | FanOpen | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 3 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132FanOpen | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
2140 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | FanOut | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 4 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132FanOut | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
2141 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 5 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
2142 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 6 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
2143 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 7 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
2144 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 8 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
2145 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | FrontTem1 | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 9 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132FrontTem1 | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
2146 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 10 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
2147 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 11 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
2148 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 12 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL FAULT
2149 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | More6hr | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 13 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 13 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132More6hr | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
2150 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20686 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20686 | 0 | 16 | aeiTUNQEC01QEC1BJETQEC1B-JET100132RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
2151 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20691 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20691 | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2152 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20691 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20691 | 2 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2153 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20691 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20691 | 4 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
2154 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 11381 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11381 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2155 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 11382 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11382 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2156 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20691 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20691 | 6 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2157 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 11383 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11383 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2158 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20691 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20691 | 8 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2159 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20691 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20691 | 10 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
2160 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | FailStart | SIL0 | MODBUS:4:Read:Input Registers | 20691 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20691 | 12 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133FailStart | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
2161 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | FailStop | SIL0 | MODBUS:4:Read:Input Registers | 20691 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20691 | 14 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133FailStop | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
2162 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | SpeedFrep | SIL0 | MODBUS:4:Read:Input Registers | 20692 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20692 | 0 | 32 | aeiTUNQEC01QEC1BJETQEC1B-JET100133SpeedFrep | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
2163 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 11384 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11384 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
2164 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11385 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11385 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2165 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20694 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20694 | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2166 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11386 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11386 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2167 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20694 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20694 | 2 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2168 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11387 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11387 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
2169 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20694 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20694 | 4 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
2170 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11388 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11388 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
2171 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20694 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20694 | 6 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
2172 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11389 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11389 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
2173 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20694 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20694 | 8 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
2174 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11390 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11390 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
2175 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20694 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20694 | 10 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
2176 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
2177 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CirOpen | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 1 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133CirOpen | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
2178 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CirOut | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 2 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133CirOut | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
2179 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | FanOpen | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 3 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133FanOpen | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
2180 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | FanOut | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 4 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133FanOut | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
2181 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 5 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
2182 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 6 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
2183 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 7 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
2184 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 8 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
2185 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | FrontTem1 | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 9 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133FrontTem1 | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
2186 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 10 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
2187 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 11 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
2188 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 12 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL FAULT
2189 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | More6hr | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 13 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 13 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133More6hr | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
2190 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20696 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20696 | 0 | 16 | aeiTUNQEC01QEC1BJETQEC1B-JET100133RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
2191 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20701 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20701 | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2192 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20701 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20701 | 2 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2193 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20701 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20701 | 4 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
2194 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 11401 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11401 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2195 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 11402 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11402 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2196 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20701 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20701 | 6 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2197 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 11403 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11403 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2198 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20701 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20701 | 8 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2199 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20701 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20701 | 10 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
2200 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | FailStart | SIL0 | MODBUS:4:Read:Input Registers | 20701 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20701 | 12 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134FailStart | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
2201 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | FailStop | SIL0 | MODBUS:4:Read:Input Registers | 20701 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20701 | 14 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134FailStop | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
2202 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | SpeedFrep | SIL0 | MODBUS:4:Read:Input Registers | 20702 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20702 | 0 | 32 | aeiTUNQEC01QEC1BJETQEC1B-JET100134SpeedFrep | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
2203 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 11404 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11404 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
2204 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11405 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11405 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2205 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20704 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20704 | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2206 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11406 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11406 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2207 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20704 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20704 | 2 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2208 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11407 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11407 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
2209 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20704 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20704 | 4 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
2210 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11408 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11408 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
2211 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20704 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20704 | 6 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
2212 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11409 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11409 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
2213 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20704 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20704 | 8 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
2214 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11410 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11410 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
2215 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20704 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20704 | 10 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
2216 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
2217 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CirOpen | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 1 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134CirOpen | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
2218 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CirOut | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 2 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134CirOut | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
2219 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | FanOpen | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 3 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134FanOpen | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
2220 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | FanOut | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 4 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134FanOut | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
2221 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 5 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
2222 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 6 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
2223 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 7 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
2224 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 8 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
2225 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | FrontTem1 | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 9 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134FrontTem1 | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
2226 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 10 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
2227 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 11 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
2228 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 12 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL FAULT
2229 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | More6hr | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 13 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 13 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134More6hr | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
2230 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20706 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20706 | 0 | 16 | aeiTUNQEC01QEC1BJETQEC1B-JET100134RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
2231 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20711 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20711 | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2232 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20711 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20711 | 2 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2233 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20711 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20711 | 4 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
2234 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 11421 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11421 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2235 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 11422 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11422 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2236 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20711 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20711 | 6 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2237 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 11423 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11423 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2238 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20711 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20711 | 8 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2239 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20711 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20711 | 10 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
2240 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | FailStart | SIL0 | MODBUS:4:Read:Input Registers | 20711 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20711 | 12 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392FailStart | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
2241 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | FailStop | SIL0 | MODBUS:4:Read:Input Registers | 20711 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20711 | 14 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392FailStop | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
2242 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | SpeedFrep | SIL0 | MODBUS:4:Read:Input Registers | 20712 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20712 | 0 | 32 | aeiTUNQEC01QEC1AJETQEC1A-JET102392SpeedFrep | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
2243 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 11424 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11424 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
2244 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11425 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11425 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2245 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20714 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20714 | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2246 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11426 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11426 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2247 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20714 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20714 | 2 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2248 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11427 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11427 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
2249 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20714 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20714 | 4 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
2250 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11428 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11428 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
2251 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20714 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20714 | 6 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
2252 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11429 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11429 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
2253 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20714 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20714 | 8 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
2254 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11430 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11430 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
2255 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20714 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20714 | 10 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
2256 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
2257 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CirOpen | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 1 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392CirOpen | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
2258 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CirOut | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 2 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392CirOut | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
2259 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | FanOpen | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 3 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392FanOpen | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
2260 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | FanOut | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 4 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392FanOut | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
2261 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 5 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
2262 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 6 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
2263 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 7 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
2264 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 8 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
2265 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | FrontTem1 | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 9 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392FrontTem1 | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
2266 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 10 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
2267 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 11 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
2268 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 12 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL FAULT
2269 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | More6hr | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 13 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 13 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392More6hr | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
2270 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20716 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20716 | 0 | 16 | aeiTUNQEC01QEC1AJETQEC1A-JET102392RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
2271 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20721 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20721 | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2272 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20721 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20721 | 2 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2273 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20721 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20721 | 4 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
2274 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 11441 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11441 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2275 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 11442 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11442 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2276 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20721 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20721 | 6 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2277 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 11443 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11443 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2278 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20721 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20721 | 8 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2279 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20721 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20721 | 10 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
2280 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | FailStart | SIL0 | MODBUS:4:Read:Input Registers | 20721 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20721 | 12 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393FailStart | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
2281 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | FailStop | SIL0 | MODBUS:4:Read:Input Registers | 20721 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20721 | 14 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393FailStop | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
2282 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | SpeedFrep | SIL0 | MODBUS:4:Read:Input Registers | 20722 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20722 | 0 | 32 | aeiTUNQEC01QEC1AJETQEC1A-JET102393SpeedFrep | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
2283 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 11444 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11444 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
2284 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11445 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11445 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2285 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20724 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20724 | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2286 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11446 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11446 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2287 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20724 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20724 | 2 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2288 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11447 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11447 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
2289 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20724 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20724 | 4 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
2290 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11448 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11448 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
2291 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20724 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20724 | 6 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
2292 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11449 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11449 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
2293 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20724 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20724 | 8 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
2294 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11450 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11450 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
2295 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20724 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20724 | 10 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
2296 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
2297 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CirOpen | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 1 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393CirOpen | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
2298 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CirOut | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 2 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393CirOut | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
2299 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | FanOpen | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 3 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393FanOpen | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
2300 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | FanOut | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 4 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393FanOut | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
2301 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 5 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
2302 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 6 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
2303 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 7 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
2304 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 8 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
2305 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | FrontTem1 | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 9 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393FrontTem1 | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
2306 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 10 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
2307 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 11 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
2308 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 12 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL FAULT
2309 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | More6hr | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 13 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 13 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393More6hr | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
2310 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20726 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20726 | 0 | 16 | aeiTUNQEC01QEC1AJETQEC1A-JET102393RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
2311 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20731 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20731 | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2312 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20731 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20731 | 2 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2313 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20731 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20731 | 4 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
2314 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 11461 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11461 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2315 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdSelMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 11462 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11462 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2316 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | AckSelMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20731 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20731 | 6 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394AckSelMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2317 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdExeMan | SIL2_Control | MODBUS:16:Write:Holding Registers | 11463 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11463 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2318 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | AckExeMan | SIL2_Control | MODBUS:4:Read:Input Registers | 20731 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20731 | 8 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394AckExeMan | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2319 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20731 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20731 | 10 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
2320 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | FailStart | SIL0 | MODBUS:4:Read:Input Registers | 20731 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20731 | 12 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394FailStart | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
2321 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | FailStop | SIL0 | MODBUS:4:Read:Input Registers | 20731 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20731 | 14 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394FailStop | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
2322 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | SpeedFrep | SIL0 | MODBUS:4:Read:Input Registers | 20732 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20732 | 0 | 32 | aeiTUNQEC01QEC1AJETQEC1A-JET102394SpeedFrep | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
2323 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 11464 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11464 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
2324 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11465 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11465 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2325 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20734 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20734 | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2326 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11466 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11466 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2327 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20734 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20734 | 2 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2328 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11467 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11467 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
2329 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20734 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20734 | 4 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
2330 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11468 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11468 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
2331 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20734 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20734 | 6 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
2332 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11469 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11469 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
2333 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20734 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20734 | 8 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
2334 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11470 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11470 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
2335 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20734 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20734 | 10 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
2336 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
2337 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CirOpen | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 1 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394CirOpen | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
2338 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CirOut | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 2 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394CirOut | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
2339 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | FanOpen | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 3 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394FanOpen | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
2340 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | FanOut | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 4 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394FanOut | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
2341 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 5 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
2342 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 6 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
2343 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 7 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
2344 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 8 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
2345 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | FrontTem1 | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 9 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394FrontTem1 | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
2346 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 10 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
2347 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 11 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
2348 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 12 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL FAULT
2349 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | More6hr | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 13 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 13 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394More6hr | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
2350 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20736 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20736 | 0 | 16 | aeiTUNQEC01QEC1AJETQEC1A-JET102394RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
2351 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Vac240SwOp | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 0 | 1 | deiTUNQEC01MMSSPLC01Vac240SwOp | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY DISCONNECTING SWITCH - OPEN
2352 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Vac240Volt | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 1 | 1 | deiTUNQEC01MMSSPLC01Vac240Volt | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY VOLTAGE PRESENCE
2353 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | VolOpen | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 2 | 1 | deiTUNQEC01MMSSPLC01VolOpen | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER OPEN
2354 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | VolFault | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 3 | 1 | deiTUNQEC01MMSSPLC01VolFault | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER FAULT
2355 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | VolSupOpen | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 4 | 1 | deiTUNQEC01MMSSPLC01VolSupOpen | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN
2356 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | VolSupFault | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 5 | 1 | deiTUNQEC01MMSSPLC01VolSupFault | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT
2357 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | CabOpen | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 6 | 1 | deiTUNQEC01MMSSPLC01CabOpen | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS OPEN
2358 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | CabFault | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 7 | 1 | deiTUNQEC01MMSSPLC01CabFault | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS FAULT
2359 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | SerOpen | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 8 | 1 | deiTUNQEC01MMSSPLC01SerOpen | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER OPEN
2360 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | SerFault | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 9 | 1 | deiTUNQEC01MMSSPLC01SerFault | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER FAULT
2361 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | UpsBreOpen | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 10 | 1 | deiTUNQEC01MMSSPLC01UpsBreOpen | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER OPEN
2362 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | UpsBreFault | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 11 | 1 | deiTUNQEC01MMSSPLC01UpsBreFault | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER FAULT
2363 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | UpsSwOpen | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 12 | 1 | deiTUNQEC01MMSSPLC01UpsSwOpen | 4 |  |  | 0 | $ComStatus , , | #UPS DISCONNECTING SWITCH OPEN
2364 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | UpsFault | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 13 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 13 | 1 | deiTUNQEC01MMSSPLC01UpsFault | 4 |  |  | 0 | $ComStatus , , | #UPS FAULT
2365 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Sup24Vdc1Open | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 14 | 1 | deiTUNQEC01MMSSPLC01Sup24Vdc1Open | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN
2366 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Sup24Vdc1Fault | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 15 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 15 | 1 | deiTUNQEC01MMSSPLC01Sup24Vdc1Fault | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT
2367 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Sup24Vdc1Volt | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 0 | 1 | deiTUNQEC01MMSSPLC01Sup24Vdc1Volt | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 ABSENCE OF VOLTAGE
2368 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Sup24Vdc2Open | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 1 | 1 | deiTUNQEC01MMSSPLC01Sup24Vdc2Open | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN
2369 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Sup24Vdc2Fault | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 2 | 1 | deiTUNQEC01MMSSPLC01Sup24Vdc2Fault | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT
2370 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Sup24Vdc2Volt | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 3 | 1 | deiTUNQEC01MMSSPLC01Sup24Vdc2Volt | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 ABSENCE OF VOLTAGE
2371 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | SwOpen | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 4 | 1 | deiTUNQEC01MMSSPLC01SwOpen | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER OPEN
2372 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | SwFault | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 5 | 1 | deiTUNQEC01MMSSPLC01SwFault | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER FAULT
2373 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | LcpOpen | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 6 | 1 | deiTUNQEC01MMSSPLC01LcpOpen | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER OPEN
2374 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | LcpFault | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 7 | 1 | deiTUNQEC01MMSSPLC01LcpFault | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER FAULT
2375 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Plc1Open | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 8 | 1 | deiTUNQEC01MMSSPLC01Plc1Open | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER OPEN
2376 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Plc1Fault | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 9 | 1 | deiTUNQEC01MMSSPLC01Plc1Fault | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER FAULT
2377 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Plc2Open | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 10 | 1 | deiTUNQEC01MMSSPLC01Plc2Open | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER OPEN
2378 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Plc2Fault | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 11 | 1 | deiTUNQEC01MMSSPLC01Plc2Fault | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER FAULT
2379 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | SuArTrig | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 12 | 1 | deiTUNQEC01MMSSPLC01SuArTrig | 4 |  |  | 0 | $ComStatus , , | #SURGE ARRESTER TRIGGERED
2380 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mcsd1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 0 | 1 | deiTUNQEC01MMSLPS-MDB01Mcsd1Stat | 4 |  |  | 0 | $ComStatus , , | #Power normal MCSD 1 status
2381 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mcsd2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 1 | 1 | deiTUNQEC01MMSLPS-MDB01Mcsd2Stat | 4 |  |  | 0 | $ComStatus , , | #Power replacement MCSD 2 status
2382 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mcsd1pos | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 2 | 1 | deiTUNQEC01MMSLPS-MDB01Mcsd1pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 1 racked position
2383 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mcsd2pos | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 3 | 1 | deiTUNQEC01MMSLPS-MDB01Mcsd2pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 2 racked position
2384 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Change | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 4 | 1 | deiTUNQEC01MMSLPS-MDB01Change | 4 |  |  | 0 | $ComStatus , , | #Change over
2385 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | relay1 | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 5 | 1 | deiTUNQEC01MMSLPS-MDB01relay1 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 1
2386 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | relay2 | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 6 | 1 | deiTUNQEC01MMSLPS-MDB01relay2 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 2
2387 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 7 | 1 | deiTUNQEC01MMSLPS-MDB01Closed | 4 |  |  | 0 | $ComStatus , , | #MCB closed status
2388 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 8 | 1 | deiTUNQEC01MMSLPS-MDB01Trip | 4 |  |  | 0 | $ComStatus , , | #MCB tripped status
2389 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | PowerCut | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 9 | 1 | deiTUNQEC01MMSLPS-MDB01PowerCut | 4 |  |  | 0 | $ComStatus , , | #Emergency power cut (push button)
2390 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mccb1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 10 | 1 | deiTUNQEC01MMSLPS-MDB01Mccb1Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 status
2391 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 11 | 1 | deiTUNQEC01MMSLPS-MDB01Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 trip
2392 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mccb2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 12 | 1 | deiTUNQEC01MMSLPS-MDB01Mccb2Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 status
2393 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 13 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 13 | 1 | deiTUNQEC01MMSLPS-MDB01Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 trip
2394 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mccb3Stat | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 14 | 1 | deiTUNQEC01MMSLPS-MDB01Mccb3Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 status
2395 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mccb3Trip | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 15 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 15 | 1 | deiTUNQEC01MMSLPS-MDB01Mccb3Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 trip
2396 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mcsd1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 0 | 1 | deiTUNQEC01MMSLPS-MDB02Mcsd1Stat | 4 |  |  | 0 | $ComStatus , , | #Power normal MCSD 1 status
2397 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mcsd2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 1 | 1 | deiTUNQEC01MMSLPS-MDB02Mcsd2Stat | 4 |  |  | 0 | $ComStatus , , | #Power replacement MCSD 2 status
2398 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mcsd1pos | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 2 | 1 | deiTUNQEC01MMSLPS-MDB02Mcsd1pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 1 racked position
2399 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mcsd2pos | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 3 | 1 | deiTUNQEC01MMSLPS-MDB02Mcsd2pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 2 racked position
2400 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Change | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 4 | 1 | deiTUNQEC01MMSLPS-MDB02Change | 4 |  |  | 0 | $ComStatus , , | #Change over
2401 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | relay1 | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 5 | 1 | deiTUNQEC01MMSLPS-MDB02relay1 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 1
2402 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | relay2 | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 6 | 1 | deiTUNQEC01MMSLPS-MDB02relay2 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 2
2403 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 7 | 1 | deiTUNQEC01MMSLPS-MDB02Closed | 4 |  |  | 0 | $ComStatus , , | #MCB closed status
2404 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 8 | 1 | deiTUNQEC01MMSLPS-MDB02Trip | 4 |  |  | 0 | $ComStatus , , | #MCB tripped status
2405 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | PowerCut | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 9 | 1 | deiTUNQEC01MMSLPS-MDB02PowerCut | 4 |  |  | 0 | $ComStatus , , | #Emergency power cut (push button)
2406 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mccb1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 10 | 1 | deiTUNQEC01MMSLPS-MDB02Mccb1Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 status
2407 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 11 | 1 | deiTUNQEC01MMSLPS-MDB02Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 trip
2408 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mccb2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 12 | 1 | deiTUNQEC01MMSLPS-MDB02Mccb2Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 status
2409 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 13 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 13 | 1 | deiTUNQEC01MMSLPS-MDB02Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 trip
2410 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mccb3Stat | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 14 | 1 | deiTUNQEC01MMSLPS-MDB02Mccb3Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 status
2411 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mccb3Trip | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 15 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 15 | 1 | deiTUNQEC01MMSLPS-MDB02Mccb3Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 trip
2412 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL1-IO01 | 77 | Relay | SIL0 | MODBUS:4:Read:Input Registers | 20771 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20771 | 0 | 1 | deiTUNQEC01MMSEL1-IO01Relay | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay
2413 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL1-IO01 | 77 | Isolator | SIL0 | MODBUS:4:Read:Input Registers | 20771 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20771 | 1 | 1 | deiTUNQEC01MMSEL1-IO01Isolator | 4 |  |  | 0 | $ComStatus , , | #LBS Main incomer isolator status
2414 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL1-IO01 | 77 | Supply | SIL0 | MODBUS:4:Read:Input Registers | 20771 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20771 | 2 | 1 | deiTUNQEC01MMSEL1-IO01Supply | 4 |  |  | 0 | $ComStatus , , | #UPS supply status
2415 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL1-IO01 | 77 | Faulty | SIL0 | MODBUS:4:Read:Input Registers | 20771 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20771 | 3 | 1 | deiTUNQEC01MMSEL1-IO01Faulty | 4 |  |  | 0 | $ComStatus , , | #UPS faulty
2416 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL1-IO01 | 77 | Power | SIL0 | MODBUS:4:Read:Input Registers | 20771 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20771 | 4 | 1 | deiTUNQEC01MMSEL1-IO01Power | 4 |  |  | 0 | $ComStatus , , | #24VDC UPS power status
2417 | QEC01_RTU | TUN:QEC01 | MMS | MCCB | EL1-UPS | 78 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20781 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20781 | 0 | 1 | deiTUNQEC01MMSEL1-UPSTrip | 4 |  |  | 0 | $ComStatus , , | #MCCB trip status
2418 | QEC01_RTU | TUN:QEC01 | MMS | MCCB | EL1-UPS | 78 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20781 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20781 | 1 | 1 | deiTUNQEC01MMSEL1-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #MCCB closed status
2419 | QEC01_RTU | TUN:QEC01 | MMS | LBS | EL1-UPS | 79 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20791 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20791 | 0 | 1 | deiTUNQEC01MMSEL1-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #LBS closed status
2420 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL1-VSD01 | 80 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20801 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20801 | 0 | 1 | deiTUNQEC01MMSUPS_EL1-VSD01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2421 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL1-VSD01 | 80 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20801 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20801 | 1 | 1 | deiTUNQEC01MMSUPS_EL1-VSD01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2422 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL1-VSD02 | 81 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20811 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20811 | 0 | 1 | deiTUNQEC01MMSUPS_EL1-VSD02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2423 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL1-VSD02 | 81 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20811 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20811 | 1 | 1 | deiTUNQEC01MMSUPS_EL1-VSD02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2424 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT3-IDP01 | 82 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20821 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20821 | 0 | 1 | deiTUNQEC01MMS3P-VT3-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2425 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT3-IDP01 | 82 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20821 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20821 | 1 | 1 | deiTUNQEC01MMS3P-VT3-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2426 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT3-IDP01 | 83 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20831 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20831 | 0 | 1 | deiTUNQEC01MMS2P-VT3-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2427 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT3-IDP01 | 83 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20831 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20831 | 1 | 1 | deiTUNQEC01MMS2P-VT3-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2428 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT4-IDP01 | 84 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20841 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20841 | 0 | 1 | deiTUNQEC01MMS3P-VT4-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2429 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT4-IDP01 | 84 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20841 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20841 | 1 | 1 | deiTUNQEC01MMS3P-VT4-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2430 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT4-IDP01 | 85 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20851 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20851 | 0 | 1 | deiTUNQEC01MMS2P-VT4-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2431 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT4-IDP01 | 85 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20851 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20851 | 1 | 1 | deiTUNQEC01MMS2P-VT4-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2432 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-01 | 86 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20861 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20861 | 0 | 1 | deiTUNQEC01MMS3P-VT6-TDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2433 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-01 | 86 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20861 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20861 | 1 | 1 | deiTUNQEC01MMS3P-VT6-TDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2434 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-01 | 87 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20871 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20871 | 0 | 1 | deiTUNQEC01MMS2P-VT6-TDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2435 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-01 | 87 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20871 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20871 | 1 | 1 | deiTUNQEC01MMS2P-VT6-TDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2436 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-02 | 88 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20881 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20881 | 0 | 1 | deiTUNQEC01MMS3P-VT6-TDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2437 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-02 | 88 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20881 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20881 | 1 | 1 | deiTUNQEC01MMS3P-VT6-TDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2438 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-02 | 89 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20891 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20891 | 0 | 1 | deiTUNQEC01MMS2P-VT6-TDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2439 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-02 | 89 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20891 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20891 | 1 | 1 | deiTUNQEC01MMS2P-VT6-TDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2440 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-03 | 90 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20901 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20901 | 0 | 1 | deiTUNQEC01MMS3P-VT6-TDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2441 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-03 | 90 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20901 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20901 | 1 | 1 | deiTUNQEC01MMS3P-VT6-TDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2442 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-03 | 91 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20911 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20911 | 0 | 1 | deiTUNQEC01MMS2P-VT6-TDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2443 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-03 | 91 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20911 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20911 | 1 | 1 | deiTUNQEC01MMS2P-VT6-TDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2444 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P--FR2-BDP01-01 | 92 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20921 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20921 | 0 | 1 | deiTUNQEC01MMS3P--FR2-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2445 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P--FR2-BDP01-01 | 92 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20921 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20921 | 1 | 1 | deiTUNQEC01MMS3P--FR2-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2446 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P--FR2-BDP01-01 | 93 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20931 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20931 | 0 | 1 | deiTUNQEC01MMS2P--FR2-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2447 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P--FR2-BDP01-01 | 93 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20931 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20931 | 1 | 1 | deiTUNQEC01MMS2P--FR2-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2448 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P--FR2-BDP01-02 | 94 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20941 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20941 | 0 | 1 | deiTUNQEC01MMS3P--FR2-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2449 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P--FR2-BDP01-02 | 94 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20941 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20941 | 1 | 1 | deiTUNQEC01MMS3P--FR2-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2450 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P--FR2-BDP01-02 | 95 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20951 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20951 | 0 | 1 | deiTUNQEC01MMS2P--FR2-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2451 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P--FR2-BDP01-02 | 95 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20951 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20951 | 1 | 1 | deiTUNQEC01MMS2P--FR2-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2452 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-94 | 96 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20961 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20961 | 0 | 1 | deiTUNQEC01MMSMSFD-CON-94McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2453 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-94 | 96 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20961 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20961 | 1 | 1 | deiTUNQEC01MMSMSFD-CON-94McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2454 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-58 | 97 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20971 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20971 | 0 | 1 | deiTUNQEC01MMSMSFD-CON-58McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2455 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-58 | 97 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20971 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20971 | 1 | 1 | deiTUNQEC01MMSMSFD-CON-58McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2456 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-88 | 98 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20981 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20981 | 0 | 1 | deiTUNQEC01MMSMSFD-CON-88McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2457 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-88 | 98 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20981 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20981 | 1 | 1 | deiTUNQEC01MMSMSFD-CON-88McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2458 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL2-IO01 | 99 | Relay | SIL0 | MODBUS:4:Read:Input Registers | 20991 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20991 | 0 | 1 | deiTUNQEC01MMSEL2-IO01Relay | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay
2459 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL2-IO01 | 99 | Isolator | SIL0 | MODBUS:4:Read:Input Registers | 20991 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20991 | 1 | 1 | deiTUNQEC01MMSEL2-IO01Isolator | 4 |  |  | 0 | $ComStatus , , | #LBS Main incomer isolator status
2460 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL2-IO01 | 99 | Supply | SIL0 | MODBUS:4:Read:Input Registers | 20991 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20991 | 2 | 1 | deiTUNQEC01MMSEL2-IO01Supply | 4 |  |  | 0 | $ComStatus , , | #UPS supply status
2461 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL2-IO01 | 99 | Faulty | SIL0 | MODBUS:4:Read:Input Registers | 20991 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20991 | 3 | 1 | deiTUNQEC01MMSEL2-IO01Faulty | 4 |  |  | 0 | $ComStatus , , | #UPS faulty
2462 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL2-IO01 | 99 | Power | SIL0 | MODBUS:4:Read:Input Registers | 20991 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20991 | 4 | 1 | deiTUNQEC01MMSEL2-IO01Power | 4 |  |  | 0 | $ComStatus , , | #24VDC UPS power status
2463 | QEC01_RTU | TUN:QEC01 | MMS | MCCB | EL2-UPS | 100 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 21001 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21001 | 0 | 1 | deiTUNQEC01MMSEL2-UPSTrip | 4 |  |  | 0 | $ComStatus , , | #MCCB trip status
2464 | QEC01_RTU | TUN:QEC01 | MMS | MCCB | EL2-UPS | 100 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 21001 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21001 | 1 | 1 | deiTUNQEC01MMSEL2-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #MCCB closed status
2465 | QEC01_RTU | TUN:QEC01 | MMS | LBS | EL2-UPS | 101 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 21011 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21011 | 0 | 1 | deiTUNQEC01MMSEL2-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #LBS closed status
2466 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL2-VSD01 | 102 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21021 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21021 | 0 | 1 | deiTUNQEC01MMSUPS_EL2-VSD01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2467 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL2-VSD01 | 102 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21021 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21021 | 1 | 1 | deiTUNQEC01MMSUPS_EL2-VSD01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2468 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL2-VSD02 | 103 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21031 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21031 | 0 | 1 | deiTUNQEC01MMSUPS_EL2-VSD02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2469 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL2-VSD02 | 103 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21031 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21031 | 1 | 1 | deiTUNQEC01MMSUPS_EL2-VSD02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2470 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT1-IDP01 | 104 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21041 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21041 | 0 | 1 | deiTUNQEC01MMS3P-VT1-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2471 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT1-IDP01 | 104 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21041 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21041 | 1 | 1 | deiTUNQEC01MMS3P-VT1-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2472 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT1-IDP01 | 105 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21051 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21051 | 0 | 1 | deiTUNQEC01MMS2P-VT1-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2473 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT1-IDP01 | 105 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21051 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21051 | 1 | 1 | deiTUNQEC01MMS2P-VT1-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2474 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT2-IDP01 | 106 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21061 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21061 | 0 | 1 | deiTUNQEC01MMS3P-VT2-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2475 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT2-IDP01 | 106 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21061 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21061 | 1 | 1 | deiTUNQEC01MMS3P-VT2-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2476 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT2-IDP01 | 107 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21071 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21071 | 0 | 1 | deiTUNQEC01MMS2P-VT2-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2477 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT2-IDP01 | 107 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21071 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21071 | 1 | 1 | deiTUNQEC01MMS2P-VT2-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2478 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-01 | 108 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21081 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21081 | 0 | 1 | deiTUNQEC01MMS3P-VT5-TDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2479 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-01 | 108 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21081 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21081 | 1 | 1 | deiTUNQEC01MMS3P-VT5-TDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2480 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-01 | 109 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21091 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21091 | 0 | 1 | deiTUNQEC01MMS2P-VT5-TDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2481 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-01 | 109 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21091 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21091 | 1 | 1 | deiTUNQEC01MMS2P-VT5-TDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2482 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-02 | 110 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21101 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21101 | 0 | 1 | deiTUNQEC01MMS3P-VT5-TDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2483 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-02 | 110 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21101 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21101 | 1 | 1 | deiTUNQEC01MMS3P-VT5-TDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2484 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-02 | 111 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21111 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21111 | 0 | 1 | deiTUNQEC01MMS2P-VT5-TDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2485 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-02 | 111 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21111 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21111 | 1 | 1 | deiTUNQEC01MMS2P-VT5-TDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2486 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-03 | 112 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21121 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21121 | 0 | 1 | deiTUNQEC01MMS3P-VT5-TDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2487 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-03 | 112 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21121 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21121 | 1 | 1 | deiTUNQEC01MMS3P-VT5-TDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2488 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-03 | 113 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21131 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21131 | 0 | 1 | deiTUNQEC01MMS2P-VT5-TDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2489 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-03 | 113 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21131 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21131 | 1 | 1 | deiTUNQEC01MMS2P-VT5-TDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2490 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-FR1-BDP01-01 | 114 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21141 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21141 | 0 | 1 | deiTUNQEC01MMS3P-FR1-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2491 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-FR1-BDP01-01 | 114 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21141 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21141 | 1 | 1 | deiTUNQEC01MMS3P-FR1-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2492 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-FR1-BDP01-01 | 115 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21151 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21151 | 0 | 1 | deiTUNQEC01MMS2P-FR1-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2493 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-FR1-BDP01-01 | 115 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21151 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21151 | 1 | 1 | deiTUNQEC01MMS2P-FR1-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2494 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-FR1-BDP01-02 | 116 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21161 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21161 | 0 | 1 | deiTUNQEC01MMS3P-FR1-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2495 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-FR1-BDP01-02 | 116 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21161 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21161 | 1 | 1 | deiTUNQEC01MMS3P-FR1-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2496 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-FR1-BDP01-02 | 117 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21171 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21171 | 0 | 1 | deiTUNQEC01MMS2P-FR1-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2497 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-FR1-BDP01-02 | 117 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21171 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21171 | 1 | 1 | deiTUNQEC01MMS2P-FR1-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2498 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-50 | 118 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21181 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21181 | 0 | 1 | deiTUNQEC01MMSMSFD-CON-50McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2499 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-50 | 118 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21181 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21181 | 1 | 1 | deiTUNQEC01MMSMSFD-CON-50McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2500 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-52 | 119 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21191 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21191 | 0 | 1 | deiTUNQEC01MMSMSFD-CON-52McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2501 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-52 | 119 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21191 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21191 | 1 | 1 | deiTUNQEC01MMSMSFD-CON-52McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2502 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-95 | 120 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21201 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21201 | 0 | 1 | deiTUNQEC01MMSMSFD-CON-95McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2503 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-95 | 120 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21201 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21201 | 1 | 1 | deiTUNQEC01MMSMSFD-CON-95McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
-END- | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10602 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10602 | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2505 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20301 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20301 | 6 | 2 | deiTUNQAP01NS01TVFVT4-TVF01AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2506 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10603 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10603 | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2507 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20301 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20301 | 8 | 2 | deiTUNQAP01NS01TVFVT4-TVF01AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2508 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20301 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20301 | 10 | 1 | deiTUNQAP01NS01TVFVT4-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
2509 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20301 | 12 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20301 | 12 | 1 | deiTUNQAP01NS01TVFVT4-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
2510 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20301 | 14 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20301 | 14 | 1 | deiTUNQAP01NS01TVFVT4-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
2511 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20302 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20302 | 0 | 32 | aeiTUNQAP01NS01TVFVT4-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
2512 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10604 | 0 | 2 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10604 | 0 | 2 | deoTUNQAP01NS01TVFVT4-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
2513 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10605 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10605 | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2514 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 0 | 2 | deiTUNQAP01NS01TVFVT4-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2515 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10606 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10606 | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2516 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 2 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 2 | 2 | deiTUNQAP01NS01TVFVT4-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2517 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10607 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10607 | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
2518 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 4 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 4 | 2 | deiTUNQAP01NS01TVFVT4-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
2519 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10608 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10608 | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
2520 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 6 | 2 | deiTUNQAP01NS01TVFVT4-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
2521 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10609 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10609 | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
2522 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 8 | 2 | deiTUNQAP01NS01TVFVT4-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
2523 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10610 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10610 | 0 | 1 | deoTUNQAP01NS01TVFVT4-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
2524 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 10 | 2 | deiTUNQAP01NS01TVFVT4-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
2525 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20304 | 12 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20304 | 12 | 1 | deiTUNQAP01NS01TVFVT4-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
2526 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20304 | 14 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20304 | 14 | 1 | deiTUNQAP01NS01TVFVT4-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
2527 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 0 | 1 | deiTUNQAP01NS01TVFVT4-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
2528 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 1 | 1 | deiTUNQAP01NS01TVFVT4-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
2529 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 2 | 1 | deiTUNQAP01NS01TVFVT4-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
2530 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 3 | 1 | deiTUNQAP01NS01TVFVT4-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
2531 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 4 | 1 | deiTUNQAP01NS01TVFVT4-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
2532 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 5 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 5 | 1 | deiTUNQAP01NS01TVFVT4-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
2533 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 6 | 1 | deiTUNQAP01NS01TVFVT4-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
2534 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 7 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 7 | 1 | deiTUNQAP01NS01TVFVT4-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
2535 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 8 | 1 | deiTUNQAP01NS01TVFVT4-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
2536 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 9 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 9 | 1 | deiTUNQAP01NS01TVFVT4-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
2537 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 10 | 1 | deiTUNQAP01NS01TVFVT4-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
2538 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 11 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 11 | 1 | deiTUNQAP01NS01TVFVT4-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
2539 | QAP01_RTU | TUN:QAP01 | NS01:TVF | TVF | VT4-TVF01 | 30 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20306 | 0 | 16 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20306 | 0 | 16 | aeiTUNQAP01NS01TVFVT4-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
2540 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | 31 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 0 | 1 | deiTUNQAP01SS01SENSORTS101733Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
2541 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | 31 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 1 | 1 | deiTUNQAP01SS01SENSORTS101733TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
2542 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | 31 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 2 | 1 | deiTUNQAP01SS01SENSORTS101733HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
2543 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | 31 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 3 | 1 | deiTUNQAP01SS01SENSORTS101733AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
2544 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | 31 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20312 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20312 | 0 | 32 | aeiTUNQAP01SS01SENSORTS101733Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
2545 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101733 | 31 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20314 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20314 | 0 | 32 | aeiTUNQAP01SS01SENSORTS101733Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
2546 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | 32 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 0 | 1 | deiTUNQAP01SS01SENSORTS101817Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
2547 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | 32 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 1 | 1 | deiTUNQAP01SS01SENSORTS101817TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
2548 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | 32 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 2 | 1 | deiTUNQAP01SS01SENSORTS101817HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
2549 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | 32 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 3 | 1 | deiTUNQAP01SS01SENSORTS101817AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
2550 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | 32 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20322 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20322 | 0 | 32 | aeiTUNQAP01SS01SENSORTS101817Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
2551 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | TTS | TS101817 | 32 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20324 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20324 | 0 | 32 | aeiTUNQAP01SS01SENSORTS101817Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
2552 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | 33 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 0 | 1 | deiTUNQAP01NS01SENSORTS102057Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
2553 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | 33 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 1 | 1 | deiTUNQAP01NS01SENSORTS102057TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
2554 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | 33 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 2 | 1 | deiTUNQAP01NS01SENSORTS102057HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
2555 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | 33 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 3 | 1 | deiTUNQAP01NS01SENSORTS102057AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
2556 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | 33 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20332 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20332 | 0 | 32 | aeiTUNQAP01NS01SENSORTS102057Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
2557 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102057 | 33 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20334 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20334 | 0 | 32 | aeiTUNQAP01NS01SENSORTS102057Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
2558 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | 34 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 0 | 1 | deiTUNQAP01NS01SENSORTS102121Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
2559 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | 34 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 1 | 1 | deiTUNQAP01NS01SENSORTS102121TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
2560 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | 34 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 2 | 1 | deiTUNQAP01NS01SENSORTS102121HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
2561 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | 34 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 3 | 1 | deiTUNQAP01NS01SENSORTS102121AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
2562 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | 34 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20342 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20342 | 0 | 32 | aeiTUNQAP01NS01SENSORTS102121Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
2563 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | TTS | TS102121 | 34 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20344 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20344 | 0 | 32 | aeiTUNQAP01NS01SENSORTS102121Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
2564 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | VS | VS101763 | 35 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20351 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20351 | 0 | 1 | deiTUNQAP01SS01SENSORVS101763Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
2565 | QAP01_RTU | TUN:QAP01 | SS01:SENSOR | VS | VS101763 | 35 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20352 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20352 | 0 | 32 | aeiTUNQAP01SS01SENSORVS101763Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
2566 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | VS | VS102092 | 36 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20361 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20361 | 0 | 1 | deiTUNQAP01NS01SENSORVS102092Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
2567 | QAP01_RTU | TUN:QAP01 | NS01:SENSOR | VS | VS102092 | 36 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20362 | 0 | 32 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20362 | 0 | 32 | aeiTUNQAP01NS01SENSORVS102092Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
2568 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20371 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20371 | 0 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2569 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20371 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20371 | 2 | 1 | deiTUNQAP01SS01DAMPERVT5-TDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2570 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20371 | 4 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20371 | 4 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2571 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 10741 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10741 | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2572 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10742 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10742 | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2573 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20371 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20371 | 6 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2574 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10743 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10743 | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2575 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20371 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20371 | 8 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2576 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10744 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10744 | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
2577 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20371 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20371 | 10 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
2578 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10745 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10745 | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
2579 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20371 | 12 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20371 | 12 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
2580 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10746 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10746 | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
2581 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20371 | 14 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20371 | 14 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
2582 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10747 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10747 | 0 | 1 | deoTUNQAP01SS01DAMPERVT5-TDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
2583 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20372 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20372 | 0 | 2 | deiTUNQAP01SS01DAMPERVT5-TDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
2584 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20372 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20372 | 2 | 1 | deiTUNQAP01SS01DAMPERVT5-TDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
2585 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20372 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20372 | 4 | 1 | deiTUNQAP01SS01DAMPERVT5-TDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
2586 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20372 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20372 | 6 | 1 | deiTUNQAP01SS01DAMPERVT5-TDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2587 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | VT5-TDP01 | 37 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20372 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20372 | 8 | 1 | deiTUNQAP01SS01DAMPERVT5-TDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2588 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20381 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20381 | 0 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2589 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20381 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20381 | 2 | 1 | deiTUNQAP01NS01DAMPERVT6-TDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2590 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20381 | 4 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20381 | 4 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2591 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 10761 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10761 | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2592 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10762 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10762 | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2593 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20381 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20381 | 6 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2594 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10763 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10763 | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2595 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20381 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20381 | 8 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2596 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10764 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10764 | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
2597 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20381 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20381 | 10 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
2598 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10765 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10765 | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
2599 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20381 | 12 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20381 | 12 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
2600 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10766 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10766 | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
2601 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20381 | 14 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20381 | 14 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
2602 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10767 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10767 | 0 | 1 | deoTUNQAP01NS01DAMPERVT6-TDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
2603 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20382 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20382 | 0 | 2 | deiTUNQAP01NS01DAMPERVT6-TDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
2604 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20382 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20382 | 2 | 1 | deiTUNQAP01NS01DAMPERVT6-TDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
2605 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20382 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20382 | 4 | 1 | deiTUNQAP01NS01DAMPERVT6-TDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
2606 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20382 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20382 | 6 | 1 | deiTUNQAP01NS01DAMPERVT6-TDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2607 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | VT6-TDP01 | 38 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20382 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20382 | 8 | 1 | deiTUNQAP01NS01DAMPERVT6-TDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2608 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | 39 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20391 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20391 | 0 | 2 | deiTUNQAP01SS01DAMPERVT1-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2609 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | 39 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20391 | 2 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20391 | 2 | 2 | deiTUNQAP01SS01DAMPERVT1-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2610 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | 39 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 4 | 1 | deiTUNQAP01SS01DAMPERVT1-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
2611 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | 39 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 6 | 1 | deiTUNQAP01SS01DAMPERVT1-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
2612 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | 39 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 8 | 1 | deiTUNQAP01SS01DAMPERVT1-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2613 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT1-IDP01 | 39 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 10 | 1 | deiTUNQAP01SS01DAMPERVT1-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2614 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | 40 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20401 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20401 | 0 | 2 | deiTUNQAP01SS01DAMPERVT2-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2615 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | 40 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20401 | 2 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20401 | 2 | 2 | deiTUNQAP01SS01DAMPERVT2-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2616 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | 40 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 4 | 1 | deiTUNQAP01SS01DAMPERVT2-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
2617 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | 40 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 6 | 1 | deiTUNQAP01SS01DAMPERVT2-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
2618 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | 40 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 8 | 1 | deiTUNQAP01SS01DAMPERVT2-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2619 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | IDP | VT2-IDP01 | 40 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 10 | 1 | deiTUNQAP01SS01DAMPERVT2-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2620 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | 41 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20411 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20411 | 0 | 2 | deiTUNQAP01NS01DAMPERVT3-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2621 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | 41 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20411 | 2 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20411 | 2 | 2 | deiTUNQAP01NS01DAMPERVT3-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2622 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | 41 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20411 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20411 | 4 | 1 | deiTUNQAP01NS01DAMPERVT3-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
2623 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | 41 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20411 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20411 | 6 | 1 | deiTUNQAP01NS01DAMPERVT3-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
2624 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | 41 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20411 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20411 | 8 | 1 | deiTUNQAP01NS01DAMPERVT3-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2625 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT3-IDP01 | 41 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20411 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20411 | 10 | 1 | deiTUNQAP01NS01DAMPERVT3-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2626 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | 42 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20421 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20421 | 0 | 2 | deiTUNQAP01NS01DAMPERVT4-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2627 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | 42 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20421 | 2 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20421 | 2 | 2 | deiTUNQAP01NS01DAMPERVT4-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2628 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | 42 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20421 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20421 | 4 | 1 | deiTUNQAP01NS01DAMPERVT4-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
2629 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | 42 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20421 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20421 | 6 | 1 | deiTUNQAP01NS01DAMPERVT4-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
2630 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | 42 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20421 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20421 | 8 | 1 | deiTUNQAP01NS01DAMPERVT4-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2631 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | IDP | VT4-IDP01 | 42 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20421 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20421 | 10 | 1 | deiTUNQAP01NS01DAMPERVT4-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2632 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20431 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20431 | 0 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2633 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20431 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20431 | 2 | 1 | deiTUNQAP01SS01DAMPERFR1-BDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2634 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20431 | 4 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20431 | 4 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2635 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 10861 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10861 | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2636 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10862 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10862 | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2637 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20431 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20431 | 6 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2638 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10863 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10863 | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2639 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20431 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20431 | 8 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2640 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10864 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10864 | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
2641 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20431 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20431 | 10 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
2642 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10865 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10865 | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
2643 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20431 | 12 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20431 | 12 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
2644 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10866 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10866 | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
2645 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20431 | 14 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20431 | 14 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
2646 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10867 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10867 | 0 | 1 | deoTUNQAP01SS01DAMPERFR1-BDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
2647 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20432 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20432 | 0 | 2 | deiTUNQAP01SS01DAMPERFR1-BDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
2648 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20432 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20432 | 2 | 1 | deiTUNQAP01SS01DAMPERFR1-BDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
2649 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20432 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20432 | 4 | 1 | deiTUNQAP01SS01DAMPERFR1-BDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
2650 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20432 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20432 | 6 | 1 | deiTUNQAP01SS01DAMPERFR1-BDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2651 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | TVD | FR1-BDP01 | 43 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20432 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20432 | 8 | 1 | deiTUNQAP01SS01DAMPERFR1-BDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2652 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20441 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20441 | 0 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2653 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20441 | 2 | 1 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20441 | 2 | 1 | deiTUNQAP01NS01DAMPERFR2-BDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2654 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20441 | 4 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20441 | 4 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2655 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 10881 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10881 | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2656 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10882 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10882 | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2657 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20441 | 6 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20441 | 6 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2658 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10883 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10883 | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2659 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20441 | 8 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20441 | 8 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2660 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10884 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10884 | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
2661 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20441 | 10 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20441 | 10 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
2662 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10885 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10885 | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
2663 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20441 | 12 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20441 | 12 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
2664 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10886 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10886 | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
2665 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20441 | 14 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20441 | 14 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
2666 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10887 | 0 | 1 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10887 | 0 | 1 | deoTUNQAP01NS01DAMPERFR2-BDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
2667 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20442 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Control |  | QAP01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20442 | 0 | 2 | deiTUNQAP01NS01DAMPERFR2-BDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
2668 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20442 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20442 | 2 | 1 | deiTUNQAP01NS01DAMPERFR2-BDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
2669 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20442 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20442 | 4 | 1 | deiTUNQAP01NS01DAMPERFR2-BDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
2670 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20442 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20442 | 6 | 1 | deiTUNQAP01NS01DAMPERFR2-BDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
2671 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | TVD | FR2-BDP01 | 44 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20442 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20442 | 8 | 1 | deiTUNQAP01NS01DAMPERFR2-BDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
2672 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-63 | 45 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20451 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20451 | 0 | 2 | deiTUNQAP01SS01DAMPERCON-63Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2673 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-63 | 45 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20451 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20451 | 2 | 1 | deiTUNQAP01SS01DAMPERCON-63CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2674 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-63 | 45 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20451 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20451 | 4 | 1 | deiTUNQAP01SS01DAMPERCON-63TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2675 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-63 | 45 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20451 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20451 | 6 | 1 | deiTUNQAP01SS01DAMPERCON-63LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2676 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-54 | 46 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20461 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20461 | 0 | 2 | deiTUNQAP01NS01DAMPERCON-54Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2677 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-54 | 46 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20461 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20461 | 2 | 1 | deiTUNQAP01NS01DAMPERCON-54CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2678 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-54 | 46 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20461 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20461 | 4 | 1 | deiTUNQAP01NS01DAMPERCON-54TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2679 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-54 | 46 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20461 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20461 | 6 | 1 | deiTUNQAP01NS01DAMPERCON-54LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2680 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-66 | 47 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20471 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20471 | 0 | 2 | deiTUNQAP01SS01DAMPERCON-66Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2681 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-66 | 47 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20471 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20471 | 2 | 1 | deiTUNQAP01SS01DAMPERCON-66CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2682 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-66 | 47 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20471 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20471 | 4 | 1 | deiTUNQAP01SS01DAMPERCON-66TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2683 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-66 | 47 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20471 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20471 | 6 | 1 | deiTUNQAP01SS01DAMPERCON-66LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2684 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-61 | 48 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20481 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20481 | 0 | 2 | deiTUNQAP01SS01DAMPERCON-61Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2685 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-61 | 48 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20481 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20481 | 2 | 1 | deiTUNQAP01SS01DAMPERCON-61CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2686 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-61 | 48 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20481 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20481 | 4 | 1 | deiTUNQAP01SS01DAMPERCON-61TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2687 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-61 | 48 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20481 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20481 | 6 | 1 | deiTUNQAP01SS01DAMPERCON-61LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2688 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-56 | 49 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20491 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20491 | 0 | 2 | deiTUNQAP01NS01DAMPERCON-56Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2689 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-56 | 49 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20491 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20491 | 2 | 1 | deiTUNQAP01NS01DAMPERCON-56CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2690 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-56 | 49 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20491 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20491 | 4 | 1 | deiTUNQAP01NS01DAMPERCON-56TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2691 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-56 | 49 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20491 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20491 | 6 | 1 | deiTUNQAP01NS01DAMPERCON-56LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2692 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-51 | 50 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20501 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20501 | 0 | 2 | deiTUNQAP01NS01DAMPERCON-51Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2693 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-51 | 50 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20501 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20501 | 2 | 1 | deiTUNQAP01NS01DAMPERCON-51CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2694 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-51 | 50 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20501 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20501 | 4 | 1 | deiTUNQAP01NS01DAMPERCON-51TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2695 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-51 | 50 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20501 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20501 | 6 | 1 | deiTUNQAP01NS01DAMPERCON-51LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2696 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-67 | 51 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20511 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20511 | 0 | 2 | deiTUNQAP01SS01DAMPERCON-67Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2697 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-67 | 51 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20511 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20511 | 2 | 1 | deiTUNQAP01SS01DAMPERCON-67CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2698 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-67 | 51 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20511 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20511 | 4 | 1 | deiTUNQAP01SS01DAMPERCON-67TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2699 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-67 | 51 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20511 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20511 | 6 | 1 | deiTUNQAP01SS01DAMPERCON-67LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2700 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-59 | 52 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20521 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20521 | 0 | 2 | deiTUNQAP01SS01DAMPERCON-59Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2701 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-59 | 52 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20521 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20521 | 2 | 1 | deiTUNQAP01SS01DAMPERCON-59CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2702 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-59 | 52 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20521 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20521 | 4 | 1 | deiTUNQAP01SS01DAMPERCON-59TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2703 | QAP01_RTU | TUN:QAP01 | SS01:DAMPER | MSFD | CON-59 | 52 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20521 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20521 | 6 | 1 | deiTUNQAP01SS01DAMPERCON-59LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2704 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-58 | 53 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20531 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20531 | 0 | 2 | deiTUNQAP01NS01DAMPERCON-58Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2705 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-58 | 53 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20531 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20531 | 2 | 1 | deiTUNQAP01NS01DAMPERCON-58CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2706 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-58 | 53 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20531 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20531 | 4 | 1 | deiTUNQAP01NS01DAMPERCON-58TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2707 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-58 | 53 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20531 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20531 | 6 | 1 | deiTUNQAP01NS01DAMPERCON-58LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2708 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-52 | 54 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20541 | 0 | 2 | Check SWC Name |  | QAP01-SIL2_Monitoring |  | QAP01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20541 | 0 | 2 | deiTUNQAP01NS01DAMPERCON-52Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
2709 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-52 | 54 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20541 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20541 | 2 | 1 | deiTUNQAP01NS01DAMPERCON-52CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
2710 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-52 | 54 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20541 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20541 | 4 | 1 | deiTUNQAP01NS01DAMPERCON-52TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
2711 | QAP01_RTU | TUN:QAP01 | NS01:DAMPER | MSFD | CON-52 | 54 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20541 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20541 | 6 | 1 | deiTUNQAP01NS01DAMPERCON-52LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
2712 | QAP01_RTU | TUN:QAP01 | SS01:AHU | AHU | CON-08 | 55 | ControlMod | SIL0 | MODBUS:4:Read:Input Registers | 20551 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20551 | 0 | 1 | deiTUNQAP01SS01AHUCON-08ControlMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2713 | QAP01_RTU | TUN:QAP01 | SS01:AHU | AHU | CON-08 | 55 | RunStat | SIL0 | MODBUS:4:Read:Input Registers | 20551 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20551 | 1 | 1 | deiTUNQAP01SS01AHUCON-08RunStat | 4 |  |  | 0 | $ComStatus , , | #RUN
2714 | QAP01_RTU | TUN:QAP01 | SS01:AHU | AHU | CON-07 | 56 | ControlMod | SIL0 | MODBUS:4:Read:Input Registers | 20561 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20561 | 0 | 1 | deiTUNQAP01SS01AHUCON-07ControlMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2715 | QAP01_RTU | TUN:QAP01 | SS01:AHU | AHU | CON-07 | 56 | RunStat | SIL0 | MODBUS:4:Read:Input Registers | 20561 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20561 | 1 | 1 | deiTUNQAP01SS01AHUCON-07RunStat | 4 |  |  | 0 | $ComStatus , , | #RUN
2716 | QAP01_RTU | TUN:QAP01 | NS01:AHU | AHU | CON-06 | 57 | ControlMod | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 0 | 1 | deiTUNQAP01NS01AHUCON-06ControlMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2717 | QAP01_RTU | TUN:QAP01 | NS01:AHU | AHU | CON-06 | 57 | RunStat | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 1 | 1 | deiTUNQAP01NS01AHUCON-06RunStat | 4 |  |  | 0 | $ComStatus , , | #RUN
2718 | QAP01_RTU | TUN:QAP01 | NS01:AHU | AHU | CON-05 | 58 | ControlMod | SIL0 | MODBUS:4:Read:Input Registers | 20581 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20581 | 0 | 1 | deiTUNQAP01NS01AHUCON-05ControlMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2719 | QAP01_RTU | TUN:QAP01 | NS01:AHU | AHU | CON-05 | 58 | RunStat | SIL0 | MODBUS:4:Read:Input Registers | 20581 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20581 | 1 | 1 | deiTUNQAP01NS01AHUCON-05RunStat | 4 |  |  | 0 | $ComStatus , , | #RUN
2720 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Vac240SwOp | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 0 | 1 | deiTUNQAP01MMSSPLC01Vac240SwOp | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY DISCONNECTING SWITCH - OPEN
2721 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Vac240Volt | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 1 | 1 | deiTUNQAP01MMSSPLC01Vac240Volt | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY VOLTAGE PRESENCE
2722 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | VolOpen | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 2 | 1 | deiTUNQAP01MMSSPLC01VolOpen | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER OPEN
2723 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | VolFault | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 3 | 1 | deiTUNQAP01MMSSPLC01VolFault | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER FAULT
2724 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | VolSupOpen | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 4 | 1 | deiTUNQAP01MMSSPLC01VolSupOpen | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN
2725 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | VolSupFault | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 5 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 5 | 1 | deiTUNQAP01MMSSPLC01VolSupFault | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT
2726 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | CabOpen | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 6 | 1 | deiTUNQAP01MMSSPLC01CabOpen | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS OPEN
2727 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | CabFault | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 7 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 7 | 1 | deiTUNQAP01MMSSPLC01CabFault | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS FAULT
2728 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | SerOpen | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 8 | 1 | deiTUNQAP01MMSSPLC01SerOpen | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER OPEN
2729 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | SerFault | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 9 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 9 | 1 | deiTUNQAP01MMSSPLC01SerFault | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER FAULT
2730 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | UpsBreOpen | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 10 | 1 | deiTUNQAP01MMSSPLC01UpsBreOpen | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER OPEN
2731 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | UpsBreFault | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 11 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 11 | 1 | deiTUNQAP01MMSSPLC01UpsBreFault | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER FAULT
2732 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | UpsSwOpen | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 12 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 12 | 1 | deiTUNQAP01MMSSPLC01UpsSwOpen | 4 |  |  | 0 | $ComStatus , , | #UPS DISCONNECTING SWITCH OPEN
2733 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | UpsFault | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 13 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 13 | 1 | deiTUNQAP01MMSSPLC01UpsFault | 4 |  |  | 0 | $ComStatus , , | #UPS FAULT
2734 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Sup24Vdc1Open | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 14 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 14 | 1 | deiTUNQAP01MMSSPLC01Sup24Vdc1Open | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN
2735 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Sup24Vdc1Fault | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 15 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 15 | 1 | deiTUNQAP01MMSSPLC01Sup24Vdc1Fault | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT
2736 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Sup24Vdc1Volt | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 0 | 1 | deiTUNQAP01MMSSPLC01Sup24Vdc1Volt | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 ABSENCE OF VOLTAGE
2737 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Sup24Vdc2Open | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 1 | 1 | deiTUNQAP01MMSSPLC01Sup24Vdc2Open | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN
2738 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Sup24Vdc2Fault | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 2 | 1 | deiTUNQAP01MMSSPLC01Sup24Vdc2Fault | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT
2739 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Sup24Vdc2Volt | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 3 | 1 | deiTUNQAP01MMSSPLC01Sup24Vdc2Volt | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 ABSENCE OF VOLTAGE
2740 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | SwOpen | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 4 | 1 | deiTUNQAP01MMSSPLC01SwOpen | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER OPEN
2741 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | SwFault | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 5 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 5 | 1 | deiTUNQAP01MMSSPLC01SwFault | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER FAULT
2742 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | LcpOpen | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 6 | 1 | deiTUNQAP01MMSSPLC01LcpOpen | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER OPEN
2743 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | LcpFault | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 7 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 7 | 1 | deiTUNQAP01MMSSPLC01LcpFault | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER FAULT
2744 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Plc1Open | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 8 | 1 | deiTUNQAP01MMSSPLC01Plc1Open | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER OPEN
2745 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Plc1Fault | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 9 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 9 | 1 | deiTUNQAP01MMSSPLC01Plc1Fault | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER FAULT
2746 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Plc2Open | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 10 | 1 | deiTUNQAP01MMSSPLC01Plc2Open | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER OPEN
2747 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | Plc2Fault | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 11 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 11 | 1 | deiTUNQAP01MMSSPLC01Plc2Fault | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER FAULT
2748 | QAP01_RTU | TUN:QAP01 | MMS | SPLCMMS | SPLC01 | 59 | SuArTrig | SIL0 | MODBUS:4:Read:Input Registers | 20592 | 12 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20592 | 12 | 1 | deiTUNQAP01MMSSPLC01SuArTrig | 4 |  |  | 0 | $ComStatus , , | #SURGE ARRESTER TRIGGERED
2749 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mcsd1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 0 | 1 | deiTUNQAP01MMSLPS-MDB01Mcsd1Stat | 4 |  |  | 0 | $ComStatus , , | #Power normal MCSD 1 status
2750 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mcsd2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 1 | 1 | deiTUNQAP01MMSLPS-MDB01Mcsd2Stat | 4 |  |  | 0 | $ComStatus , , | #Power replacement MCSD 2 status
2751 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mcsd1pos | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 2 | 1 | deiTUNQAP01MMSLPS-MDB01Mcsd1pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 1 racked position
2752 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mcsd2pos | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 3 | 1 | deiTUNQAP01MMSLPS-MDB01Mcsd2pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 2 racked position
2753 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Change | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 4 | 1 | deiTUNQAP01MMSLPS-MDB01Change | 4 |  |  | 0 | $ComStatus , , | #Change over
2754 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | relay1 | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 5 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 5 | 1 | deiTUNQAP01MMSLPS-MDB01relay1 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 1
2755 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | relay2 | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 6 | 1 | deiTUNQAP01MMSLPS-MDB01relay2 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 2
2756 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 7 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 7 | 1 | deiTUNQAP01MMSLPS-MDB01Closed | 4 |  |  | 0 | $ComStatus , , | #MCB closed status
2757 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 8 | 1 | deiTUNQAP01MMSLPS-MDB01Trip | 4 |  |  | 0 | $ComStatus , , | #MCB tripped status
2758 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | PowerCut | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 9 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 9 | 1 | deiTUNQAP01MMSLPS-MDB01PowerCut | 4 |  |  | 0 | $ComStatus , , | #Emergency power cut (push button)
2759 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mccb1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 10 | 1 | deiTUNQAP01MMSLPS-MDB01Mccb1Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 status
2760 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 11 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 11 | 1 | deiTUNQAP01MMSLPS-MDB01Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 trip
2761 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mccb2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 12 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 12 | 1 | deiTUNQAP01MMSLPS-MDB01Mccb2Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 status
2762 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 13 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 13 | 1 | deiTUNQAP01MMSLPS-MDB01Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 trip
2763 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mccb3Stat | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 14 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 14 | 1 | deiTUNQAP01MMSLPS-MDB01Mccb3Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 status
2764 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB01 | 60 | Mccb3Trip | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 15 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 15 | 1 | deiTUNQAP01MMSLPS-MDB01Mccb3Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 trip
2765 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mcsd1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 0 | 1 | deiTUNQAP01MMSLPS-MDB02Mcsd1Stat | 4 |  |  | 0 | $ComStatus , , | #Power normal MCSD 1 status
2766 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mcsd2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 1 | 1 | deiTUNQAP01MMSLPS-MDB02Mcsd2Stat | 4 |  |  | 0 | $ComStatus , , | #Power replacement MCSD 2 status
2767 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mcsd1pos | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 2 | 1 | deiTUNQAP01MMSLPS-MDB02Mcsd1pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 1 racked position
2768 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mcsd2pos | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 3 | 1 | deiTUNQAP01MMSLPS-MDB02Mcsd2pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 2 racked position
2769 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Change | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 4 | 1 | deiTUNQAP01MMSLPS-MDB02Change | 4 |  |  | 0 | $ComStatus , , | #Change over
2770 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | relay1 | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 5 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 5 | 1 | deiTUNQAP01MMSLPS-MDB02relay1 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 1
2771 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | relay2 | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 6 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 6 | 1 | deiTUNQAP01MMSLPS-MDB02relay2 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 2
2772 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 7 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 7 | 1 | deiTUNQAP01MMSLPS-MDB02Closed | 4 |  |  | 0 | $ComStatus , , | #MCB closed status
2773 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 8 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 8 | 1 | deiTUNQAP01MMSLPS-MDB02Trip | 4 |  |  | 0 | $ComStatus , , | #MCB tripped status
2774 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | PowerCut | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 9 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 9 | 1 | deiTUNQAP01MMSLPS-MDB02PowerCut | 4 |  |  | 0 | $ComStatus , , | #Emergency power cut (push button)
2775 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mccb1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 10 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 10 | 1 | deiTUNQAP01MMSLPS-MDB02Mccb1Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 status
2776 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 11 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 11 | 1 | deiTUNQAP01MMSLPS-MDB02Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 trip
2777 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mccb2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 12 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 12 | 1 | deiTUNQAP01MMSLPS-MDB02Mccb2Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 status
2778 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 13 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 13 | 1 | deiTUNQAP01MMSLPS-MDB02Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 trip
2779 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mccb3Stat | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 14 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 14 | 1 | deiTUNQAP01MMSLPS-MDB02Mccb3Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 status
2780 | QAP01_RTU | TUN:QAP01 | MMS | MDB | LPS-MDB02 | 61 | Mccb3Trip | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 15 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 15 | 1 | deiTUNQAP01MMSLPS-MDB02Mccb3Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 trip
2781 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL1-IO01 | 62 | Relay | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 0 | 1 | deiTUNQAP01MMSEL1-IO01Relay | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay
2782 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL1-IO01 | 62 | Isolator | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 1 | 1 | deiTUNQAP01MMSEL1-IO01Isolator | 4 |  |  | 0 | $ComStatus , , | #LBS Main incomer isolator status
2783 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL1-IO01 | 62 | Supply | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 2 | 1 | deiTUNQAP01MMSEL1-IO01Supply | 4 |  |  | 0 | $ComStatus , , | #UPS supply status
2784 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL1-IO01 | 62 | Faulty | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 3 | 1 | deiTUNQAP01MMSEL1-IO01Faulty | 4 |  |  | 0 | $ComStatus , , | #UPS faulty
2785 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL1-IO01 | 62 | Power | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 4 | 1 | deiTUNQAP01MMSEL1-IO01Power | 4 |  |  | 0 | $ComStatus , , | #24VDC UPS power status
2786 | QAP01_RTU | TUN:QAP01 | MMS | MCCB | EL1-UPS | 63 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20631 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20631 | 0 | 1 | deiTUNQAP01MMSEL1-UPSTrip | 4 |  |  | 0 | $ComStatus , , | #MCCB trip status
2787 | QAP01_RTU | TUN:QAP01 | MMS | MCCB | EL1-UPS | 63 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20631 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20631 | 1 | 1 | deiTUNQAP01MMSEL1-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #MCCB closed status
2788 | QAP01_RTU | TUN:QAP01 | MMS | LBS | EL1-UPS | 64 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 0 | 1 | deiTUNQAP01MMSEL1-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #LBS closed status
2789 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL1-VSD01 | 65 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 0 | 1 | deiTUNQAP01MMSUPS_EL1-VSD01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2790 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL1-VSD01 | 65 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 1 | 1 | deiTUNQAP01MMSUPS_EL1-VSD01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2791 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL1-VSD02 | 66 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20661 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20661 | 0 | 1 | deiTUNQAP01MMSUPS_EL1-VSD02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2792 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL1-VSD02 | 66 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20661 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20661 | 1 | 1 | deiTUNQAP01MMSUPS_EL1-VSD02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2793 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT3-IDP01 | 67 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 0 | 1 | deiTUNQAP01MMS3P-VT3-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2794 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT3-IDP01 | 67 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 1 | 1 | deiTUNQAP01MMS3P-VT3-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2795 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT3-IDP01 | 68 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20681 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20681 | 0 | 1 | deiTUNQAP01MMS2P-VT3-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2796 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT3-IDP01 | 68 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20681 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20681 | 1 | 1 | deiTUNQAP01MMS2P-VT3-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2797 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT4-IDP01 | 69 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20691 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20691 | 0 | 1 | deiTUNQAP01MMS3P-VT4-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2798 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT4-IDP01 | 69 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20691 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20691 | 1 | 1 | deiTUNQAP01MMS3P-VT4-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2799 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT4-IDP01 | 70 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20701 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20701 | 0 | 1 | deiTUNQAP01MMS2P-VT4-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2800 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT4-IDP01 | 70 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20701 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20701 | 1 | 1 | deiTUNQAP01MMS2P-VT4-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2801 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-01 | 71 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20711 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20711 | 0 | 1 | deiTUNQAP01MMS3P-VT6-TDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2802 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-01 | 71 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20711 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20711 | 1 | 1 | deiTUNQAP01MMS3P-VT6-TDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2803 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-01 | 72 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20721 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20721 | 0 | 1 | deiTUNQAP01MMS2P-VT6-TDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2804 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-01 | 72 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20721 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20721 | 1 | 1 | deiTUNQAP01MMS2P-VT6-TDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2805 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-02 | 73 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20731 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20731 | 0 | 1 | deiTUNQAP01MMS3P-VT6-TDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2806 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-02 | 73 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20731 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20731 | 1 | 1 | deiTUNQAP01MMS3P-VT6-TDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2807 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-02 | 74 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 0 | 1 | deiTUNQAP01MMS2P-VT6-TDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2808 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-02 | 74 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 1 | 1 | deiTUNQAP01MMS2P-VT6-TDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2809 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-03 | 75 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 0 | 1 | deiTUNQAP01MMS3P-VT6-TDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2810 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT6-TDP01-03 | 75 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 1 | 1 | deiTUNQAP01MMS3P-VT6-TDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2811 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-03 | 76 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 0 | 1 | deiTUNQAP01MMS2P-VT6-TDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2812 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT6-TDP01-03 | 76 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 1 | 1 | deiTUNQAP01MMS2P-VT6-TDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2813 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P--FR2-BDP01-01 | 77 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20771 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20771 | 0 | 1 | deiTUNQAP01MMS3P--FR2-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2814 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P--FR2-BDP01-01 | 77 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20771 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20771 | 1 | 1 | deiTUNQAP01MMS3P--FR2-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2815 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P--FR2-BDP01-01 | 78 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20781 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20781 | 0 | 1 | deiTUNQAP01MMS2P--FR2-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2816 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P--FR2-BDP01-01 | 78 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20781 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20781 | 1 | 1 | deiTUNQAP01MMS2P--FR2-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2817 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P--FR2-BDP01-02 | 79 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20791 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20791 | 0 | 1 | deiTUNQAP01MMS3P--FR2-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2818 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P--FR2-BDP01-02 | 79 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20791 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20791 | 1 | 1 | deiTUNQAP01MMS3P--FR2-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2819 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P--FR2-BDP01-02 | 80 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20801 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20801 | 0 | 1 | deiTUNQAP01MMS2P--FR2-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2820 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P--FR2-BDP01-02 | 80 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20801 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20801 | 1 | 1 | deiTUNQAP01MMS2P--FR2-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2821 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-54 | 81 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20811 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20811 | 0 | 1 | deiTUNQAP01MMSMSFD-CON-54McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2822 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-54 | 81 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20811 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20811 | 1 | 1 | deiTUNQAP01MMSMSFD-CON-54McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2823 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-52 | 82 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20821 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20821 | 0 | 1 | deiTUNQAP01MMSMSFD-CON-52McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2824 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-52 | 82 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20821 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20821 | 1 | 1 | deiTUNQAP01MMSMSFD-CON-52McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2825 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-58 | 83 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20831 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20831 | 0 | 1 | deiTUNQAP01MMSMSFD-CON-58McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2826 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-58 | 83 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20831 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20831 | 1 | 1 | deiTUNQAP01MMSMSFD-CON-58McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2827 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL2-IO01 | 84 | Relay | SIL0 | MODBUS:4:Read:Input Registers | 20841 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20841 | 0 | 1 | deiTUNQAP01MMSEL2-IO01Relay | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay
2828 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL2-IO01 | 84 | Isolator | SIL0 | MODBUS:4:Read:Input Registers | 20841 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20841 | 1 | 1 | deiTUNQAP01MMSEL2-IO01Isolator | 4 |  |  | 0 | $ComStatus , , | #LBS Main incomer isolator status
2829 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL2-IO01 | 84 | Supply | SIL0 | MODBUS:4:Read:Input Registers | 20841 | 2 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20841 | 2 | 1 | deiTUNQAP01MMSEL2-IO01Supply | 4 |  |  | 0 | $ComStatus , , | #UPS supply status
2830 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL2-IO01 | 84 | Faulty | SIL0 | MODBUS:4:Read:Input Registers | 20841 | 3 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20841 | 3 | 1 | deiTUNQAP01MMSEL2-IO01Faulty | 4 |  |  | 0 | $ComStatus , , | #UPS faulty
2831 | QAP01_RTU | TUN:QAP01 | MMS | EL | EL2-IO01 | 84 | Power | SIL0 | MODBUS:4:Read:Input Registers | 20841 | 4 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20841 | 4 | 1 | deiTUNQAP01MMSEL2-IO01Power | 4 |  |  | 0 | $ComStatus , , | #24VDC UPS power status
2832 | QAP01_RTU | TUN:QAP01 | MMS | MCCB | EL2-UPS | 85 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20851 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20851 | 0 | 1 | deiTUNQAP01MMSEL2-UPSTrip | 4 |  |  | 0 | $ComStatus , , | #MCCB trip status
2833 | QAP01_RTU | TUN:QAP01 | MMS | MCCB | EL2-UPS | 85 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20851 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20851 | 1 | 1 | deiTUNQAP01MMSEL2-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #MCCB closed status
2834 | QAP01_RTU | TUN:QAP01 | MMS | LBS | EL2-UPS | 86 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20861 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20861 | 0 | 1 | deiTUNQAP01MMSEL2-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #LBS closed status
2835 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL2-VSD01 | 87 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20871 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20871 | 0 | 1 | deiTUNQAP01MMSUPS_EL2-VSD01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2836 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL2-VSD01 | 87 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20871 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20871 | 1 | 1 | deiTUNQAP01MMSUPS_EL2-VSD01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2837 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL2-VSD02 | 88 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20881 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20881 | 0 | 1 | deiTUNQAP01MMSUPS_EL2-VSD02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2838 | QAP01_RTU | TUN:QAP01 | MMS | MCB | UPS_EL2-VSD02 | 88 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20881 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20881 | 1 | 1 | deiTUNQAP01MMSUPS_EL2-VSD02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2839 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT1-IDP01 | 89 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20891 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20891 | 0 | 1 | deiTUNQAP01MMS3P-VT1-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2840 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT1-IDP01 | 89 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20891 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20891 | 1 | 1 | deiTUNQAP01MMS3P-VT1-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2841 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT1-IDP01 | 90 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20901 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20901 | 0 | 1 | deiTUNQAP01MMS2P-VT1-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2842 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT1-IDP01 | 90 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20901 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20901 | 1 | 1 | deiTUNQAP01MMS2P-VT1-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2843 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT2-IDP01 | 91 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20911 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20911 | 0 | 1 | deiTUNQAP01MMS3P-VT2-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2844 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT2-IDP01 | 91 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20911 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20911 | 1 | 1 | deiTUNQAP01MMS3P-VT2-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2845 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT2-IDP01 | 92 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20921 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20921 | 0 | 1 | deiTUNQAP01MMS2P-VT2-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2846 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT2-IDP01 | 92 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20921 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20921 | 1 | 1 | deiTUNQAP01MMS2P-VT2-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2847 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-01 | 93 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20931 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20931 | 0 | 1 | deiTUNQAP01MMS3P-VT5-TDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2848 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-01 | 93 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20931 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20931 | 1 | 1 | deiTUNQAP01MMS3P-VT5-TDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2849 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-01 | 94 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20941 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20941 | 0 | 1 | deiTUNQAP01MMS2P-VT5-TDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2850 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-01 | 94 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20941 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20941 | 1 | 1 | deiTUNQAP01MMS2P-VT5-TDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2851 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-02 | 95 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20951 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20951 | 0 | 1 | deiTUNQAP01MMS3P-VT5-TDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2852 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-02 | 95 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20951 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20951 | 1 | 1 | deiTUNQAP01MMS3P-VT5-TDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2853 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-02 | 96 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20961 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20961 | 0 | 1 | deiTUNQAP01MMS2P-VT5-TDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2854 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-02 | 96 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20961 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20961 | 1 | 1 | deiTUNQAP01MMS2P-VT5-TDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2855 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-03 | 97 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20971 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20971 | 0 | 1 | deiTUNQAP01MMS3P-VT5-TDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2856 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-VT5-TDP01-03 | 97 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20971 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20971 | 1 | 1 | deiTUNQAP01MMS3P-VT5-TDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2857 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-03 | 98 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20981 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20981 | 0 | 1 | deiTUNQAP01MMS2P-VT5-TDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2858 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-VT5-TDP01-03 | 98 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20981 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20981 | 1 | 1 | deiTUNQAP01MMS2P-VT5-TDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2859 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-FR1-BDP01-01 | 99 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20991 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20991 | 0 | 1 | deiTUNQAP01MMS3P-FR1-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2860 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-FR1-BDP01-01 | 99 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20991 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20991 | 1 | 1 | deiTUNQAP01MMS3P-FR1-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2861 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-FR1-BDP01-01 | 100 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21001 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21001 | 0 | 1 | deiTUNQAP01MMS2P-FR1-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2862 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-FR1-BDP01-01 | 100 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21001 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21001 | 1 | 1 | deiTUNQAP01MMS2P-FR1-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2863 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-FR1-BDP01-02 | 101 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21011 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21011 | 0 | 1 | deiTUNQAP01MMS3P-FR1-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2864 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 3P-FR1-BDP01-02 | 101 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21011 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21011 | 1 | 1 | deiTUNQAP01MMS3P-FR1-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2865 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-FR1-BDP01-02 | 102 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21021 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21021 | 0 | 1 | deiTUNQAP01MMS2P-FR1-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2866 | QAP01_RTU | TUN:QAP01 | MMS | MCB | 2P-FR1-BDP01-02 | 102 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21021 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21021 | 1 | 1 | deiTUNQAP01MMS2P-FR1-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2867 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-63 | 103 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21031 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21031 | 0 | 1 | deiTUNQAP01MMSMSFD-CON-63McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2868 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-63 | 103 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21031 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21031 | 1 | 1 | deiTUNQAP01MMSMSFD-CON-63McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2869 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-59 | 104 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21041 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21041 | 0 | 1 | deiTUNQAP01MMSMSFD-CON-59McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2870 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-59 | 104 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21041 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21041 | 1 | 1 | deiTUNQAP01MMSMSFD-CON-59McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2871 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-67 | 105 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21051 | 0 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21051 | 0 | 1 | deiTUNQAP01MMSMSFD-CON-67McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
2872 | QAP01_RTU | TUN:QAP01 | MMS | MCB | MSFD-CON-67 | 105 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21051 | 1 | 1 | Check SWC Name |  | QAP01-SIL0 |  | QAP01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21051 | 1 | 1 | deiTUNQAP01MMSMSFD-CON-67McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
2873 | QEC01_RTU | TUN:QEC01 | SCR | LCP | LCP01 | 1 | ComFaultPlc | SIL0 | MODBUS:4:Read:Input Registers | 20011 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20011 | 0 | 1 | deiTUNQEC01SCRLCP01ComFaultPlc | 4 |  |  | 0 | $ComStatus , , | #COMMUNICATION FAULT WITH PLC
2874 | QEC01_RTU | TUN:QEC01 | SCR | LCP | LCP01 | 1 | LcpMode | SIL0 | MODBUS:4:Read:Input Registers | 20011 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20011 | 1 | 1 | deiTUNQEC01SCRLCP01LcpMode | 4 |  |  | 0 | $ComStatus , , | #LOCAL / REMOTE STATUS
2875 | QEC01_RTU | TUN:QEC01 | SCR | FMOP | FMOP01 | 2 | EmergNod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20021 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20021 | 0 | 1 | deiTUNQEC01SCRFMOP01EmergNod | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
2876 | QEC01_RTU | TUN:QEC01 | SCR | FMOP | FMOP01 | 2 | RightStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20021 | 1 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20021 | 1 | 1 | deiTUNQEC01SCRFMOP01RightStat | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
2877 | QEC01_RTU | TUN:QEC01 | SCR | FMOP | FMOP01 | 2 | LeftStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20021 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20021 | 2 | 1 | deiTUNQEC01SCRFMOP01LeftStat | 4 |  |  | 0 | $ComStatus , , | #ACTIVE / INACTIVE STATUS
2878 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 3 | PlcState | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 0 | 1 | deiTUNQEC01TELPLC01PlcState | 4 |  |  | 0 | $ComStatus , , | #PLC A/B OFFLINE
2879 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 3 | OpStatus | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 1 | 1 | deiTUNQEC01TELPLC01OpStatus | 4 |  |  | 0 | $ComStatus , , | #PLC RUNNING.
2880 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 3 | PwStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 2 | 1 | deiTUNQEC01TELPLC01PwStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: POWER SUPPLY FAULT
2881 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 3 | CpuStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 3 | 1 | deiTUNQEC01TELPLC01CpuStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CPU MODULE FAULT
2882 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 3 | CrpStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 4 | 1 | deiTUNQEC01TELPLC01CrpStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CRP MODULE FAULT
2883 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 3 | CraStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 5 | 1 | deiTUNQEC01TELPLC01CraStat | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
2884 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 3 | NrpStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 6 | 1 | deiTUNQEC01TELPLC01NrpStat | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
2885 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 3 | ComStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 7 | 1 | deiTUNQEC01TELPLC01ComStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
2886 | QEC01_RTU | TUN:QEC01 | TEL | SPLC | PLC01 | 3 | IoStat | SIL0 | MODBUS:4:Read:Input Registers | 20031 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20031 | 8 | 1 | deiTUNQEC01TELPLC01IoStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
2887 | QEC01_RTU | TUN:QEC01 | TEL | SWI | SWI01 | 4 | SwStat | SIL0 | MODBUS:4:Read:Input Registers | 20041 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20041 | 0 | 1 | deiTUNQEC01TELSWI01SwStat | 4 |  |  | 0 | $ComStatus , , | #SWITCH FAULT
2888 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20051 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20051 | 0 | 1 | deiTUNQEC01SS01PFAPLA-01ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2889 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20051 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20051 | 2 | 1 | deiTUNQEC01SS01PFAPLA-01OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2890 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20051 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20051 | 4 | 1 | deiTUNQEC01SS01PFAPLA-01AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
2891 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | CmdManSel | SIL0 | MODBUS:16:Write:Holding Registers | 10101 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10101 | 0 | 1 | deoTUNQEC01SS01PFAPLA-01CmdManSel | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2892 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10102 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10102 | 0 | 1 | deoTUNQEC01SS01PFAPLA-01CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2893 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 6 | 2 | deiTUNQEC01SS01PFAPLA-01AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2894 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10103 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10103 | 0 | 1 | deoTUNQEC01SS01PFAPLA-01CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2895 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 8 | 2 | deiTUNQEC01SS01PFAPLA-01AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2896 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10104 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10104 | 0 | 1 | deoTUNQEC01SS01PFAPLA-01CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2897 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 10 | 2 | deiTUNQEC01SS01PFAPLA-01AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2898 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10105 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10105 | 0 | 1 | deoTUNQEC01SS01PFAPLA-01CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2899 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 12 | 2 | deiTUNQEC01SS01PFAPLA-01AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2900 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10106 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10106 | 0 | 1 | deoTUNQEC01SS01PFAPLA-01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2901 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20051 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20051 | 14 | 2 | deiTUNQEC01SS01PFAPLA-01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2902 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10107 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10107 | 0 | 1 | deoTUNQEC01SS01PFAPLA-01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2903 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20052 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20052 | 0 | 2 | deiTUNQEC01SS01PFAPLA-01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2904 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20052 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20052 | 2 | 1 | deiTUNQEC01SS01PFAPLA-01StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2905 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | PLA-01 | 5 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20052 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20052 | 4 | 1 | deiTUNQEC01SS01PFAPLA-01StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2906 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20061 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20061 | 0 | 1 | deiTUNQEC01SS01PFAGRD-01ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2907 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20061 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20061 | 2 | 1 | deiTUNQEC01SS01PFAGRD-01OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2908 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20061 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20061 | 4 | 1 | deiTUNQEC01SS01PFAGRD-01AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
2909 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | CmdManSel | SIL0 | MODBUS:16:Write:Holding Registers | 10121 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10121 | 0 | 1 | deoTUNQEC01SS01PFAGRD-01CmdManSel | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2910 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10122 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10122 | 0 | 1 | deoTUNQEC01SS01PFAGRD-01CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2911 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 6 | 2 | deiTUNQEC01SS01PFAGRD-01AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2912 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10123 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10123 | 0 | 1 | deoTUNQEC01SS01PFAGRD-01CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2913 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 8 | 2 | deiTUNQEC01SS01PFAGRD-01AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2914 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10124 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10124 | 0 | 1 | deoTUNQEC01SS01PFAGRD-01CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2915 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 10 | 2 | deiTUNQEC01SS01PFAGRD-01AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2916 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10125 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10125 | 0 | 1 | deoTUNQEC01SS01PFAGRD-01CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2917 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 12 | 2 | deiTUNQEC01SS01PFAGRD-01AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2918 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10126 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10126 | 0 | 1 | deoTUNQEC01SS01PFAGRD-01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2919 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20061 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20061 | 14 | 2 | deiTUNQEC01SS01PFAGRD-01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2920 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10127 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10127 | 0 | 1 | deoTUNQEC01SS01PFAGRD-01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2921 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20062 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20062 | 0 | 2 | deiTUNQEC01SS01PFAGRD-01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2922 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20062 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20062 | 2 | 1 | deiTUNQEC01SS01PFAGRD-01StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2923 | QEC01_RTU | TUN:QEC01 | SS01:PFA | PFA | GRD-01 | 6 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20062 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20062 | 4 | 1 | deiTUNQEC01SS01PFAGRD-01StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2924 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20071 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20071 | 0 | 1 | deiTUNQEC01NS01PFAPLA-02ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2925 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20071 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20071 | 2 | 1 | deiTUNQEC01NS01PFAPLA-02OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2926 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20071 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20071 | 4 | 1 | deiTUNQEC01NS01PFAPLA-02AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
2927 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | CmdManSel | SIL0 | MODBUS:16:Write:Holding Registers | 10141 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10141 | 0 | 1 | deoTUNQEC01NS01PFAPLA-02CmdManSel | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2928 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10142 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10142 | 0 | 1 | deoTUNQEC01NS01PFAPLA-02CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2929 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 6 | 2 | deiTUNQEC01NS01PFAPLA-02AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2930 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10143 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10143 | 0 | 1 | deoTUNQEC01NS01PFAPLA-02CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2931 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 8 | 2 | deiTUNQEC01NS01PFAPLA-02AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2932 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10144 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10144 | 0 | 1 | deoTUNQEC01NS01PFAPLA-02CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2933 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 10 | 2 | deiTUNQEC01NS01PFAPLA-02AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2934 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10145 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10145 | 0 | 1 | deoTUNQEC01NS01PFAPLA-02CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2935 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 12 | 2 | deiTUNQEC01NS01PFAPLA-02AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2936 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10146 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10146 | 0 | 1 | deoTUNQEC01NS01PFAPLA-02CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2937 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20071 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20071 | 14 | 2 | deiTUNQEC01NS01PFAPLA-02AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2938 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10147 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10147 | 0 | 1 | deoTUNQEC01NS01PFAPLA-02CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2939 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20072 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20072 | 0 | 2 | deiTUNQEC01NS01PFAPLA-02AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2940 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20072 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20072 | 2 | 1 | deiTUNQEC01NS01PFAPLA-02StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2941 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | PLA-02 | 7 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20072 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20072 | 4 | 1 | deiTUNQEC01NS01PFAPLA-02StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2942 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20081 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20081 | 0 | 1 | deiTUNQEC01NS01PFACON-04ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2943 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20081 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20081 | 2 | 1 | deiTUNQEC01NS01PFACON-04OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2944 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20081 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20081 | 4 | 1 | deiTUNQEC01NS01PFACON-04AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
2945 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | CmdManSel | SIL0 | MODBUS:16:Write:Holding Registers | 10161 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10161 | 0 | 1 | deoTUNQEC01NS01PFACON-04CmdManSel | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2946 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10162 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10162 | 0 | 1 | deoTUNQEC01NS01PFACON-04CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2947 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 6 | 2 | deiTUNQEC01NS01PFACON-04AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2948 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10163 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10163 | 0 | 1 | deoTUNQEC01NS01PFACON-04CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2949 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 8 | 2 | deiTUNQEC01NS01PFACON-04AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2950 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10164 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10164 | 0 | 1 | deoTUNQEC01NS01PFACON-04CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2951 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 10 | 2 | deiTUNQEC01NS01PFACON-04AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2952 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10165 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10165 | 0 | 1 | deoTUNQEC01NS01PFACON-04CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2953 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 12 | 2 | deiTUNQEC01NS01PFACON-04AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2954 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10166 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10166 | 0 | 1 | deoTUNQEC01NS01PFACON-04CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2955 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20081 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20081 | 14 | 2 | deiTUNQEC01NS01PFACON-04AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2956 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10167 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10167 | 0 | 1 | deoTUNQEC01NS01PFACON-04CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2957 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20082 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20082 | 0 | 2 | deiTUNQEC01NS01PFACON-04AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2958 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20082 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20082 | 2 | 1 | deiTUNQEC01NS01PFACON-04StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2959 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-04 | 8 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20082 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20082 | 4 | 1 | deiTUNQEC01NS01PFACON-04StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2960 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20091 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20091 | 0 | 1 | deiTUNQEC01NS01PFACON-03ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2961 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20091 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20091 | 2 | 1 | deiTUNQEC01NS01PFACON-03OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2962 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20091 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20091 | 4 | 1 | deiTUNQEC01NS01PFACON-03AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
2963 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | CmdManSel | SIL0 | MODBUS:16:Write:Holding Registers | 10181 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10181 | 0 | 1 | deoTUNQEC01NS01PFACON-03CmdManSel | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2964 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10182 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10182 | 0 | 1 | deoTUNQEC01NS01PFACON-03CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2965 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 6 | 2 | deiTUNQEC01NS01PFACON-03AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2966 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10183 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10183 | 0 | 1 | deoTUNQEC01NS01PFACON-03CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2967 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 8 | 2 | deiTUNQEC01NS01PFACON-03AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2968 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10184 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10184 | 0 | 1 | deoTUNQEC01NS01PFACON-03CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2969 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 10 | 2 | deiTUNQEC01NS01PFACON-03AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2970 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10185 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10185 | 0 | 1 | deoTUNQEC01NS01PFACON-03CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2971 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 12 | 2 | deiTUNQEC01NS01PFACON-03AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2972 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10186 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10186 | 0 | 1 | deoTUNQEC01NS01PFACON-03CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2973 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20091 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20091 | 14 | 2 | deiTUNQEC01NS01PFACON-03AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2974 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10187 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10187 | 0 | 1 | deoTUNQEC01NS01PFACON-03CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2975 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20092 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20092 | 0 | 2 | deiTUNQEC01NS01PFACON-03AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2976 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20092 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20092 | 2 | 1 | deiTUNQEC01NS01PFACON-03StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2977 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | CON-03 | 9 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20092 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20092 | 4 | 1 | deiTUNQEC01NS01PFACON-03StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2978 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | ControlMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20101 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20101 | 0 | 1 | deiTUNQEC01NS01PFAGRD-03ControlMod | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
2979 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | OpMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20101 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20101 | 2 | 1 | deiTUNQEC01NS01PFAGRD-03OpMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
2980 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | AutoCom | SIL0 | MODBUS:4:Read:Input Registers | 20101 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20101 | 4 | 1 | deiTUNQEC01NS01PFAGRD-03AutoCom | 4 |  |  | 0 | $ComStatus , , | #RUN
2981 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | CmdManSel | SIL0 | MODBUS:16:Write:Holding Registers | 10201 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10201 | 0 | 1 | deoTUNQEC01NS01PFAGRD-03CmdManSel | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
2982 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10202 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10202 | 0 | 1 | deoTUNQEC01NS01PFAGRD-03CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
2983 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 6 | 2 | deiTUNQEC01NS01PFAGRD-03AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
2984 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10203 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10203 | 0 | 1 | deoTUNQEC01NS01PFAGRD-03CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
2985 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 8 | 2 | deiTUNQEC01NS01PFAGRD-03AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
2986 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | CmdSelRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10204 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10204 | 0 | 1 | deoTUNQEC01NS01PFAGRD-03CmdSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT
2987 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | AckSelRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 10 | 2 | deiTUNQEC01NS01PFAGRD-03AckSelRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER SELECT ACK
2988 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | CmdExeRun | SIL2_Control | MODBUS:16:Write:Holding Registers | 10205 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10205 | 0 | 1 | deoTUNQEC01NS01PFAGRD-03CmdExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE
2989 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | AckExeRun | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 12 | 2 | deiTUNQEC01NS01PFAGRD-03AckExeRun | 4 |  |  | 0 | $ComStatus , , | #RUN ORDER EXECUTE ACK
2990 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10206 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10206 | 0 | 1 | deoTUNQEC01NS01PFAGRD-03CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
2991 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20101 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20101 | 14 | 2 | deiTUNQEC01NS01PFAGRD-03AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
2992 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10207 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10207 | 0 | 1 | deoTUNQEC01NS01PFAGRD-03CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
2993 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20102 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20102 | 0 | 2 | deiTUNQEC01NS01PFAGRD-03AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
2994 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | StartMis | SIL0 | MODBUS:4:Read:Input Registers | 20102 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20102 | 2 | 1 | deiTUNQEC01NS01PFAGRD-03StartMis | 4 |  |  | 0 | $ComStatus , , | #START MISMATCH
2995 | QEC01_RTU | TUN:QEC01 | NS01:PFA | PFA | GRD-03 | 10 | StopMis | SIL0 | MODBUS:4:Read:Input Registers | 20102 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20102 | 4 | 1 | deiTUNQEC01NS01PFAGRD-03StopMis | 4 |  |  | 0 | $ComStatus , , | #STOP MISMATCH
2996 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC01 | 11 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20111 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20111 | 0 | 1 | deiTUNQEC01SMCSMC01State | 4 |  |  | 0 | $ComStatus , , | #STATE
2997 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC02 | 12 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20121 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20121 | 0 | 1 | deiTUNQEC01SMCSMC02State | 4 |  |  | 0 | $ComStatus , , | #STATE
2998 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC03 | 13 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20131 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20131 | 0 | 1 | deiTUNQEC01SMCSMC03State | 4 |  |  | 0 | $ComStatus , , | #STATE
2999 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC04 | 14 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20141 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20141 | 0 | 1 | deiTUNQEC01SMCSMC04State | 4 |  |  | 0 | $ComStatus , , | #STATE
3000 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC05 | 15 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20151 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20151 | 0 | 1 | deiTUNQEC01SMCSMC05State | 4 |  |  | 0 | $ComStatus , , | #STATE
3001 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC06 | 16 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20161 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20161 | 0 | 1 | deiTUNQEC01SMCSMC06State | 4 |  |  | 0 | $ComStatus , , | #STATE
3002 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC07 | 17 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20171 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20171 | 0 | 1 | deiTUNQEC01SMCSMC07State | 4 |  |  | 0 | $ComStatus , , | #STATE
3003 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC08 | 18 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20181 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20181 | 0 | 1 | deiTUNQEC01SMCSMC08State | 4 |  |  | 0 | $ComStatus , , | #STATE
3004 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC09 | 19 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20191 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20191 | 0 | 1 | deiTUNQEC01SMCSMC09State | 4 |  |  | 0 | $ComStatus , , | #STATE
3005 | QEC01_RTU | TUN:QEC01 | SMC | SMC | SMC10 | 20 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20201 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20201 | 0 | 1 | deiTUNQEC01SMCSMC10State | 4 |  |  | 0 | $ComStatus , , | #STATE
3006 | QEC01_RTU | TUN:QEC01 | SED | SED | SED01 | 21 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20211 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20211 | 0 | 1 | deiTUNQEC01SEDSED01State | 4 |  |  | 0 | $ComStatus , , | #STATE
3007 | QEC01_RTU | TUN:QEC01 | SED | SED | SED01 | 21 | Open | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20211 | 1 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20211 | 1 | 1 | deiTUNQEC01SEDSED01Open | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
3008 | QEC01_RTU | TUN:QEC01 | SED | SED | SED02 | 22 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20221 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20221 | 0 | 1 | deiTUNQEC01SEDSED02State | 4 |  |  | 0 | $ComStatus , , | #STATE
3009 | QEC01_RTU | TUN:QEC01 | SED | SED | SED02 | 22 | Open | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20221 | 1 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20221 | 1 | 1 | deiTUNQEC01SEDSED02Open | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
3010 | QEC01_RTU | TUN:QEC01 | SED | SED | SED03 | 23 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20231 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20231 | 0 | 1 | deiTUNQEC01SEDSED03State | 4 |  |  | 0 | $ComStatus , , | #STATE
3011 | QEC01_RTU | TUN:QEC01 | SED | SED | SED03 | 23 | Open | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20231 | 1 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20231 | 1 | 1 | deiTUNQEC01SEDSED03Open | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
3012 | QEC01_RTU | TUN:QEC01 | SED | SED | SED04 | 24 | State | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20241 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20241 | 0 | 1 | deiTUNQEC01SEDSED04State | 4 |  |  | 0 | $ComStatus , , | #STATE
3013 | QEC01_RTU | TUN:QEC01 | SED | SED | SED04 | 24 | Open | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20241 | 1 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20241 | 1 | 1 | deiTUNQEC01SEDSED04Open | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SENT BY TVS
3014 | QEC01_RTU | TUN:QEC01 | OTS | OTS | OTS001 | 25 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20251 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20251 | 0 | 1 | deiTUNQEC01OTSOTS001AvailStat | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3015 | QEC01_RTU | TUN:QEC01 | OTS | OTS | OTS001 | 25 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20251 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20251 | 2 | 1 | deiTUNQEC01OTSOTS001AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3016 | QEC01_RTU | TUN:QEC01 | OTS | OTS | OTS001 | 25 | TemMeasure | SIL0 | MODBUS:4:Read:Input Registers | 20252 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20252 | 0 | 32 | aeiTUNQEC01OTSOTS001TemMeasure | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3017 | QEC01_RTU | TUN:QEC01 | OTS | OTS | OTS002 | 26 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20261 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20261 | 0 | 1 | deiTUNQEC01OTSOTS002AvailStat | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3018 | QEC01_RTU | TUN:QEC01 | OTS | OTS | OTS002 | 26 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20261 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20261 | 2 | 1 | deiTUNQEC01OTSOTS002AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3019 | QEC01_RTU | TUN:QEC01 | OTS | OTS | OTS002 | 26 | TemMeasure | SIL0 | MODBUS:4:Read:Input Registers | 20262 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20262 | 0 | 32 | aeiTUNQEC01OTSOTS002TemMeasure | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3020 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20271 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20271 | 0 | 2 | deiTUNQEC01SS01TVFVT1-TVF01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3021 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20271 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20271 | 2 | 1 | deiTUNQEC01SS01TVFVT1-TVF01OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3022 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20271 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20271 | 4 | 2 | deiTUNQEC01SS01TVFVT1-TVF01RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3023 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 10541 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10541 | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3024 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10542 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10542 | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3025 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20271 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20271 | 6 | 2 | deiTUNQEC01SS01TVFVT1-TVF01AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3026 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10543 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10543 | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3027 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20271 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20271 | 8 | 2 | deiTUNQEC01SS01TVFVT1-TVF01AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3028 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20271 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20271 | 10 | 1 | deiTUNQEC01SS01TVFVT1-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3029 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20271 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20271 | 12 | 1 | deiTUNQEC01SS01TVFVT1-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3030 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20271 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20271 | 14 | 1 | deiTUNQEC01SS01TVFVT1-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3031 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20272 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20272 | 0 | 32 | aeiTUNQEC01SS01TVFVT1-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3032 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10544 | 0 | 2 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10544 | 0 | 2 | deoTUNQEC01SS01TVFVT1-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3033 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10545 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10545 | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3034 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 0 | 2 | deiTUNQEC01SS01TVFVT1-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3035 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10546 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10546 | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3036 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 2 | 2 | deiTUNQEC01SS01TVFVT1-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3037 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10547 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10547 | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3038 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 4 | 2 | deiTUNQEC01SS01TVFVT1-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3039 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10548 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10548 | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3040 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 6 | 2 | deiTUNQEC01SS01TVFVT1-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3041 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10549 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10549 | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3042 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 8 | 2 | deiTUNQEC01SS01TVFVT1-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3043 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10550 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10550 | 0 | 1 | deoTUNQEC01SS01TVFVT1-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3044 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20274 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20274 | 10 | 2 | deiTUNQEC01SS01TVFVT1-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3045 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20274 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20274 | 12 | 1 | deiTUNQEC01SS01TVFVT1-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3046 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20274 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20274 | 14 | 1 | deiTUNQEC01SS01TVFVT1-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3047 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 0 | 1 | deiTUNQEC01SS01TVFVT1-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3048 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 1 | 1 | deiTUNQEC01SS01TVFVT1-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3049 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 2 | 1 | deiTUNQEC01SS01TVFVT1-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3050 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 3 | 1 | deiTUNQEC01SS01TVFVT1-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3051 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 4 | 1 | deiTUNQEC01SS01TVFVT1-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3052 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 5 | 1 | deiTUNQEC01SS01TVFVT1-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3053 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 6 | 1 | deiTUNQEC01SS01TVFVT1-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3054 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 7 | 1 | deiTUNQEC01SS01TVFVT1-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3055 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 8 | 1 | deiTUNQEC01SS01TVFVT1-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3056 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 9 | 1 | deiTUNQEC01SS01TVFVT1-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3057 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 10 | 1 | deiTUNQEC01SS01TVFVT1-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
3058 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20275 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20275 | 11 | 1 | deiTUNQEC01SS01TVFVT1-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3059 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT1-TVF01 | 27 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20276 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20276 | 0 | 16 | aeiTUNQEC01SS01TVFVT1-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3060 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20281 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20281 | 0 | 2 | deiTUNQEC01SS01TVFVT2-TVF01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3061 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20281 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20281 | 2 | 1 | deiTUNQEC01SS01TVFVT2-TVF01OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3062 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20281 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20281 | 4 | 2 | deiTUNQEC01SS01TVFVT2-TVF01RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3063 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 10561 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10561 | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3064 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10562 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10562 | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3065 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20281 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20281 | 6 | 2 | deiTUNQEC01SS01TVFVT2-TVF01AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3066 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10563 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10563 | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3067 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20281 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20281 | 8 | 2 | deiTUNQEC01SS01TVFVT2-TVF01AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3068 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20281 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20281 | 10 | 1 | deiTUNQEC01SS01TVFVT2-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3069 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20281 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20281 | 12 | 1 | deiTUNQEC01SS01TVFVT2-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3070 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20281 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20281 | 14 | 1 | deiTUNQEC01SS01TVFVT2-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3071 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20282 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20282 | 0 | 32 | aeiTUNQEC01SS01TVFVT2-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3072 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10564 | 0 | 2 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10564 | 0 | 2 | deoTUNQEC01SS01TVFVT2-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3073 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10565 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10565 | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3074 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 0 | 2 | deiTUNQEC01SS01TVFVT2-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3075 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10566 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10566 | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3076 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 2 | 2 | deiTUNQEC01SS01TVFVT2-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3077 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10567 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10567 | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3078 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 4 | 2 | deiTUNQEC01SS01TVFVT2-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3079 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10568 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10568 | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3080 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 6 | 2 | deiTUNQEC01SS01TVFVT2-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3081 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10569 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10569 | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3082 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 8 | 2 | deiTUNQEC01SS01TVFVT2-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3083 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10570 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10570 | 0 | 1 | deoTUNQEC01SS01TVFVT2-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3084 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20284 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20284 | 10 | 2 | deiTUNQEC01SS01TVFVT2-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3085 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20284 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20284 | 12 | 1 | deiTUNQEC01SS01TVFVT2-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3086 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20284 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20284 | 14 | 1 | deiTUNQEC01SS01TVFVT2-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3087 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 0 | 1 | deiTUNQEC01SS01TVFVT2-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3088 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 1 | 1 | deiTUNQEC01SS01TVFVT2-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3089 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 2 | 1 | deiTUNQEC01SS01TVFVT2-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3090 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 3 | 1 | deiTUNQEC01SS01TVFVT2-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3091 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 4 | 1 | deiTUNQEC01SS01TVFVT2-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3092 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 5 | 1 | deiTUNQEC01SS01TVFVT2-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3093 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 6 | 1 | deiTUNQEC01SS01TVFVT2-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3094 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 7 | 1 | deiTUNQEC01SS01TVFVT2-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3095 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 8 | 1 | deiTUNQEC01SS01TVFVT2-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3096 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 9 | 1 | deiTUNQEC01SS01TVFVT2-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3097 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 10 | 1 | deiTUNQEC01SS01TVFVT2-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
3098 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20285 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20285 | 11 | 1 | deiTUNQEC01SS01TVFVT2-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3099 | QEC01_RTU | TUN:QEC01 | SS01:TVF | TVF | VT2-TVF01 | 28 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20286 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20286 | 0 | 16 | aeiTUNQEC01SS01TVFVT2-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3100 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20291 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20291 | 0 | 2 | deiTUNQEC01NS01TVFVT3-TVF01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3101 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20291 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20291 | 2 | 1 | deiTUNQEC01NS01TVFVT3-TVF01OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3102 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20291 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20291 | 4 | 2 | deiTUNQEC01NS01TVFVT3-TVF01RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3103 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 10581 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10581 | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3104 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10582 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10582 | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3105 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20291 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20291 | 6 | 2 | deiTUNQEC01NS01TVFVT3-TVF01AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3106 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10583 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10583 | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3107 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20291 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20291 | 8 | 2 | deiTUNQEC01NS01TVFVT3-TVF01AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3108 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20291 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20291 | 10 | 1 | deiTUNQEC01NS01TVFVT3-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3109 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20291 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20291 | 12 | 1 | deiTUNQEC01NS01TVFVT3-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3110 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20291 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20291 | 14 | 1 | deiTUNQEC01NS01TVFVT3-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3111 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20292 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20292 | 0 | 32 | aeiTUNQEC01NS01TVFVT3-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3112 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10584 | 0 | 2 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10584 | 0 | 2 | deoTUNQEC01NS01TVFVT3-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3113 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10585 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10585 | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3114 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 0 | 2 | deiTUNQEC01NS01TVFVT3-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3115 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10586 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10586 | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3116 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 2 | 2 | deiTUNQEC01NS01TVFVT3-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3117 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10587 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10587 | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3118 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 4 | 2 | deiTUNQEC01NS01TVFVT3-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3119 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10588 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10588 | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3120 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 6 | 2 | deiTUNQEC01NS01TVFVT3-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3121 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10589 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10589 | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3122 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 8 | 2 | deiTUNQEC01NS01TVFVT3-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3123 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10590 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10590 | 0 | 1 | deoTUNQEC01NS01TVFVT3-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3124 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20294 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20294 | 10 | 2 | deiTUNQEC01NS01TVFVT3-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3125 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20294 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20294 | 12 | 1 | deiTUNQEC01NS01TVFVT3-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3126 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20294 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20294 | 14 | 1 | deiTUNQEC01NS01TVFVT3-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3127 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 0 | 1 | deiTUNQEC01NS01TVFVT3-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3128 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 1 | 1 | deiTUNQEC01NS01TVFVT3-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3129 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 2 | 1 | deiTUNQEC01NS01TVFVT3-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3130 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 3 | 1 | deiTUNQEC01NS01TVFVT3-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3131 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 4 | 1 | deiTUNQEC01NS01TVFVT3-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3132 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 5 | 1 | deiTUNQEC01NS01TVFVT3-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3133 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 6 | 1 | deiTUNQEC01NS01TVFVT3-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3134 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 7 | 1 | deiTUNQEC01NS01TVFVT3-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3135 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 8 | 1 | deiTUNQEC01NS01TVFVT3-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3136 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 9 | 1 | deiTUNQEC01NS01TVFVT3-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3137 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 10 | 1 | deiTUNQEC01NS01TVFVT3-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
3138 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20295 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20295 | 11 | 1 | deiTUNQEC01NS01TVFVT3-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3139 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT3-TVF01 | 29 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20296 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20296 | 0 | 16 | aeiTUNQEC01NS01TVFVT3-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3140 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20301 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20301 | 0 | 2 | deiTUNQEC01NS01TVFVT4-TVF01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3141 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20301 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20301 | 2 | 1 | deiTUNQEC01NS01TVFVT4-TVF01OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3142 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20301 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20301 | 4 | 2 | deiTUNQEC01NS01TVFVT4-TVF01RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3143 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 10601 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10601 | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3144 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10602 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10602 | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3145 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20301 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20301 | 6 | 2 | deiTUNQEC01NS01TVFVT4-TVF01AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3146 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10603 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10603 | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3147 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20301 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20301 | 8 | 2 | deiTUNQEC01NS01TVFVT4-TVF01AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3148 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20301 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20301 | 10 | 1 | deiTUNQEC01NS01TVFVT4-TVF01EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3149 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | StartStat | SIL0 | MODBUS:4:Read:Input Registers | 20301 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20301 | 12 | 1 | deiTUNQEC01NS01TVFVT4-TVF01StartStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3150 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | StopStat | SIL0 | MODBUS:4:Read:Input Registers | 20301 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20301 | 14 | 1 | deiTUNQEC01NS01TVFVT4-TVF01StopStat | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3151 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | SpeedFreq | SIL0 | MODBUS:4:Read:Input Registers | 20302 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20302 | 0 | 32 | aeiTUNQEC01NS01TVFVT4-TVF01SpeedFreq | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3152 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 10604 | 0 | 2 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10604 | 0 | 2 | deoTUNQEC01NS01TVFVT4-TVF01CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3153 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10605 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10605 | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3154 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 0 | 2 | deiTUNQEC01NS01TVFVT4-TVF01AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3155 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 10606 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10606 | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3156 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 2 | 2 | deiTUNQEC01NS01TVFVT4-TVF01AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3157 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10607 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10607 | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3158 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 4 | 2 | deiTUNQEC01NS01TVFVT4-TVF01AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3159 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10608 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10608 | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3160 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 6 | 2 | deiTUNQEC01NS01TVFVT4-TVF01AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3161 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10609 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10609 | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3162 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 8 | 2 | deiTUNQEC01NS01TVFVT4-TVF01AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3163 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 10610 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10610 | 0 | 1 | deoTUNQEC01NS01TVFVT4-TVF01CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3164 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20304 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20304 | 10 | 2 | deiTUNQEC01NS01TVFVT4-TVF01AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3165 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20304 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20304 | 12 | 1 | deiTUNQEC01NS01TVFVT4-TVF01AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3166 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CirPos | SIL0 | MODBUS:4:Read:Input Registers | 20304 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20304 | 14 | 1 | deiTUNQEC01NS01TVFVT4-TVF01CirPos | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3167 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | CirTrip | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 0 | 1 | deiTUNQEC01NS01TVFVT4-TVF01CirTrip | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3168 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | FanPos | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 1 | 1 | deiTUNQEC01NS01TVFVT4-TVF01FanPos | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3169 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | FanTrip | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 2 | 1 | deiTUNQEC01NS01TVFVT4-TVF01FanTrip | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3170 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 3 | 1 | deiTUNQEC01NS01TVFVT4-TVF01ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3171 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 4 | 1 | deiTUNQEC01NS01TVFVT4-TVF01RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3172 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 5 | 1 | deiTUNQEC01NS01TVFVT4-TVF01StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3173 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 6 | 1 | deiTUNQEC01NS01TVFVT4-TVF01WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3174 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | FrontTem | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 7 | 1 | deiTUNQEC01NS01TVFVT4-TVF01FrontTem | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3175 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 8 | 1 | deiTUNQEC01NS01TVFVT4-TVF01RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3176 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 9 | 1 | deiTUNQEC01NS01TVFVT4-TVF01Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3177 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 10 | 1 | deiTUNQEC01NS01TVFVT4-TVF01Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL ALARM
3178 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | More10 | SIL0 | MODBUS:4:Read:Input Registers | 20305 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20305 | 11 | 1 | deiTUNQEC01NS01TVFVT4-TVF01More10 | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3179 | QEC01_RTU | TUN:QEC01 | NS01:TVF | TVF | VT4-TVF01 | 30 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20306 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20306 | 0 | 16 | aeiTUNQEC01NS01TVFVT4-TVF01RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3180 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | 31 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 0 | 1 | deiTUNQEC01SS01SENSORTS101871Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3181 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | 31 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 1 | 1 | deiTUNQEC01SS01SENSORTS101871TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3182 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | 31 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 2 | 1 | deiTUNQEC01SS01SENSORTS101871HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3183 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | 31 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20311 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20311 | 3 | 1 | deiTUNQEC01SS01SENSORTS101871AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3184 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | 31 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20312 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20312 | 0 | 32 | aeiTUNQEC01SS01SENSORTS101871Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3185 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101871 | 31 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20314 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20314 | 0 | 32 | aeiTUNQEC01SS01SENSORTS101871Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3186 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | 32 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 0 | 1 | deiTUNQEC01SS01SENSORTS101984Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3187 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | 32 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 1 | 1 | deiTUNQEC01SS01SENSORTS101984TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3188 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | 32 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 2 | 1 | deiTUNQEC01SS01SENSORTS101984HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3189 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | 32 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20321 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20321 | 3 | 1 | deiTUNQEC01SS01SENSORTS101984AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3190 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | 32 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20322 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20322 | 0 | 32 | aeiTUNQEC01SS01SENSORTS101984Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3191 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | TTS | TS101984 | 32 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20324 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20324 | 0 | 32 | aeiTUNQEC01SS01SENSORTS101984Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3192 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | 33 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 0 | 1 | deiTUNQEC01NS01SENSORTS102441Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3193 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | 33 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 1 | 1 | deiTUNQEC01NS01SENSORTS102441TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3194 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | 33 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 2 | 1 | deiTUNQEC01NS01SENSORTS102441HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3195 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | 33 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20331 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20331 | 3 | 1 | deiTUNQEC01NS01SENSORTS102441AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3196 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | 33 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20332 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20332 | 0 | 32 | aeiTUNQEC01NS01SENSORTS102441Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3197 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102441 | 33 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20334 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20334 | 0 | 32 | aeiTUNQEC01NS01SENSORTS102441Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3198 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | 34 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 0 | 1 | deiTUNQEC01NS01SENSORTS102499Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3199 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | 34 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 1 | 1 | deiTUNQEC01NS01SENSORTS102499TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3200 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | 34 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 2 | 1 | deiTUNQEC01NS01SENSORTS102499HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3201 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | 34 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20341 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20341 | 3 | 1 | deiTUNQEC01NS01SENSORTS102499AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3202 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | 34 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20342 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20342 | 0 | 32 | aeiTUNQEC01NS01SENSORTS102499Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3203 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102499 | 34 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20344 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20344 | 0 | 32 | aeiTUNQEC01NS01SENSORTS102499Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3204 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | 35 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20351 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20351 | 0 | 1 | deiTUNQEC01NS01SENSORTS102261Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3205 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | 35 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20351 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20351 | 1 | 1 | deiTUNQEC01NS01SENSORTS102261TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3206 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | 35 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20351 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20351 | 2 | 1 | deiTUNQEC01NS01SENSORTS102261HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3207 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | 35 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20351 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20351 | 3 | 1 | deiTUNQEC01NS01SENSORTS102261AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3208 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | 35 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20352 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20352 | 0 | 32 | aeiTUNQEC01NS01SENSORTS102261Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3209 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS102261 | 35 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20354 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20354 | 0 | 32 | aeiTUNQEC01NS01SENSORTS102261Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3210 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | 36 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20361 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20361 | 0 | 1 | deiTUNQEC01NS01SENSORTS100023Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3211 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | 36 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20361 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20361 | 1 | 1 | deiTUNQEC01NS01SENSORTS100023TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3212 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | 36 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20361 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20361 | 2 | 1 | deiTUNQEC01NS01SENSORTS100023HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3213 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | 36 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20361 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20361 | 3 | 1 | deiTUNQEC01NS01SENSORTS100023AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3214 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | 36 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20362 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20362 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100023Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3215 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100023 | 36 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20364 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20364 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100023Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3216 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | 37 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20371 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20371 | 0 | 1 | deiTUNQEC01NS01SENSORTS100062Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3217 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | 37 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20371 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20371 | 1 | 1 | deiTUNQEC01NS01SENSORTS100062TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3218 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | 37 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20371 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20371 | 2 | 1 | deiTUNQEC01NS01SENSORTS100062HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3219 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | 37 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20371 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20371 | 3 | 1 | deiTUNQEC01NS01SENSORTS100062AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3220 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | 37 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20372 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20372 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100062Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3221 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100062 | 37 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20374 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20374 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100062Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3222 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | 38 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20381 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20381 | 0 | 1 | deiTUNQEC01NS01SENSORTS100108Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3223 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | 38 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20381 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20381 | 1 | 1 | deiTUNQEC01NS01SENSORTS100108TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3224 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | 38 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20381 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20381 | 2 | 1 | deiTUNQEC01NS01SENSORTS100108HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3225 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | 38 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20381 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20381 | 3 | 1 | deiTUNQEC01NS01SENSORTS100108AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3226 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | 38 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20382 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20382 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100108Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3227 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100108 | 38 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20384 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20384 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100108Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3228 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | 39 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 0 | 1 | deiTUNQEC01NS01SENSORTS100230Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3229 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | 39 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 1 | 1 | deiTUNQEC01NS01SENSORTS100230TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3230 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | 39 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 2 | 1 | deiTUNQEC01NS01SENSORTS100230HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3231 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | 39 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20391 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20391 | 3 | 1 | deiTUNQEC01NS01SENSORTS100230AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3232 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | 39 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20392 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20392 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100230Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3233 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100230 | 39 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20394 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20394 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100230Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3234 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | 40 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 0 | 1 | deiTUNQEC01NS01SENSORTS100335Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3235 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | 40 | TemOut | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 1 | 1 | deiTUNQEC01NS01SENSORTS100335TemOut | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE SENSOR FAULT
3236 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | 40 | HumOut | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 2 | 1 | deiTUNQEC01NS01SENSORTS100335HumOut | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY SENSOR FAULT
3237 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | 40 | AveTem | SIL0 | MODBUS:4:Read:Input Registers | 20401 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20401 | 3 | 1 | deiTUNQEC01NS01SENSORTS100335AveTem | 4 |  |  | 0 | $ComStatus , , | #AVERAGE TEMPERATURE EXCLUSION
3238 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | 40 | Temperature | SIL0 | MODBUS:4:Read:Input Registers | 20402 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20402 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100335Temperature | 4 |  |  | 0 | $ComStatus , , | #TEMPERATURE MEASUREMENT
3239 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | TTS | TS100335 | 40 | Humidity | SIL0 | MODBUS:4:Read:Input Registers | 20404 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20404 | 0 | 32 | aeiTUNQEC01NS01SENSORTS100335Humidity | 4 |  |  | 0 | $ComStatus , , | #HUMIDITY MEASUREMENT
3240 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | VS | VS101909 | 41 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20411 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20411 | 0 | 1 | deiTUNQEC01SS01SENSORVS101909Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3241 | QEC01_RTU | TUN:QEC01 | SS01:SENSOR | VS | VS101909 | 41 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20412 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20412 | 0 | 32 | aeiTUNQEC01SS01SENSORVS101909Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
3242 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS102357 | 42 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20421 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20421 | 0 | 1 | deiTUNQEC01NS01SENSORVS102357Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3243 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS102357 | 42 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20422 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20422 | 0 | 32 | aeiTUNQEC01NS01SENSORVS102357Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
3244 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS102467 | 43 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20431 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20431 | 0 | 1 | deiTUNQEC01NS01SENSORVS102467Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3245 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS102467 | 43 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20432 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20432 | 0 | 32 | aeiTUNQEC01NS01SENSORVS102467Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
3246 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS102276 | 44 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20441 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20441 | 0 | 1 | deiTUNQEC01NS01SENSORVS102276Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3247 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS102276 | 44 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20442 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20442 | 0 | 32 | aeiTUNQEC01NS01SENSORVS102276Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
3248 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS100080 | 45 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20451 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20451 | 0 | 1 | deiTUNQEC01NS01SENSORVS100080Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3249 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS100080 | 45 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20452 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20452 | 0 | 32 | aeiTUNQEC01NS01SENSORVS100080Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
3250 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS100285 | 46 | Availability | SIL0 | MODBUS:4:Read:Input Registers | 20461 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20461 | 0 | 1 | deiTUNQEC01NS01SENSORVS100285Availability | 4 |  |  | 0 | $ComStatus , , | #UNAVAILABLE STATUS
3251 | QEC01_RTU | TUN:QEC01 | NS01:SENSOR | VS | VS100285 | 46 | Velocity | SIL0 | MODBUS:4:Read:Input Registers | 20462 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20462 | 0 | 32 | aeiTUNQEC01NS01SENSORVS100285Velocity | 4 |  |  | 0 | $ComStatus , , | #VELOCITY MEASUREMENT
3252 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20471 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20471 | 0 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3253 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20471 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20471 | 2 | 1 | deiTUNQEC01SS01DAMPERVT5-TDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3254 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20471 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20471 | 4 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3255 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 10941 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10941 | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3256 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10942 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10942 | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3257 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20471 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20471 | 6 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3258 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10943 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10943 | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3259 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20471 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20471 | 8 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3260 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10944 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10944 | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
3261 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20471 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20471 | 10 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
3262 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10945 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10945 | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
3263 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20471 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20471 | 12 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
3264 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10946 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10946 | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
3265 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20471 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20471 | 14 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
3266 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10947 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10947 | 0 | 1 | deoTUNQEC01SS01DAMPERVT5-TDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
3267 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20472 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20472 | 0 | 2 | deiTUNQEC01SS01DAMPERVT5-TDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
3268 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20472 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20472 | 2 | 1 | deiTUNQEC01SS01DAMPERVT5-TDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
3269 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20472 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20472 | 4 | 1 | deiTUNQEC01SS01DAMPERVT5-TDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
3270 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20472 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20472 | 6 | 1 | deiTUNQEC01SS01DAMPERVT5-TDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
3271 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | VT5-TDP01 | 47 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20472 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20472 | 8 | 1 | deiTUNQEC01SS01DAMPERVT5-TDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
3272 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20481 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20481 | 0 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3273 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20481 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20481 | 2 | 1 | deiTUNQEC01NS01DAMPERVT6-TDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3274 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20481 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20481 | 4 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3275 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 10961 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 10961 | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3276 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10962 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10962 | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3277 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20481 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20481 | 6 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3278 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 10963 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10963 | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3279 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20481 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20481 | 8 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3280 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10964 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10964 | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
3281 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20481 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20481 | 10 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
3282 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 10965 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10965 | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
3283 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20481 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20481 | 12 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
3284 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10966 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10966 | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
3285 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20481 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20481 | 14 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
3286 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 10967 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 10967 | 0 | 1 | deoTUNQEC01NS01DAMPERVT6-TDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
3287 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20482 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20482 | 0 | 2 | deiTUNQEC01NS01DAMPERVT6-TDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
3288 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20482 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20482 | 2 | 1 | deiTUNQEC01NS01DAMPERVT6-TDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
3289 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20482 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20482 | 4 | 1 | deiTUNQEC01NS01DAMPERVT6-TDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
3290 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20482 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20482 | 6 | 1 | deiTUNQEC01NS01DAMPERVT6-TDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
3291 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | VT6-TDP01 | 48 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20482 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20482 | 8 | 1 | deiTUNQEC01NS01DAMPERVT6-TDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
3292 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | 49 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20491 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20491 | 0 | 2 | deiTUNQEC01SS01DAMPERVT1-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3293 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | 49 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20491 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20491 | 2 | 2 | deiTUNQEC01SS01DAMPERVT1-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3294 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | 49 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20491 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20491 | 4 | 1 | deiTUNQEC01SS01DAMPERVT1-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
3295 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | 49 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20491 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20491 | 6 | 1 | deiTUNQEC01SS01DAMPERVT1-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
3296 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | 49 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20491 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20491 | 8 | 1 | deiTUNQEC01SS01DAMPERVT1-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
3297 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT1-IDP01 | 49 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20491 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20491 | 10 | 1 | deiTUNQEC01SS01DAMPERVT1-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
3298 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | 50 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20501 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20501 | 0 | 2 | deiTUNQEC01SS01DAMPERVT2-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3299 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | 50 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20501 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20501 | 2 | 2 | deiTUNQEC01SS01DAMPERVT2-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3300 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | 50 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20501 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20501 | 4 | 1 | deiTUNQEC01SS01DAMPERVT2-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
3301 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | 50 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20501 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20501 | 6 | 1 | deiTUNQEC01SS01DAMPERVT2-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
3302 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | 50 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20501 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20501 | 8 | 1 | deiTUNQEC01SS01DAMPERVT2-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
3303 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | IDP | VT2-IDP01 | 50 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20501 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20501 | 10 | 1 | deiTUNQEC01SS01DAMPERVT2-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
3304 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | 51 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20511 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20511 | 0 | 2 | deiTUNQEC01NS01DAMPERVT3-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3305 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | 51 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20511 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20511 | 2 | 2 | deiTUNQEC01NS01DAMPERVT3-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3306 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | 51 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20511 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20511 | 4 | 1 | deiTUNQEC01NS01DAMPERVT3-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
3307 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | 51 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20511 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20511 | 6 | 1 | deiTUNQEC01NS01DAMPERVT3-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
3308 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | 51 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20511 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20511 | 8 | 1 | deiTUNQEC01NS01DAMPERVT3-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
3309 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT3-IDP01 | 51 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20511 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20511 | 10 | 1 | deiTUNQEC01NS01DAMPERVT3-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
3310 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | 52 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20521 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20521 | 0 | 2 | deiTUNQEC01NS01DAMPERVT4-IDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3311 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | 52 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20521 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20521 | 2 | 2 | deiTUNQEC01NS01DAMPERVT4-IDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3312 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | 52 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20521 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20521 | 4 | 1 | deiTUNQEC01NS01DAMPERVT4-IDP01CloseStat | 4 |  |  | 0 | $ComStatus , , | #IDP-MCB-H closed status
3313 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | 52 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20521 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20521 | 6 | 1 | deiTUNQEC01NS01DAMPERVT4-IDP01TripStat | 4 |  |  | 0 | $ComStatus , , | #IDP- MCB-H tripped status
3314 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | 52 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20521 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20521 | 8 | 1 | deiTUNQEC01NS01DAMPERVT4-IDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
3315 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | IDP | VT4-IDP01 | 52 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20521 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20521 | 10 | 1 | deiTUNQEC01NS01DAMPERVT4-IDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
3316 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20531 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20531 | 0 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3317 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20531 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20531 | 2 | 1 | deiTUNQEC01SS01DAMPERFR1-BDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3318 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20531 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20531 | 4 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3319 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 11061 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11061 | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3320 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 11062 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11062 | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3321 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20531 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20531 | 6 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3322 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 11063 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11063 | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3323 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20531 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20531 | 8 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3324 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 11064 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11064 | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
3325 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20531 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20531 | 10 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
3326 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 11065 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11065 | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
3327 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20531 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20531 | 12 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
3328 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 11066 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11066 | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
3329 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20531 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20531 | 14 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
3330 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 11067 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11067 | 0 | 1 | deoTUNQEC01SS01DAMPERFR1-BDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
3331 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20532 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20532 | 0 | 2 | deiTUNQEC01SS01DAMPERFR1-BDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
3332 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20532 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20532 | 2 | 1 | deiTUNQEC01SS01DAMPERFR1-BDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
3333 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20532 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20532 | 4 | 1 | deiTUNQEC01SS01DAMPERFR1-BDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
3334 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20532 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20532 | 6 | 1 | deiTUNQEC01SS01DAMPERFR1-BDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
3335 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | TVD | FR1-BDP01 | 53 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20532 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20532 | 8 | 1 | deiTUNQEC01SS01DAMPERFR1-BDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
3336 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20541 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20541 | 0 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3337 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | OpMod | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20541 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20541 | 2 | 1 | deiTUNQEC01NS01DAMPERFR2-BDP01OpMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3338 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20541 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20541 | 4 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3339 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 11081 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11081 | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3340 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 11082 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11082 | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3341 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20541 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20541 | 6 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3342 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 11083 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11083 | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3343 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20541 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20541 | 8 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3344 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | CmdSelOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 11084 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11084 | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01CmdSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT
3345 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | AckSelOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20541 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20541 | 10 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01AckSelOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER SELECT ACK
3346 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | CmdExeOpen | SIL2_Control | MODBUS:16:Write:Holding Registers | 11085 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11085 | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01CmdExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE
3347 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | AckExeOpen | SIL2_Control | MODBUS:4:Read:Input Registers | 20541 | 12 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20541 | 12 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01AckExeOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN ORDER EXECUTE ACK
3348 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | CmdSelClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 11086 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11086 | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01CmdSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT
3349 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | AckSelClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20541 | 14 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20541 | 14 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01AckSelClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER SELECT ACK
3350 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | CmdExeClose | SIL2_Control | MODBUS:16:Write:Holding Registers | 11087 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11087 | 0 | 1 | deoTUNQEC01NS01DAMPERFR2-BDP01CmdExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE
3351 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | AckExeClose | SIL2_Control | MODBUS:4:Read:Input Registers | 20542 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20542 | 0 | 2 | deiTUNQEC01NS01DAMPERFR2-BDP01AckExeClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE ORDER EXECUTE ACK
3352 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | DamOpen | SIL0 | MODBUS:4:Read:Input Registers | 20542 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20542 | 2 | 1 | deiTUNQEC01NS01DAMPERFR2-BDP01DamOpen | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER OPEN
3353 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | DamOut | SIL0 | MODBUS:4:Read:Input Registers | 20542 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20542 | 4 | 1 | deiTUNQEC01NS01DAMPERFR2-BDP01DamOut | 4 |  |  | 0 | $ComStatus , , | #DAMPER SUPPLY CIRCUIT BREAKER FAULT
3354 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | FailOpen | SIL0 | MODBUS:4:Read:Input Registers | 20542 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20542 | 6 | 1 | deiTUNQEC01NS01DAMPERFR2-BDP01FailOpen | 4 |  |  | 0 | $ComStatus , , | #OPEN MISMATCH ALARM
3355 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | TVD | FR2-BDP01 | 54 | FailClose | SIL0 | MODBUS:4:Read:Input Registers | 20542 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20542 | 8 | 1 | deiTUNQEC01NS01DAMPERFR2-BDP01FailClose | 4 |  |  | 0 | $ComStatus , , | #CLOSE MISMATCH ALARM
3356 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-95 | 55 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20551 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20551 | 0 | 2 | deiTUNQEC01SS01DAMPERCON-95Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3357 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-95 | 55 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20551 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20551 | 2 | 1 | deiTUNQEC01SS01DAMPERCON-95CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3358 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-95 | 55 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20551 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20551 | 4 | 1 | deiTUNQEC01SS01DAMPERCON-95TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3359 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-95 | 55 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20551 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20551 | 6 | 1 | deiTUNQEC01SS01DAMPERCON-95LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
3360 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-94 | 56 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20561 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20561 | 0 | 2 | deiTUNQEC01NS01DAMPERCON-94Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3361 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-94 | 56 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20561 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20561 | 2 | 1 | deiTUNQEC01NS01DAMPERCON-94CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3362 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-94 | 56 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20561 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20561 | 4 | 1 | deiTUNQEC01NS01DAMPERCON-94TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3363 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-94 | 56 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20561 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20561 | 6 | 1 | deiTUNQEC01NS01DAMPERCON-94LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
3364 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-51 | 57 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20571 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20571 | 0 | 2 | deiTUNQEC01SS01DAMPERCON-51Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3365 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-51 | 57 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 2 | 1 | deiTUNQEC01SS01DAMPERCON-51CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3366 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-51 | 57 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 4 | 1 | deiTUNQEC01SS01DAMPERCON-51TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3367 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-51 | 57 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20571 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20571 | 6 | 1 | deiTUNQEC01SS01DAMPERCON-51LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
3368 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-49 | 58 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20581 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20581 | 0 | 2 | deiTUNQEC01SS01DAMPERCON-49Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3369 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-49 | 58 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20581 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20581 | 2 | 1 | deiTUNQEC01SS01DAMPERCON-49CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3370 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-49 | 58 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20581 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20581 | 4 | 1 | deiTUNQEC01SS01DAMPERCON-49TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3371 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-49 | 58 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20581 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20581 | 6 | 1 | deiTUNQEC01SS01DAMPERCON-49LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
3372 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-34 | 59 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20591 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20591 | 0 | 2 | deiTUNQEC01NS01DAMPERCON-34Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3373 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-34 | 59 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 2 | 1 | deiTUNQEC01NS01DAMPERCON-34CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3374 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-34 | 59 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 4 | 1 | deiTUNQEC01NS01DAMPERCON-34TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3375 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-34 | 59 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20591 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20591 | 6 | 1 | deiTUNQEC01NS01DAMPERCON-34LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
3376 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-53 | 60 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20601 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20601 | 0 | 2 | deiTUNQEC01NS01DAMPERCON-53Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3377 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-53 | 60 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 2 | 1 | deiTUNQEC01NS01DAMPERCON-53CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3378 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-53 | 60 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 4 | 1 | deiTUNQEC01NS01DAMPERCON-53TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3379 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-53 | 60 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20601 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20601 | 6 | 1 | deiTUNQEC01NS01DAMPERCON-53LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
3380 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-52 | 61 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20611 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20611 | 0 | 2 | deiTUNQEC01SS01DAMPERCON-52Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3381 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-52 | 61 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 2 | 1 | deiTUNQEC01SS01DAMPERCON-52CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3382 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-52 | 61 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 4 | 1 | deiTUNQEC01SS01DAMPERCON-52TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3383 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-52 | 61 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20611 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20611 | 6 | 1 | deiTUNQEC01SS01DAMPERCON-52LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
3384 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-50 | 62 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20621 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20621 | 0 | 2 | deiTUNQEC01SS01DAMPERCON-50Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3385 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-50 | 62 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 2 | 1 | deiTUNQEC01SS01DAMPERCON-50CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3386 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-50 | 62 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 4 | 1 | deiTUNQEC01SS01DAMPERCON-50TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3387 | QEC01_RTU | TUN:QEC01 | SS01:DAMPER | MSFD | CON-50 | 62 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20621 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20621 | 6 | 1 | deiTUNQEC01SS01DAMPERCON-50LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
3388 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-88 | 63 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20631 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20631 | 0 | 2 | deiTUNQEC01NS01DAMPERCON-88Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3389 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-88 | 63 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20631 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20631 | 2 | 1 | deiTUNQEC01NS01DAMPERCON-88CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3390 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-88 | 63 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20631 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20631 | 4 | 1 | deiTUNQEC01NS01DAMPERCON-88TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3391 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-88 | 63 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20631 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20631 | 6 | 1 | deiTUNQEC01NS01DAMPERCON-88LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
3392 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-58 | 64 | Stat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20641 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20641 | 0 | 2 | deiTUNQEC01NS01DAMPERCON-58Stat | 4 |  |  | 0 | $ComStatus , , | #DAMPER OPENED STATUS
3393 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-58 | 64 | CloseStat | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 2 | 1 | deiTUNQEC01NS01DAMPERCON-58CloseStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB closed status
3394 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-58 | 64 | TripStat | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 4 | 1 | deiTUNQEC01NS01DAMPERCON-58TripStat | 4 |  |  | 0 | $ComStatus , , | # MSFD - CON- MCB tripped status
3395 | QEC01_RTU | TUN:QEC01 | NS01:DAMPER | MSFD | CON-58 | 64 | LocalMod | SIL0 | MODBUS:4:Read:Input Registers | 20641 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20641 | 6 | 1 | deiTUNQEC01NS01DAMPERCON-58LocalMod | 4 |  |  | 0 | $ComStatus , , | #LOCAL MODE STATUS
3396 | QEC01_RTU | TUN:QEC01 | SS01:AHU | AHU | CON-02 | 65 | ControlMod | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 0 | 1 | deiTUNQEC01SS01AHUCON-02ControlMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3397 | QEC01_RTU | TUN:QEC01 | SS01:AHU | AHU | CON-02 | 65 | RunStat | SIL0 | MODBUS:4:Read:Input Registers | 20651 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20651 | 1 | 1 | deiTUNQEC01SS01AHUCON-02RunStat | 4 |  |  | 0 | $ComStatus , , | #RUN
3398 | QEC01_RTU | TUN:QEC01 | NS01:AHU | AHU | PLA-02 | 66 | ControlMod | SIL0 | MODBUS:4:Read:Input Registers | 20661 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20661 | 0 | 1 | deiTUNQEC01NS01AHUPLA-02ControlMod | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3399 | QEC01_RTU | TUN:QEC01 | NS01:AHU | AHU | PLA-02 | 66 | RunStat | SIL0 | MODBUS:4:Read:Input Registers | 20661 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20661 | 1 | 1 | deiTUNQEC01NS01AHUPLA-02RunStat | 4 |  |  | 0 | $ComStatus , , | #RUN
3400 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 67 | PlcState | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 0 | 1 | deiTUNQEC01SCRJETPLC01PlcState | 4 |  |  | 0 | $ComStatus , , | #PLC A/B OFFLINE
3401 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 67 | OpStatus | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 1 | 1 | deiTUNQEC01SCRJETPLC01OpStatus | 4 |  |  | 0 | $ComStatus , , | #PLC RUNNING.
3402 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 67 | PwStat | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 2 | 1 | deiTUNQEC01SCRJETPLC01PwStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: POWER SUPPLY FAULT
3403 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 67 | CpuStat | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 3 | 1 | deiTUNQEC01SCRJETPLC01CpuStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CPU MODULE FAULT
3404 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 67 | CrpStat | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 4 | 1 | deiTUNQEC01SCRJETPLC01CrpStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: CRP MODULE FAULT
3405 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 67 | CraStat | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 5 | 1 | deiTUNQEC01SCRJETPLC01CraStat | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
3406 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 67 | NrpStat | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 6 | 1 | deiTUNQEC01SCRJETPLC01NrpStat | 4 |  |  | 0 | $ComStatus , , | #NRP MODULE FAULT
3407 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 67 | ComStat | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 7 | 1 | deiTUNQEC01SCRJETPLC01ComStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
3408 | QEC01_RTU | TUN:QEC01 | SCR | SPLC | JETPLC01 | 67 | IoStat | SIL0 | MODBUS:4:Read:Input Registers | 20671 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20671 | 8 | 1 | deiTUNQEC01SCRJETPLC01IoStat | 4 |  |  | 0 | $ComStatus , , | #PLC A/B: NOE MODULE FAULT (STATION/SHAFT PLCS COMMUNICATION)
3409 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20681 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20681 | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3410 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20681 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20681 | 2 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3411 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20681 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20681 | 4 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3412 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 11361 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11361 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3413 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 11362 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11362 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3414 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20681 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20681 | 6 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3415 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 11363 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11363 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3416 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20681 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20681 | 8 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3417 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20681 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20681 | 10 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3418 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | FailStart | SIL0 | MODBUS:4:Read:Input Registers | 20681 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20681 | 12 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132FailStart | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3419 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | FailStop | SIL0 | MODBUS:4:Read:Input Registers | 20681 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20681 | 14 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132FailStop | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3420 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | SpeedFrep | SIL0 | MODBUS:4:Read:Input Registers | 20682 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20682 | 0 | 32 | aeiTUNQEC01QEC1BJETQEC1B-JET100132SpeedFrep | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3421 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 11364 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11364 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3422 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11365 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11365 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3423 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20684 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20684 | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3424 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11366 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11366 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3425 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20684 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20684 | 2 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3426 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11367 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11367 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3427 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20684 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20684 | 4 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3428 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11368 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11368 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3429 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20684 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20684 | 6 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3430 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11369 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11369 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3431 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20684 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20684 | 8 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3432 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11370 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11370 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100132CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3433 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20684 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20684 | 10 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100132AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3434 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3435 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CirOpen | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 1 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132CirOpen | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3436 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | CirOut | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 2 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132CirOut | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3437 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | FanOpen | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 3 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132FanOpen | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3438 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | FanOut | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 4 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132FanOut | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3439 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 5 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3440 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 6 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3441 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 7 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3442 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 8 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3443 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | FrontTem1 | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 9 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132FrontTem1 | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3444 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 10 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3445 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 11 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3446 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 12 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL FAULT
3447 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | More6hr | SIL0 | MODBUS:4:Read:Input Registers | 20685 | 13 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20685 | 13 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100132More6hr | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3448 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100132 | 68 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20686 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20686 | 0 | 16 | aeiTUNQEC01QEC1BJETQEC1B-JET100132RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3449 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20691 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20691 | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3450 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20691 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20691 | 2 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3451 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20691 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20691 | 4 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3452 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 11381 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11381 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3453 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 11382 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11382 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3454 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20691 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20691 | 6 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3455 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 11383 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11383 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3456 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20691 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20691 | 8 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3457 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20691 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20691 | 10 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3458 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | FailStart | SIL0 | MODBUS:4:Read:Input Registers | 20691 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20691 | 12 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133FailStart | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3459 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | FailStop | SIL0 | MODBUS:4:Read:Input Registers | 20691 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20691 | 14 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133FailStop | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3460 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | SpeedFrep | SIL0 | MODBUS:4:Read:Input Registers | 20692 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20692 | 0 | 32 | aeiTUNQEC01QEC1BJETQEC1B-JET100133SpeedFrep | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3461 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 11384 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11384 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3462 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11385 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11385 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3463 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20694 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20694 | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3464 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11386 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11386 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3465 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20694 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20694 | 2 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3466 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11387 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11387 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3467 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20694 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20694 | 4 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3468 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11388 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11388 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3469 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20694 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20694 | 6 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3470 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11389 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11389 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3471 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20694 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20694 | 8 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3472 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11390 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11390 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100133CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3473 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20694 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20694 | 10 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100133AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3474 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3475 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CirOpen | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 1 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133CirOpen | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3476 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | CirOut | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 2 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133CirOut | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3477 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | FanOpen | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 3 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133FanOpen | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3478 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | FanOut | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 4 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133FanOut | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3479 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 5 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3480 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 6 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3481 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 7 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3482 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 8 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3483 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | FrontTem1 | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 9 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133FrontTem1 | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3484 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 10 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3485 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 11 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3486 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 12 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL FAULT
3487 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | More6hr | SIL0 | MODBUS:4:Read:Input Registers | 20695 | 13 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20695 | 13 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100133More6hr | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3488 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100133 | 69 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20696 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20696 | 0 | 16 | aeiTUNQEC01QEC1BJETQEC1B-JET100133RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3489 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20701 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20701 | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3490 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20701 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20701 | 2 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3491 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20701 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20701 | 4 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3492 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 11401 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11401 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3493 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 11402 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11402 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3494 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20701 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20701 | 6 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3495 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 11403 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11403 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3496 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20701 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20701 | 8 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3497 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20701 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20701 | 10 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3498 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | FailStart | SIL0 | MODBUS:4:Read:Input Registers | 20701 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20701 | 12 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134FailStart | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3499 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | FailStop | SIL0 | MODBUS:4:Read:Input Registers | 20701 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20701 | 14 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134FailStop | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3500 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | SpeedFrep | SIL0 | MODBUS:4:Read:Input Registers | 20702 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20702 | 0 | 32 | aeiTUNQEC01QEC1BJETQEC1B-JET100134SpeedFrep | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3501 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 11404 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11404 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3502 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11405 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11405 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3503 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20704 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20704 | 0 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3504 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11406 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11406 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3505 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20704 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20704 | 2 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3506 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11407 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11407 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3507 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20704 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20704 | 4 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3508 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11408 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11408 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3509 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20704 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20704 | 6 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3510 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11409 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11409 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3511 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20704 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20704 | 8 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3512 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11410 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11410 | 0 | 1 | deoTUNQEC01QEC1BJETQEC1B-JET100134CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3513 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20704 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20704 | 10 | 2 | deiTUNQEC01QEC1BJETQEC1B-JET100134AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3514 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 0 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3515 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CirOpen | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 1 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134CirOpen | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3516 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | CirOut | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 2 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134CirOut | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3517 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | FanOpen | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 3 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134FanOpen | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3518 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | FanOut | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 4 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134FanOut | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3519 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 5 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3520 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 6 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3521 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 7 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3522 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 8 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3523 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | FrontTem1 | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 9 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134FrontTem1 | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3524 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 10 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3525 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 11 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3526 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 12 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL FAULT
3527 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | More6hr | SIL0 | MODBUS:4:Read:Input Registers | 20705 | 13 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20705 | 13 | 1 | deiTUNQEC01QEC1BJETQEC1B-JET100134More6hr | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3528 | QEC01_RTU | TUN:QEC01 | QEC1B:JET | JET | QEC1B-JET100134 | 70 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20706 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20706 | 0 | 16 | aeiTUNQEC01QEC1BJETQEC1B-JET100134RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3529 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20711 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20711 | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3530 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20711 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20711 | 2 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3531 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20711 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20711 | 4 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3532 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 11421 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11421 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3533 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 11422 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11422 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3534 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20711 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20711 | 6 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3535 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 11423 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11423 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3536 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20711 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20711 | 8 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3537 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20711 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20711 | 10 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3538 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | FailStart | SIL0 | MODBUS:4:Read:Input Registers | 20711 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20711 | 12 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392FailStart | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3539 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | FailStop | SIL0 | MODBUS:4:Read:Input Registers | 20711 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20711 | 14 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392FailStop | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3540 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | SpeedFrep | SIL0 | MODBUS:4:Read:Input Registers | 20712 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20712 | 0 | 32 | aeiTUNQEC01QEC1AJETQEC1A-JET102392SpeedFrep | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3541 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 11424 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11424 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3542 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11425 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11425 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3543 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20714 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20714 | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3544 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11426 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11426 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3545 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20714 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20714 | 2 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3546 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11427 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11427 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3547 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20714 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20714 | 4 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3548 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11428 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11428 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3549 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20714 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20714 | 6 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3550 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11429 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11429 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3551 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20714 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20714 | 8 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3552 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11430 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11430 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102392CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3553 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20714 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20714 | 10 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102392AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3554 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3555 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CirOpen | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 1 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392CirOpen | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3556 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | CirOut | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 2 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392CirOut | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3557 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | FanOpen | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 3 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392FanOpen | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3558 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | FanOut | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 4 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392FanOut | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3559 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 5 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3560 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 6 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3561 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 7 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3562 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 8 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3563 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | FrontTem1 | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 9 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392FrontTem1 | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3564 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 10 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3565 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 11 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3566 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 12 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL FAULT
3567 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | More6hr | SIL0 | MODBUS:4:Read:Input Registers | 20715 | 13 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20715 | 13 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102392More6hr | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3568 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102392 | 71 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20716 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20716 | 0 | 16 | aeiTUNQEC01QEC1AJETQEC1A-JET102392RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3569 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20721 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20721 | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3570 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20721 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20721 | 2 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3571 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20721 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20721 | 4 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3572 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 11441 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11441 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3573 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 11442 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11442 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3574 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20721 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20721 | 6 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3575 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 11443 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11443 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3576 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20721 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20721 | 8 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3577 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20721 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20721 | 10 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3578 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | FailStart | SIL0 | MODBUS:4:Read:Input Registers | 20721 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20721 | 12 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393FailStart | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3579 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | FailStop | SIL0 | MODBUS:4:Read:Input Registers | 20721 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20721 | 14 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393FailStop | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3580 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | SpeedFrep | SIL0 | MODBUS:4:Read:Input Registers | 20722 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20722 | 0 | 32 | aeiTUNQEC01QEC1AJETQEC1A-JET102393SpeedFrep | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3581 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 11444 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11444 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3582 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11445 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11445 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3583 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20724 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20724 | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3584 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11446 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11446 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3585 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20724 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20724 | 2 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3586 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11447 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11447 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3587 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20724 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20724 | 4 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3588 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11448 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11448 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3589 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20724 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20724 | 6 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3590 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11449 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11449 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3591 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20724 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20724 | 8 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3592 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11450 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11450 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102393CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3593 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20724 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20724 | 10 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102393AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3594 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3595 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CirOpen | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 1 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393CirOpen | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3596 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | CirOut | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 2 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393CirOut | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3597 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | FanOpen | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 3 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393FanOpen | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3598 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | FanOut | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 4 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393FanOut | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3599 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 5 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3600 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 6 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3601 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 7 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3602 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 8 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3603 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | FrontTem1 | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 9 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393FrontTem1 | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3604 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 10 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3605 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 11 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3606 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 12 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL FAULT
3607 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | More6hr | SIL0 | MODBUS:4:Read:Input Registers | 20725 | 13 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20725 | 13 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102393More6hr | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3608 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102393 | 72 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20726 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20726 | 0 | 16 | aeiTUNQEC01QEC1AJETQEC1A-JET102393RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3609 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | SwitchStat | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20731 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20731 | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394SwitchStat | 4 |  |  | 0 | $ComStatus , , | #ELECTRICAL PANEL SELECTOR SWITCH STATUS
3610 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | OperatingMode | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20731 | 2 | 1 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20731 | 2 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394OperatingMode | 4 |  |  | 0 | $ComStatus , , | #OPERATING MODE (00=AUTO SCADA;01=MANUAL SCADA;10=MANUAL LCP)
3611 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | RunStatus | SIL2_Monitoring | MODBUS:4:Read:Input Registers | 20731 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Monitoring |  | QEC01_RTU_S2M_EVariables.dat | DEIV | 4 | 1 | 20731 | 4 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394RunStatus | 4 |  |  | 0 | $ComStatus , , | #SUPPLY / EXHAUST / STOP STATUS
3612 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdAutoCom | SIL0 | MODBUS:16:Write:Holding Registers | 11461 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11461 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdAutoCom | 4 |  |  | 0 | $ComStatus , , | #SCADA AUTO MODE COMMAND
3613 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdSelSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 11462 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11462 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT
3614 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | AckSelSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20731 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20731 | 6 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394AckSelSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE SELECT ACK
3615 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdExeSca | SIL2_Control | MODBUS:16:Write:Holding Registers | 11463 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11463 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE
3616 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | AckExeSca | SIL2_Control | MODBUS:4:Read:Input Registers | 20731 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20731 | 8 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394AckExeSca | 4 |  |  | 0 | $ComStatus , , | #SCADA MANUAL MODE EXECUTE ACK
3617 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | EleStat | SIL0 | MODBUS:4:Read:Input Registers | 20731 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20731 | 10 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394EleStat | 4 |  |  | 0 | $ComStatus , , | #VSD ELECTRICAL STATUS
3618 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | FailStart | SIL0 | MODBUS:4:Read:Input Registers | 20731 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20731 | 12 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394FailStart | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO START
3619 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | FailStop | SIL0 | MODBUS:4:Read:Input Registers | 20731 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20731 | 14 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394FailStop | 4 |  |  | 0 | $ComStatus , , | #VSD FAIL TO STOP
3620 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | SpeedFrep | SIL0 | MODBUS:4:Read:Input Registers | 20732 | 0 | 32 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20732 | 0 | 32 | aeiTUNQEC01QEC1AJETQEC1A-JET102394SpeedFrep | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED FREQUENCY
3621 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdSpeedOrd | SIL0 | MODBUS:16:Write:Holding Registers | 11464 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEOV | 16 | 16 | 11464 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdSpeedOrd | 4 |  |  | 0 | $ComStatus , , | #VSD SPEED ORDER
3622 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdSelStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11465 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11465 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT
3623 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | AckSelStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20734 | 0 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20734 | 0 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394AckSelStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER SELECT ACK
3624 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdExeStop | SIL2_Control | MODBUS:16:Write:Holding Registers | 11466 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11466 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE
3625 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | AckExeStop | SIL2_Control | MODBUS:4:Read:Input Registers | 20734 | 2 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20734 | 2 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394AckExeStop | 4 |  |  | 0 | $ComStatus , , | #STOP ORDER EXECUTE ACK
3626 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdSelFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11467 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11467 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT
3627 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | AckSelFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20734 | 4 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20734 | 4 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394AckSelFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER SELECT ACK
3628 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdExeFwOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11468 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11468 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE
3629 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | AckExeFwOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20734 | 6 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20734 | 6 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394AckExeFwOrd | 4 |  |  | 0 | $ComStatus , , | #FORWARD DIRECTION ORDER EXECUTE ACK
3630 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdSelRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11469 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11469 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT
3631 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | AckSelRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20734 | 8 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20734 | 8 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394AckSelRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER SELECT ACK
3632 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CmdExeRvOrd | SIL2_Control | MODBUS:16:Write:Holding Registers | 11470 | 0 | 1 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEOV | 16 | 16 | 11470 | 0 | 1 | deoTUNQEC01QEC1AJETQEC1A-JET102394CmdExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE
3633 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | AckExeRvOrd | SIL2_Control | MODBUS:4:Read:Input Registers | 20734 | 10 | 2 | Check SWC Name |  | QEC01-SIL2_Control |  | QEC01_RTU_S2C_EVariables.dat | DEIV | 4 | 1 | 20734 | 10 | 2 | deiTUNQEC01QEC1AJETQEC1A-JET102394AckExeRvOrd | 4 |  |  | 0 | $ComStatus , , | #REVERSE DIRECTION ORDER EXECUTE ACK
3634 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | AvailStat | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 0 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394AvailStat | 4 |  |  | 0 | $ComStatus , , | #FAN UNAVAILABLE STATUS
3635 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CirOpen | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 1 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394CirOpen | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER OPEN
3636 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | CirOut | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 2 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394CirOut | 4 |  |  | 0 | $ComStatus , , | #VSD CIRCUIT BREAKER FAULT
3637 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | FanOpen | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 3 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394FanOpen | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER OPEN
3638 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | FanOut | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 4 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394FanOut | 4 |  |  | 0 | $ComStatus , , | #FAN HEATER CIRCUIT BREAKER FAULT
3639 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | ForOut | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 5 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394ForOut | 4 |  |  | 0 | $ComStatus , , | #FORWARD COMMAND MISMATCH ALARM
3640 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | RevOut | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 6 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394RevOut | 4 |  |  | 0 | $ComStatus , , | #REVERSE COMMAND MISMATCH ALARM
3641 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | StopOut | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 7 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394StopOut | 4 |  |  | 0 | $ComStatus , , | #STOP COMMAND MISMATCH ALARM
3642 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | WindTem | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 8 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394WindTem | 4 |  |  | 0 | $ComStatus , , | #WINDING TEMPERATURE FAULT
3643 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | FrontTem1 | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 9 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394FrontTem1 | 4 |  |  | 0 | $ComStatus , , | #FRONT BEARING TEMPERATURE 1 FAULT
3644 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | RearTem | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 10 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394RearTem | 4 |  |  | 0 | $ComStatus , , | #REAR BEARING TEMPERATURE 1 FAULT
3645 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | Vib1 | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 11 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394Vib1 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 1ST LEVEL ALARM
3646 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | Vib2 | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 12 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394Vib2 | 4 |  |  | 0 | $ComStatus , , | #VIBRATION 2ND LEVEL FAULT
3647 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | More6hr | SIL0 | MODBUS:4:Read:Input Registers | 20735 | 13 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20735 | 13 | 1 | deiTUNQEC01QEC1AJETQEC1A-JET102394More6hr | 4 |  |  | 0 | $ComStatus , , | #MORE THAN 6 STARTUP PER HOUR
3648 | QEC01_RTU | TUN:QEC01 | QEC1A:JET | JET | QEC1A-JET102394 | 73 | RunHrs | SIL0 | MODBUS:4:Read:Input Registers | 20736 | 0 | 16 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | AEIV | 4 | 1 | 20736 | 0 | 16 | aeiTUNQEC01QEC1AJETQEC1A-JET102394RunHrs | 4 |  |  | 0 | $ComStatus , , | #RUNNING HOURS
3649 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Vac240SwOp | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 0 | 1 | deiTUNQEC01MMSSPLC01Vac240SwOp | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY DISCONNECTING SWITCH - OPEN
3650 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Vac240Volt | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 1 | 1 | deiTUNQEC01MMSSPLC01Vac240Volt | 4 |  |  | 0 | $ComStatus , , | #240VAC SUPPLY VOLTAGE PRESENCE
3651 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | VolOpen | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 2 | 1 | deiTUNQEC01MMSSPLC01VolOpen | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER OPEN
3652 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | VolFault | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 3 | 1 | deiTUNQEC01MMSSPLC01VolFault | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY CIRCUIT BREAKER FAULT
3653 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | VolSupOpen | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 4 | 1 | deiTUNQEC01MMSSPLC01VolSupOpen | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER OPEN
3654 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | VolSupFault | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 5 | 1 | deiTUNQEC01MMSSPLC01VolSupFault | 4 |  |  | 0 | $ComStatus , , | #VOLTAGE RELAY SUPPLY CIRCUIT BREAKER FAULT
3655 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | CabOpen | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 6 | 1 | deiTUNQEC01MMSSPLC01CabOpen | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS OPEN
3656 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | CabFault | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 7 | 1 | deiTUNQEC01MMSSPLC01CabFault | 4 |  |  | 0 | $ComStatus , , | #CABINET SOCKETS CIRCUIT BREAKERS FAULT
3657 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | SerOpen | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 8 | 1 | deiTUNQEC01MMSSPLC01SerOpen | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER OPEN
3658 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | SerFault | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 9 | 1 | deiTUNQEC01MMSSPLC01SerFault | 4 |  |  | 0 | $ComStatus , , | #SERVICES CIRCUIT BREAKER FAULT
3659 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | UpsBreOpen | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 10 | 1 | deiTUNQEC01MMSSPLC01UpsBreOpen | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER OPEN
3660 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | UpsBreFault | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 11 | 1 | deiTUNQEC01MMSSPLC01UpsBreFault | 4 |  |  | 0 | $ComStatus , , | #UPS CIRCUIT BREAKER FAULT
3661 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | UpsSwOpen | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 12 | 1 | deiTUNQEC01MMSSPLC01UpsSwOpen | 4 |  |  | 0 | $ComStatus , , | #UPS DISCONNECTING SWITCH OPEN
3662 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | UpsFault | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 13 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 13 | 1 | deiTUNQEC01MMSSPLC01UpsFault | 4 |  |  | 0 | $ComStatus , , | #UPS FAULT
3663 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Sup24Vdc1Open | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 14 | 1 | deiTUNQEC01MMSSPLC01Sup24Vdc1Open | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER OPEN
3664 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Sup24Vdc1Fault | SIL0 | MODBUS:4:Read:Input Registers | 20741 | 15 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20741 | 15 | 1 | deiTUNQEC01MMSSPLC01Sup24Vdc1Fault | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 CIRCUIT BREAKER FAULT
3665 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Sup24Vdc1Volt | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 0 | 1 | deiTUNQEC01MMSSPLC01Sup24Vdc1Volt | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 1 ABSENCE OF VOLTAGE
3666 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Sup24Vdc2Open | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 1 | 1 | deiTUNQEC01MMSSPLC01Sup24Vdc2Open | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER OPEN
3667 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Sup24Vdc2Fault | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 2 | 1 | deiTUNQEC01MMSSPLC01Sup24Vdc2Fault | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 CIRCUIT BREAKER FAULT
3668 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Sup24Vdc2Volt | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 3 | 1 | deiTUNQEC01MMSSPLC01Sup24Vdc2Volt | 4 |  |  | 0 | $ComStatus , , | #SUPPLY 24VDC 2 ABSENCE OF VOLTAGE
3669 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | SwOpen | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 4 | 1 | deiTUNQEC01MMSSPLC01SwOpen | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER OPEN
3670 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | SwFault | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 5 | 1 | deiTUNQEC01MMSSPLC01SwFault | 4 |  |  | 0 | $ComStatus , , | #SWITCH CIRCUIT BREAKER FAULT
3671 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | LcpOpen | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 6 | 1 | deiTUNQEC01MMSSPLC01LcpOpen | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER OPEN
3672 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | LcpFault | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 7 | 1 | deiTUNQEC01MMSSPLC01LcpFault | 4 |  |  | 0 | $ComStatus , , | #LCP CIRCUIT BREAKER FAULT
3673 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Plc1Open | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 8 | 1 | deiTUNQEC01MMSSPLC01Plc1Open | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER OPEN
3674 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Plc1Fault | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 9 | 1 | deiTUNQEC01MMSSPLC01Plc1Fault | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 1 CIRCUIT BREAKER FAULT
3675 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Plc2Open | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 10 | 1 | deiTUNQEC01MMSSPLC01Plc2Open | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER OPEN
3676 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | Plc2Fault | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 11 | 1 | deiTUNQEC01MMSSPLC01Plc2Fault | 4 |  |  | 0 | $ComStatus , , | #PLC SUPPLY 2 CIRCUIT BREAKER FAULT
3677 | QEC01_RTU | TUN:QEC01 | MMS | SPLCMMS | SPLC01 | 74 | SuArTrig | SIL0 | MODBUS:4:Read:Input Registers | 20742 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20742 | 12 | 1 | deiTUNQEC01MMSSPLC01SuArTrig | 4 |  |  | 0 | $ComStatus , , | #SURGE ARRESTER TRIGGERED
3678 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mcsd1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 0 | 1 | deiTUNQEC01MMSLPS-MDB01Mcsd1Stat | 4 |  |  | 0 | $ComStatus , , | #Power normal MCSD 1 status
3679 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mcsd2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 1 | 1 | deiTUNQEC01MMSLPS-MDB01Mcsd2Stat | 4 |  |  | 0 | $ComStatus , , | #Power replacement MCSD 2 status
3680 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mcsd1pos | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 2 | 1 | deiTUNQEC01MMSLPS-MDB01Mcsd1pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 1 racked position
3681 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mcsd2pos | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 3 | 1 | deiTUNQEC01MMSLPS-MDB01Mcsd2pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 2 racked position
3682 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Change | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 4 | 1 | deiTUNQEC01MMSLPS-MDB01Change | 4 |  |  | 0 | $ComStatus , , | #Change over
3683 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | relay1 | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 5 | 1 | deiTUNQEC01MMSLPS-MDB01relay1 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 1
3684 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | relay2 | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 6 | 1 | deiTUNQEC01MMSLPS-MDB01relay2 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 2
3685 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 7 | 1 | deiTUNQEC01MMSLPS-MDB01Closed | 4 |  |  | 0 | $ComStatus , , | #MCB closed status
3686 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 8 | 1 | deiTUNQEC01MMSLPS-MDB01Trip | 4 |  |  | 0 | $ComStatus , , | #MCB tripped status
3687 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | PowerCut | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 9 | 1 | deiTUNQEC01MMSLPS-MDB01PowerCut | 4 |  |  | 0 | $ComStatus , , | #Emergency power cut (push button)
3688 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mccb1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 10 | 1 | deiTUNQEC01MMSLPS-MDB01Mccb1Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 status
3689 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 11 | 1 | deiTUNQEC01MMSLPS-MDB01Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 trip
3690 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mccb2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 12 | 1 | deiTUNQEC01MMSLPS-MDB01Mccb2Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 status
3691 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 13 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 13 | 1 | deiTUNQEC01MMSLPS-MDB01Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 trip
3692 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mccb3Stat | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 14 | 1 | deiTUNQEC01MMSLPS-MDB01Mccb3Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 status
3693 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB01 | 75 | Mccb3Trip | SIL0 | MODBUS:4:Read:Input Registers | 20751 | 15 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20751 | 15 | 1 | deiTUNQEC01MMSLPS-MDB01Mccb3Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 trip
3694 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mcsd1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 0 | 1 | deiTUNQEC01MMSLPS-MDB02Mcsd1Stat | 4 |  |  | 0 | $ComStatus , , | #Power normal MCSD 1 status
3695 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mcsd2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 1 | 1 | deiTUNQEC01MMSLPS-MDB02Mcsd2Stat | 4 |  |  | 0 | $ComStatus , , | #Power replacement MCSD 2 status
3696 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mcsd1pos | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 2 | 1 | deiTUNQEC01MMSLPS-MDB02Mcsd1pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 1 racked position
3697 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mcsd2pos | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 3 | 1 | deiTUNQEC01MMSLPS-MDB02Mcsd2pos | 4 |  |  | 0 | $ComStatus , , | #MDB-01 MCSD 2 racked position
3698 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Change | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 4 | 1 | deiTUNQEC01MMSLPS-MDB02Change | 4 |  |  | 0 | $ComStatus , , | #Change over
3699 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | relay1 | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 5 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 5 | 1 | deiTUNQEC01MMSLPS-MDB02relay1 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 1
3700 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | relay2 | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 6 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 6 | 1 | deiTUNQEC01MMSLPS-MDB02relay2 | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay 2
3701 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 7 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 7 | 1 | deiTUNQEC01MMSLPS-MDB02Closed | 4 |  |  | 0 | $ComStatus , , | #MCB closed status
3702 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 8 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 8 | 1 | deiTUNQEC01MMSLPS-MDB02Trip | 4 |  |  | 0 | $ComStatus , , | #MCB tripped status
3703 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | PowerCut | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 9 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 9 | 1 | deiTUNQEC01MMSLPS-MDB02PowerCut | 4 |  |  | 0 | $ComStatus , , | #Emergency power cut (push button)
3704 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mccb1Stat | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 10 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 10 | 1 | deiTUNQEC01MMSLPS-MDB02Mccb1Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 status
3705 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 11 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 11 | 1 | deiTUNQEC01MMSLPS-MDB02Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 1 Incomer EL2 trip
3706 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mccb2Stat | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 12 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 12 | 1 | deiTUNQEC01MMSLPS-MDB02Mccb2Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 status
3707 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mccb2Trip | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 13 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 13 | 1 | deiTUNQEC01MMSLPS-MDB02Mccb2Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 2 Incomer EL2 trip
3708 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mccb3Stat | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 14 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 14 | 1 | deiTUNQEC01MMSLPS-MDB02Mccb3Stat | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 status
3709 | QEC01_RTU | TUN:QEC01 | MMS | MDB | LPS-MDB02 | 76 | Mccb3Trip | SIL0 | MODBUS:4:Read:Input Registers | 20761 | 15 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20761 | 15 | 1 | deiTUNQEC01MMSLPS-MDB02Mccb3Trip | 4 |  |  | 0 | $ComStatus , , | #MCCB 3 Incomer EL2 trip
3710 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL1-IO01 | 77 | Relay | SIL0 | MODBUS:4:Read:Input Registers | 20771 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20771 | 0 | 1 | deiTUNQEC01MMSEL1-IO01Relay | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay
3711 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL1-IO01 | 77 | Isolator | SIL0 | MODBUS:4:Read:Input Registers | 20771 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20771 | 1 | 1 | deiTUNQEC01MMSEL1-IO01Isolator | 4 |  |  | 0 | $ComStatus , , | #LBS Main incomer isolator status
3712 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL1-IO01 | 77 | Supply | SIL0 | MODBUS:4:Read:Input Registers | 20771 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20771 | 2 | 1 | deiTUNQEC01MMSEL1-IO01Supply | 4 |  |  | 0 | $ComStatus , , | #UPS supply status
3713 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL1-IO01 | 77 | Faulty | SIL0 | MODBUS:4:Read:Input Registers | 20771 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20771 | 3 | 1 | deiTUNQEC01MMSEL1-IO01Faulty | 4 |  |  | 0 | $ComStatus , , | #UPS faulty
3714 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL1-IO01 | 77 | Power | SIL0 | MODBUS:4:Read:Input Registers | 20771 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20771 | 4 | 1 | deiTUNQEC01MMSEL1-IO01Power | 4 |  |  | 0 | $ComStatus , , | #24VDC UPS power status
3715 | QEC01_RTU | TUN:QEC01 | MMS | MCCB | EL1-UPS | 78 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 20781 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20781 | 0 | 1 | deiTUNQEC01MMSEL1-UPSTrip | 4 |  |  | 0 | $ComStatus , , | #MCCB trip status
3716 | QEC01_RTU | TUN:QEC01 | MMS | MCCB | EL1-UPS | 78 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20781 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20781 | 1 | 1 | deiTUNQEC01MMSEL1-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #MCCB closed status
3717 | QEC01_RTU | TUN:QEC01 | MMS | LBS | EL1-UPS | 79 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 20791 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20791 | 0 | 1 | deiTUNQEC01MMSEL1-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #LBS closed status
3718 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL1-VSD01 | 80 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20801 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20801 | 0 | 1 | deiTUNQEC01MMSUPS_EL1-VSD01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3719 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL1-VSD01 | 80 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20801 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20801 | 1 | 1 | deiTUNQEC01MMSUPS_EL1-VSD01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3720 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL1-VSD02 | 81 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20811 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20811 | 0 | 1 | deiTUNQEC01MMSUPS_EL1-VSD02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3721 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL1-VSD02 | 81 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20811 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20811 | 1 | 1 | deiTUNQEC01MMSUPS_EL1-VSD02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3722 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT3-IDP01 | 82 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20821 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20821 | 0 | 1 | deiTUNQEC01MMS3P-VT3-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3723 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT3-IDP01 | 82 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20821 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20821 | 1 | 1 | deiTUNQEC01MMS3P-VT3-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3724 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT3-IDP01 | 83 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20831 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20831 | 0 | 1 | deiTUNQEC01MMS2P-VT3-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3725 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT3-IDP01 | 83 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20831 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20831 | 1 | 1 | deiTUNQEC01MMS2P-VT3-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3726 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT4-IDP01 | 84 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20841 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20841 | 0 | 1 | deiTUNQEC01MMS3P-VT4-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3727 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT4-IDP01 | 84 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20841 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20841 | 1 | 1 | deiTUNQEC01MMS3P-VT4-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3728 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT4-IDP01 | 85 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20851 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20851 | 0 | 1 | deiTUNQEC01MMS2P-VT4-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3729 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT4-IDP01 | 85 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20851 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20851 | 1 | 1 | deiTUNQEC01MMS2P-VT4-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3730 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-01 | 86 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20861 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20861 | 0 | 1 | deiTUNQEC01MMS3P-VT6-TDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3731 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-01 | 86 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20861 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20861 | 1 | 1 | deiTUNQEC01MMS3P-VT6-TDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3732 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-01 | 87 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20871 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20871 | 0 | 1 | deiTUNQEC01MMS2P-VT6-TDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3733 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-01 | 87 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20871 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20871 | 1 | 1 | deiTUNQEC01MMS2P-VT6-TDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3734 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-02 | 88 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20881 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20881 | 0 | 1 | deiTUNQEC01MMS3P-VT6-TDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3735 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-02 | 88 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20881 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20881 | 1 | 1 | deiTUNQEC01MMS3P-VT6-TDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3736 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-02 | 89 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20891 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20891 | 0 | 1 | deiTUNQEC01MMS2P-VT6-TDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3737 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-02 | 89 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20891 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20891 | 1 | 1 | deiTUNQEC01MMS2P-VT6-TDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3738 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-03 | 90 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20901 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20901 | 0 | 1 | deiTUNQEC01MMS3P-VT6-TDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3739 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT6-TDP01-03 | 90 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20901 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20901 | 1 | 1 | deiTUNQEC01MMS3P-VT6-TDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3740 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-03 | 91 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20911 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20911 | 0 | 1 | deiTUNQEC01MMS2P-VT6-TDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3741 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT6-TDP01-03 | 91 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20911 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20911 | 1 | 1 | deiTUNQEC01MMS2P-VT6-TDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3742 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P--FR2-BDP01-01 | 92 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20921 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20921 | 0 | 1 | deiTUNQEC01MMS3P--FR2-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3743 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P--FR2-BDP01-01 | 92 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20921 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20921 | 1 | 1 | deiTUNQEC01MMS3P--FR2-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3744 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P--FR2-BDP01-01 | 93 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20931 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20931 | 0 | 1 | deiTUNQEC01MMS2P--FR2-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3745 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P--FR2-BDP01-01 | 93 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20931 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20931 | 1 | 1 | deiTUNQEC01MMS2P--FR2-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3746 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P--FR2-BDP01-02 | 94 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20941 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20941 | 0 | 1 | deiTUNQEC01MMS3P--FR2-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3747 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P--FR2-BDP01-02 | 94 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20941 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20941 | 1 | 1 | deiTUNQEC01MMS3P--FR2-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3748 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P--FR2-BDP01-02 | 95 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20951 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20951 | 0 | 1 | deiTUNQEC01MMS2P--FR2-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3749 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P--FR2-BDP01-02 | 95 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20951 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20951 | 1 | 1 | deiTUNQEC01MMS2P--FR2-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3750 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-94 | 96 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20961 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20961 | 0 | 1 | deiTUNQEC01MMSMSFD-CON-94McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3751 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-94 | 96 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20961 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20961 | 1 | 1 | deiTUNQEC01MMSMSFD-CON-94McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3752 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-58 | 97 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20971 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20971 | 0 | 1 | deiTUNQEC01MMSMSFD-CON-58McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3753 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-58 | 97 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20971 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20971 | 1 | 1 | deiTUNQEC01MMSMSFD-CON-58McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3754 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-88 | 98 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 20981 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20981 | 0 | 1 | deiTUNQEC01MMSMSFD-CON-88McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3755 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-88 | 98 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 20981 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20981 | 1 | 1 | deiTUNQEC01MMSMSFD-CON-88McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3756 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL2-IO01 | 99 | Relay | SIL0 | MODBUS:4:Read:Input Registers | 20991 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20991 | 0 | 1 | deiTUNQEC01MMSEL2-IO01Relay | 4 |  |  | 0 | $ComStatus , , | #Phase failure relay
3757 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL2-IO01 | 99 | Isolator | SIL0 | MODBUS:4:Read:Input Registers | 20991 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20991 | 1 | 1 | deiTUNQEC01MMSEL2-IO01Isolator | 4 |  |  | 0 | $ComStatus , , | #LBS Main incomer isolator status
3758 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL2-IO01 | 99 | Supply | SIL0 | MODBUS:4:Read:Input Registers | 20991 | 2 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20991 | 2 | 1 | deiTUNQEC01MMSEL2-IO01Supply | 4 |  |  | 0 | $ComStatus , , | #UPS supply status
3759 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL2-IO01 | 99 | Faulty | SIL0 | MODBUS:4:Read:Input Registers | 20991 | 3 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20991 | 3 | 1 | deiTUNQEC01MMSEL2-IO01Faulty | 4 |  |  | 0 | $ComStatus , , | #UPS faulty
3760 | QEC01_RTU | TUN:QEC01 | MMS | EL | EL2-IO01 | 99 | Power | SIL0 | MODBUS:4:Read:Input Registers | 20991 | 4 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 20991 | 4 | 1 | deiTUNQEC01MMSEL2-IO01Power | 4 |  |  | 0 | $ComStatus , , | #24VDC UPS power status
3761 | QEC01_RTU | TUN:QEC01 | MMS | MCCB | EL2-UPS | 100 | Trip | SIL0 | MODBUS:4:Read:Input Registers | 21001 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21001 | 0 | 1 | deiTUNQEC01MMSEL2-UPSTrip | 4 |  |  | 0 | $ComStatus , , | #MCCB trip status
3762 | QEC01_RTU | TUN:QEC01 | MMS | MCCB | EL2-UPS | 100 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 21001 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21001 | 1 | 1 | deiTUNQEC01MMSEL2-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #MCCB closed status
3763 | QEC01_RTU | TUN:QEC01 | MMS | LBS | EL2-UPS | 101 | Closed | SIL0 | MODBUS:4:Read:Input Registers | 21011 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21011 | 0 | 1 | deiTUNQEC01MMSEL2-UPSClosed | 4 |  |  | 0 | $ComStatus , , | #LBS closed status
3764 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL2-VSD01 | 102 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21021 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21021 | 0 | 1 | deiTUNQEC01MMSUPS_EL2-VSD01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3765 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL2-VSD01 | 102 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21021 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21021 | 1 | 1 | deiTUNQEC01MMSUPS_EL2-VSD01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3766 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL2-VSD02 | 103 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21031 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21031 | 0 | 1 | deiTUNQEC01MMSUPS_EL2-VSD02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3767 | QEC01_RTU | TUN:QEC01 | MMS | MCB | UPS_EL2-VSD02 | 103 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21031 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21031 | 1 | 1 | deiTUNQEC01MMSUPS_EL2-VSD02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3768 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT1-IDP01 | 104 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21041 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21041 | 0 | 1 | deiTUNQEC01MMS3P-VT1-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3769 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT1-IDP01 | 104 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21041 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21041 | 1 | 1 | deiTUNQEC01MMS3P-VT1-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3770 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT1-IDP01 | 105 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21051 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21051 | 0 | 1 | deiTUNQEC01MMS2P-VT1-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3771 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT1-IDP01 | 105 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21051 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21051 | 1 | 1 | deiTUNQEC01MMS2P-VT1-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3772 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT2-IDP01 | 106 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21061 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21061 | 0 | 1 | deiTUNQEC01MMS3P-VT2-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3773 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT2-IDP01 | 106 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21061 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21061 | 1 | 1 | deiTUNQEC01MMS3P-VT2-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3774 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT2-IDP01 | 107 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21071 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21071 | 0 | 1 | deiTUNQEC01MMS2P-VT2-IDP01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3775 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT2-IDP01 | 107 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21071 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21071 | 1 | 1 | deiTUNQEC01MMS2P-VT2-IDP01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3776 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-01 | 108 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21081 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21081 | 0 | 1 | deiTUNQEC01MMS3P-VT5-TDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3777 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-01 | 108 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21081 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21081 | 1 | 1 | deiTUNQEC01MMS3P-VT5-TDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3778 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-01 | 109 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21091 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21091 | 0 | 1 | deiTUNQEC01MMS2P-VT5-TDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3779 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-01 | 109 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21091 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21091 | 1 | 1 | deiTUNQEC01MMS2P-VT5-TDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3780 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-02 | 110 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21101 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21101 | 0 | 1 | deiTUNQEC01MMS3P-VT5-TDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3781 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-02 | 110 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21101 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21101 | 1 | 1 | deiTUNQEC01MMS3P-VT5-TDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3782 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-02 | 111 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21111 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21111 | 0 | 1 | deiTUNQEC01MMS2P-VT5-TDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3783 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-02 | 111 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21111 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21111 | 1 | 1 | deiTUNQEC01MMS2P-VT5-TDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3784 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-03 | 112 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21121 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21121 | 0 | 1 | deiTUNQEC01MMS3P-VT5-TDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3785 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-VT5-TDP01-03 | 112 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21121 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21121 | 1 | 1 | deiTUNQEC01MMS3P-VT5-TDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3786 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-03 | 113 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21131 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21131 | 0 | 1 | deiTUNQEC01MMS2P-VT5-TDP01-03McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3787 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-VT5-TDP01-03 | 113 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21131 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21131 | 1 | 1 | deiTUNQEC01MMS2P-VT5-TDP01-03McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3788 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-FR1-BDP01-01 | 114 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21141 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21141 | 0 | 1 | deiTUNQEC01MMS3P-FR1-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3789 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-FR1-BDP01-01 | 114 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21141 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21141 | 1 | 1 | deiTUNQEC01MMS3P-FR1-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3790 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-FR1-BDP01-01 | 115 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21151 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21151 | 0 | 1 | deiTUNQEC01MMS2P-FR1-BDP01-01McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3791 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-FR1-BDP01-01 | 115 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21151 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21151 | 1 | 1 | deiTUNQEC01MMS2P-FR1-BDP01-01McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3792 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-FR1-BDP01-02 | 116 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21161 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21161 | 0 | 1 | deiTUNQEC01MMS3P-FR1-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3793 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 3P-FR1-BDP01-02 | 116 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21161 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21161 | 1 | 1 | deiTUNQEC01MMS3P-FR1-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3794 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-FR1-BDP01-02 | 117 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21171 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21171 | 0 | 1 | deiTUNQEC01MMS2P-FR1-BDP01-02McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3795 | QEC01_RTU | TUN:QEC01 | MMS | MCB | 2P-FR1-BDP01-02 | 117 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21171 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21171 | 1 | 1 | deiTUNQEC01MMS2P-FR1-BDP01-02McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3796 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-50 | 118 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21181 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21181 | 0 | 1 | deiTUNQEC01MMSMSFD-CON-50McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3797 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-50 | 118 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21181 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21181 | 1 | 1 | deiTUNQEC01MMSMSFD-CON-50McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3798 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-52 | 119 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21191 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21191 | 0 | 1 | deiTUNQEC01MMSMSFD-CON-52McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3799 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-52 | 119 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21191 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21191 | 1 | 1 | deiTUNQEC01MMSMSFD-CON-52McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
3800 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-95 | 120 | McbTrip | SIL0 | MODBUS:4:Read:Input Registers | 21201 | 0 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21201 | 0 | 1 | deiTUNQEC01MMSMSFD-CON-95McbTrip | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB trip status
3801 | QEC01_RTU | TUN:QEC01 | MMS | MCB | MSFD-CON-95 | 120 | McbClose | SIL0 | MODBUS:4:Read:Input Registers | 21201 | 1 | 1 | Check SWC Name |  | QEC01-SIL0 |  | QEC01_RTU_S0_EVariables.dat | DEIV | 4 | 1 | 21201 | 1 | 1 | deiTUNQEC01MMSMSFD-CON-95McbClose | 4 |  |  | 0 | $ComStatus , , | #Auxiliary MCB closed status
-END-

## A-Validation Data list
RTU_Protocol_Operation_Code | Memory_Block | RTU_Protocol | Operation Code List | Association with Memory Block | RTU_Undefined_Operation_Code | RTU_Undefined_Operation_Code | RTU_Modbus_Operation_Code | Modbus_Memory_Block | RTU_IEC104_Operation_Code | IEC104_Memory_Block | RTU_Data_Check_Function | RTU_Data_Translation_Function | Bit_Position
MODBUS:1:Read:Coils | MODBUS:MEMBLOCK01 | MODBUS-TCP | SE_RTU_Modbus_Operation_Code | SE_RTU_Modbus_Table |  |  | MODBUS:1:Read:Coils | MODBUS:MEMBLOCK01 | IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | cfRANGE | tfNOT | 0
MODBUS:2:Read:Discrete Inputs | MODBUS:MEMBLOCK02 | MODBUS-RTU | SE_RTU_Modbus_Operation_Code | SE_RTU_Modbus_Table |  |  | MODBUS:2:Read:Discrete Inputs | MODBUS:MEMBLOCK02 | IEC104:M_DP_NA_1 | IEC104:MEMBLOCK01 |  | tfLIN | 1
MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | IEC60870-5-104 | SE_RTU_IEC104_Operation_Code | SE_RTU_IEC104_Table |  |  | MODBUS:3:Read:Holding Registers | MODBUS:MEMBLOCK03 | IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 |  | BTL32 | 2
MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | IEC60870-5-101 | SE_RTU_IEC104_Operation_Code | SE_RTU_IEC104_Table |  |  | MODBUS:4:Read:Input Registers | MODBUS:MEMBLOCK04 | IEC104:M_ME_NB_1 | IEC104:MEMBLOCK01 |  | LTB16 | 3
MODBUS:5:Write:Coil | MODBUS:MEMBLOCK01 | DNP3.0 | SE_RTU_Undefined_Operation_Code | SE_RTU_Undefined_Table |  |  | MODBUS:5:Write:Coil | MODBUS:MEMBLOCK01 | IEC104:M_ME_NC_1 | IEC104:MEMBLOCK01 |  | USHORT | 4
MODBUS:6:Write:Holding Register | MODBUS:MEMBLOCK03 | BACNET-TCP | SE_RTU_Undefined_Operation_Code | SE_RTU_Undefined_Table |  |  | MODBUS:6:Write:Holding Register | MODBUS:MEMBLOCK03 | IEC104:M_IT_NA_1 | IEC104:MEMBLOCK01 |  |  | 5
MODBUS:15:Write:Coils | MODBUS:MEMBLOCK01 |  | SE_RTU_Undefined_Operation_Code | SE_RTU_Undefined_Table |  |  | MODBUS:15:Write:Coils | MODBUS:MEMBLOCK01 | IEC104:M_SP_TB_1 | IEC104:MEMBLOCK01 |  |  | 6
MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | [5 empty] | MODBUS:16:Write:Holding Registers | MODBUS:MEMBLOCK03 | IEC104:M_DP_TB_1 | IEC104:MEMBLOCK01 |  |  | 7
IEC104:M_SP_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SC_NA_1 | IEC104:MEMBLOCK01 |  |  | 8
IEC104:M_DP_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 |  |  | 9
IEC104:M_ME_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_RC_NA_1 | IEC104:MEMBLOCK01 |  |  | 10
IEC104:M_ME_NB_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SE_NA_1 | IEC104:MEMBLOCK01 |  |  | 11
IEC104:M_ME_NC_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SE_NB_1 | IEC104:MEMBLOCK01 |  |  | 12
IEC104:M_IT_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_SE_NC_1 | IEC104:MEMBLOCK01 |  |  | 13
IEC104:M_SP_TB_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_IC_NA_1 | IEC104:MEMBLOCK01 |  |  | 14
IEC104:M_DP_TB_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_CI_NA_1 | IEC104:MEMBLOCK01 |  |  | 15
IEC104:C_SC_NA_1 | IEC104:MEMBLOCK01 | [7 empty] | IEC104:C_RD_NA_1 | IEC104:MEMBLOCK01 |  |  | 16
IEC104:C_DC_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 17
IEC104:C_RC_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 18
IEC104:C_SE_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 19
IEC104:C_SE_NB_1 | IEC104:MEMBLOCK01 | [11 empty] | 20
IEC104:C_SE_NC_1 | IEC104:MEMBLOCK01 | [11 empty] | 21
IEC104:C_IC_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 22
IEC104:C_CI_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 23
IEC104:C_RD_NA_1 | IEC104:MEMBLOCK01 | [11 empty] | 24
25
|  | Check of Validation Lists | [10 empty] | 26
|  | PLC Protocol | Available Operation Code | [9 empty] | 27
|  | IEC60870-5-104 | IEC104:M_ME_NA_1 | [9 empty] | 28
|  | MODBUS-RTU | MODBUS:4:Read:Input Registers | [9 empty] | 29
30
31
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
Note on E1: BERNARD Olivier: This column identifies the list to the associated operation codes. This list is defined through a name (Excel Formula name)

## B-Address Qty
FC / Class Name | MPLC | MSPLC | WTDG | SWI | SPLC | SHAFT | TVF | JET | TVD | MEPD | OTS | TTS | VS | LCP | AHU | PFA | SMC | SED | MUL | FXL | IOM | IOC | MDB | MSH1 | MSH2 | MJF1 | MJF2 | CSH | CJF | SCB | MCB | TRU | TRD | MPLCMMS | VENTILATION | EMERGENCY | FMOP | IDP | MSFD | SPLCMMS | ADS | TRF | ACB | EL | MCCB | LBS
MODBUS:1:Read:Coils | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000 | 40;1000
MODBUS:2:Read:Discrete Inputs | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000 | 40;5000
MODBUS:3:Read:Holding Registers | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000 | 40;10000
MODBUS:4:Read:Input Registers | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 40;30000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000 | 10;20000
MODBUS:5:Write:Coil | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 30;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000
MODBUS:6:Write:Holding Register | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 30;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000
MODBUS:15:Write:Coils | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 30;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000 | 20;1000
MODBUS:16:Write:Holding Registers | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 30;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000 | 20;10000
IEC104:M_SP_NA_1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
IEC104:M_DP_NA_1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
IEC104:M_ME_NA_1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
IEC104:M_ME_NB_1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
IEC104:M_ME_NC_1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
IEC104:M_IT_NA_1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
IEC104:M_SP_TB_1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
IEC104:M_DP_TB_1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
IEC104:C_SC_NA_1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
IEC104:C_DC_NA_1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
IEC104:C_RC_NA_1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
IEC104:C_SE_NA_1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
IEC104:C_SE_NB_1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
IEC104:C_SE_NC_1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
IEC104:C_IC_NA_1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
IEC104:C_CI_NA_1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
IEC104:C_RD_NA_1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20